## Test ExtLWRad
EnergyPlus Results for ASHRAE 1052RP Analytical Tests
1052 Toolkit Software Version 1.0
EnergyPlus Version 8.2.0
t=.10m
k=1.00W/m-K
Test ExtLWRad: External Long Wave Radiation
| Test Parameter | Units | 1052RP | EnergyPlus | % Diff
| Heat Flux | W/m2 | 18.7755 | 24.3094 | 29.47%
| Zone Load | W | 168.9795 | 218.7847 | 29.47%
Delta
| Inside Surface Temperature | C | 15.3526 | 16.8012 | 1.4486
| Outside Surface Temperature | C | 13.4751 | 14.3702 | 0.89514
| Inside Convection Coefficient | W/m2-K | 4.04 | 4.04
| Outside Convection Coefficient | W/m2-K | 1.352 | 1.3518
| Sky Temperature | C | 7.552 | 7.5521
Note: Convection coefficients were taken from EnergyPlus and entered into 1052RP Toolkit software
Zone Load = Heat Flux x 9 m2 surface area