## EPlus 100 Conv
EnergyPlus Results for ASHRAE 1052RP Analytical Test IntHeatGain
Step change in internal load
2700 W for 168 hours, 100% convective
Hour | Date/Time | Environment:Outdoor Dry Bulb [C](Hourly) | Environment:Diffuse Solar [W/m2](Hourly) | Environment:Direct Solar [W/m2](Hourly) | ZONE ONE:Zone/Sys Sensible Heating Energy[J](Hourly) | ZONE ONE:Zone/Sys Sensible Cooling Energy[J](Hourly) | ZONE ONE:Mean Air Temperature[C](Hourly) | ZONE ONE:Zone-Total Radiant Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Convective Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Lost Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Radiant Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Convective Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Lost Heat Gain[J](Hourly) | EnergyPlus - !00% Convective | ZONE SURFACE NORTH:Surface Outside Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE NORTH:Surface Ext Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE SOUTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE EAST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE WEST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE CEILING:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE FLOOR:Surface Int Convection Coeff[W/m2-K](Hourly) | EnergyPlus - 100% Convective
1 | 08/01 01:00:00 | 20 | 0 | 0 | 0 | 9719995.9333 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
2 | 08/01 02:00:00 | 20 | 0 | 0 | 0 | 9719995.8683 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
3 | 08/01 03:00:00 | 20 | 0 | 0 | 0 | 9719995.7938 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
4 | 08/01 04:00:00 | 20 | 0 | 0 | 0 | 9719995.7214 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
5 | 08/01 05:00:00 | 20 | 0 | 0 | 0 | 9719995.6532 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
6 | 08/01 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.5884 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
7 | 08/01 07:00:00 | 20 | 0 | 181 | 0 | 9719995.5311 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
8 | 08/01 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.4831 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
9 | 08/01 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.437 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
10 | 08/01 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.3903 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
11 | 08/01 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.3456 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
12 | 08/01 12:00:00 | 20 | 0 | 899.5 | 0 | 9719995.3049 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
13 | 08/01 13:00:00 | 20 | 0 | 907 | 0 | 9719995.2681 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
14 | 08/01 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719995.2315 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
15 | 08/01 15:00:00 | 20 | 0 | 887.25 | 0 | 9719995.1961 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
16 | 08/01 16:00:00 | 20 | 0 | 853.5 | 0 | 9719995.1656 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
17 | 08/01 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719995.1387 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
18 | 08/01 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719995.1156 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
19 | 08/01 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719995.1024 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
20 | 08/01 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719995.1002 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
21 | 08/01 21:00:00 | 20 | 0 | 0 | 0 | 9719995.1043 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
22 | 08/01 22:00:00 | 20 | 0 | 0 | 0 | 9719995.1095 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
23 | 08/01 23:00:00 | 20 | 0 | 0 | 0 | 9719995.1139 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
24 | 08/01 24:00:00 | 20 | 0 | 0 | 0 | 9719995.1189 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
25 | 08/02 01:00:00 | 20 | 0 | 0 | 0 | 9719995.1295 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9986
26 | 08/02 02:00:00 | 20 | 0 | 0 | 0 | 9719995.1486 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
27 | 08/02 03:00:00 | 20 | 0 | 0 | 0 | 9719995.1773 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
28 | 08/02 04:00:00 | 20 | 0 | 0 | 0 | 9719995.2162 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
29 | 08/02 05:00:00 | 20 | 0 | 0 | 0 | 9719995.2631 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
30 | 08/02 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.3106 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
31 | 08/02 07:00:00 | 20 | 0 | 181 | 0 | 9719995.3451 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
32 | 08/02 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.3546 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
33 | 08/02 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.3343 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
34 | 08/02 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.2909 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
35 | 08/02 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.2405 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
36 | 08/02 12:00:00 | 20 | 0 | 899.5 | 0 | 9719995.1966 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
37 | 08/02 13:00:00 | 20 | 0 | 907 | 0 | 9719995.1666 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
38 | 08/02 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719995.1528 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
39 | 08/02 15:00:00 | 20 | 0 | 887.25 | 0 | 9719995.1547 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
40 | 08/02 16:00:00 | 20 | 0 | 853.5 | 0 | 9719995.1698 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
41 | 08/02 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719995.195 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
42 | 08/02 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719995.2265 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
43 | 08/02 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719995.2601 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
44 | 08/02 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719995.2967 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
45 | 08/02 21:00:00 | 20 | 0 | 0 | 0 | 9719995.3414 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
46 | 08/02 22:00:00 | 20 | 0 | 0 | 0 | 9719995.3909 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
47 | 08/02 23:00:00 | 20 | 0 | 0 | 0 | 9719995.4357 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
48 | 08/02 24:00:00 | 20 | 0 | 0 | 0 | 9719995.475 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
49 | 08/03 01:00:00 | 20 | 0 | 0 | 0 | 9719995.5152 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
50 | 08/03 02:00:00 | 20 | 0 | 0 | 0 | 9719995.5582 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
51 | 08/03 03:00:00 | 20 | 0 | 0 | 0 | 9719995.6025 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
52 | 08/03 04:00:00 | 20 | 0 | 0 | 0 | 9719995.6492 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
53 | 08/03 05:00:00 | 20 | 0 | 0 | 0 | 9719995.6969 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
54 | 08/03 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.7393 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
55 | 08/03 07:00:00 | 20 | 0 | 181 | 0 | 9719995.7739 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
56 | 08/03 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.8073 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
57 | 08/03 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.8501 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
58 | 08/03 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.9075 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
59 | 08/03 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.9739 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
60 | 08/03 12:00:00 | 20 | 0 | 899.5 | 0 | 9719996.0393 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
61 | 08/03 13:00:00 | 20 | 0 | 907 | 0 | 9719996.0959 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
62 | 08/03 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719996.1409 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
63 | 08/03 15:00:00 | 20 | 0 | 887.25 | 0 | 9719996.1729 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
64 | 08/03 16:00:00 | 20 | 0 | 853.5 | 0 | 9719996.1926 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
65 | 08/03 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719996.2042 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
66 | 08/03 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719996.2144 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
67 | 08/03 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719996.2286 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
68 | 08/03 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719996.2481 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
69 | 08/03 21:00:00 | 20 | 0 | 0 | 0 | 9719996.2713 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
70 | 08/03 22:00:00 | 20 | 0 | 0 | 0 | 9719996.2955 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
71 | 08/03 23:00:00 | 20 | 0 | 0 | 0 | 9719996.3128 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
72 | 08/03 24:00:00 | 20 | 0 | 0 | 0 | 9719996.3181 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
73 | 08/04 01:00:00 | 20 | 0 | 0 | 0 | 9719996.3184 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
74 | 08/04 02:00:00 | 20 | 0 | 0 | 0 | 9719996.3197 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
75 | 08/04 03:00:00 | 20 | 0 | 0 | 0 | 9719996.3181 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
76 | 08/04 04:00:00 | 20 | 0 | 0 | 0 | 9719996.3117 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
77 | 08/04 05:00:00 | 20 | 0 | 0 | 0 | 9719996.3032 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
78 | 08/04 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719996.2923 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
79 | 08/04 07:00:00 | 20 | 0 | 181 | 0 | 9719996.2732 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
80 | 08/04 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719996.2419 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.999
81 | 08/04 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719996.2011 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
82 | 08/04 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719996.1571 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
83 | 08/04 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719996.1177 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
84 | 08/04 12:00:00 | 20 | 0 | 899.5 | 0 | 9719996.0879 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
85 | 08/04 13:00:00 | 20 | 0 | 907 | 0 | 9719996.0683 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
86 | 08/04 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719996.0595 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
87 | 08/04 15:00:00 | 20 | 0 | 887.25 | 0 | 9719996.0602 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
88 | 08/04 16:00:00 | 20 | 0 | 853.5 | 0 | 9719996.0626 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
89 | 08/04 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719996.0585 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
90 | 08/04 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719996.0444 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
91 | 08/04 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719996.0229 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
92 | 08/04 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719995.999 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
93 | 08/04 21:00:00 | 20 | 0 | 0 | 0 | 9719995.9767 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
94 | 08/04 22:00:00 | 20 | 0 | 0 | 0 | 9719995.9582 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
95 | 08/04 23:00:00 | 20 | 0 | 0 | 0 | 9719995.9443 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
96 | 08/04 24:00:00 | 20 | 0 | 0 | 0 | 9719995.9393 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
97 | 08/05 01:00:00 | 20 | 0 | 0 | 0 | 9719995.9461 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
98 | 08/05 02:00:00 | 20 | 0 | 0 | 0 | 9719995.9622 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
99 | 08/05 03:00:00 | 20 | 0 | 0 | 0 | 9719995.979 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
100 | 08/05 04:00:00 | 20 | 0 | 0 | 0 | 9719995.9831 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
101 | 08/05 05:00:00 | 20 | 0 | 0 | 0 | 9719995.9664 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
102 | 08/05 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.9309 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
103 | 08/05 07:00:00 | 20 | 0 | 181 | 0 | 9719995.8816 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
104 | 08/05 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.8227 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
105 | 08/05 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.7563 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
106 | 08/05 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.6865 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
107 | 08/05 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.6276 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
108 | 08/05 12:00:00 | 20 | 0 | 899.5 | 0 | 9719995.5935 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
109 | 08/05 13:00:00 | 20 | 0 | 907 | 0 | 9719995.5865 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
110 | 08/05 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719995.6062 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
111 | 08/05 15:00:00 | 20 | 0 | 887.25 | 0 | 9719995.6505 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
112 | 08/05 16:00:00 | 20 | 0 | 853.5 | 0 | 9719995.7078 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
113 | 08/05 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719995.7592 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
114 | 08/05 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719995.7928 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
115 | 08/05 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719995.8115 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
116 | 08/05 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719995.8196 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
117 | 08/05 21:00:00 | 20 | 0 | 0 | 0 | 9719995.8195 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
118 | 08/05 22:00:00 | 20 | 0 | 0 | 0 | 9719995.8171 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
119 | 08/05 23:00:00 | 20 | 0 | 0 | 0 | 9719995.8124 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
120 | 08/05 24:00:00 | 20 | 0 | 0 | 0 | 9719995.7982 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
121 | 08/06 01:00:00 | 20 | 0 | 0 | 0 | 9719995.7724 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
122 | 08/06 02:00:00 | 20 | 0 | 0 | 0 | 9719995.7376 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
123 | 08/06 03:00:00 | 20 | 0 | 0 | 0 | 9719995.696 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
124 | 08/06 04:00:00 | 20 | 0 | 0 | 0 | 9719995.6527 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
125 | 08/06 05:00:00 | 20 | 0 | 0 | 0 | 9719995.6149 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
126 | 08/06 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.5883 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
127 | 08/06 07:00:00 | 20 | 0 | 181 | 0 | 9719995.5721 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
128 | 08/06 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.5614 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
129 | 08/06 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.5533 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
130 | 08/06 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.5491 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
131 | 08/06 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.5557 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
132 | 08/06 12:00:00 | 20 | 0 | 899.5 | 0 | 9719995.5775 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
133 | 08/06 13:00:00 | 20 | 0 | 907 | 0 | 9719995.6144 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
134 | 08/06 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719995.6685 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
135 | 08/06 15:00:00 | 20 | 0 | 887.25 | 0 | 9719995.7407 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
136 | 08/06 16:00:00 | 20 | 0 | 853.5 | 0 | 9719995.818 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
137 | 08/06 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719995.8813 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
138 | 08/06 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719995.9171 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
139 | 08/06 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719995.9224 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
140 | 08/06 20:00:00 | 20 | 0 | 32.4167 | 0 | 9719995.9042 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
141 | 08/06 21:00:00 | 20 | 0 | 0 | 0 | 9719995.8683 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9989
142 | 08/06 22:00:00 | 20 | 0 | 0 | 0 | 9719995.8202 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
143 | 08/06 23:00:00 | 20 | 0 | 0 | 0 | 9719995.7722 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
144 | 08/06 24:00:00 | 20 | 0 | 0 | 0 | 9719995.7377 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
145 | 08/07 01:00:00 | 20 | 0 | 0 | 0 | 9719995.7195 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
146 | 08/07 02:00:00 | 20 | 0 | 0 | 0 | 9719995.7078 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
147 | 08/07 03:00:00 | 20 | 0 | 0 | 0 | 9719995.693 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
148 | 08/07 04:00:00 | 20 | 0 | 0 | 0 | 9719995.6734 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
149 | 08/07 05:00:00 | 20 | 0 | 0 | 0 | 9719995.651 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
150 | 08/07 06:00:00 | 20 | 0 | 9.8333 | 0 | 9719995.6266 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
151 | 08/07 07:00:00 | 20 | 0 | 181 | 0 | 9719995.6005 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
152 | 08/07 08:00:00 | 20 | 0 | 551.0833 | 0 | 9719995.5732 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
153 | 08/07 09:00:00 | 20 | 0 | 747.9167 | 0 | 9719995.5501 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
154 | 08/07 10:00:00 | 20 | 0 | 835.0833 | 0 | 9719995.5352 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
155 | 08/07 11:00:00 | 20 | 0 | 878.0833 | 0 | 9719995.524 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
156 | 08/07 12:00:00 | 20 | 0 | 899.5 | 0 | 9719995.507 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
157 | 08/07 13:00:00 | 20 | 0 | 907 | 0 | 9719995.4807 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
158 | 08/07 14:00:00 | 20 | 0 | 903.6667 | 0 | 9719995.4497 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
159 | 08/07 15:00:00 | 20 | 0 | 887.25 | 0 | 9719995.4189 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
160 | 08/07 16:00:00 | 20 | 0 | 853.5 | 0 | 9719995.3985 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
161 | 08/07 17:00:00 | 20 | 0 | 785.6667 | 0 | 9719995.4011 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
162 | 08/07 18:00:00 | 20 | 0 | 636.6667 | 0 | 9719995.4301 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
163 | 08/07 19:00:00 | 20 | 0 | 330.4167 | 0 | 9719995.4792 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9987
164 | 08/07 20:00:00 | 20 | 0 | 31.5833 | 0 | 9719995.5361 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
165 | 08/07 21:00:00 | 20 | 0 | 0 | 0 | 9719995.5873 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
166 | 08/07 22:00:00 | 20 | 0 | 0 | 0 | 9719995.6236 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
167 | 08/07 23:00:00 | 20 | 0 | 0 | 0 | 9719995.6437 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
168 | 08/07 24:00:00 | 20 | 0 | 0 | 0 | 9719995.6517 | 20 | 0 | 9720000 | 0 | 9720000 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.9988
169 | 08/08 01:00:00 | 20 | 0 | 0 | 4.348 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
170 | 08/08 02:00:00 | 20 | 0 | 0 | 4.3484 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
171 | 08/08 03:00:00 | 20 | 0 | 0 | 4.3406 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
172 | 08/08 04:00:00 | 20 | 0 | 0 | 4.319 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
173 | 08/08 05:00:00 | 20 | 0 | 0 | 4.2845 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
174 | 08/08 06:00:00 | 20 | 0 | 9.8333 | 4.2375 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
175 | 08/08 07:00:00 | 20 | 0 | 181 | 4.178 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
176 | 08/08 08:00:00 | 20 | 0 | 551.0833 | 4.1101 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
177 | 08/08 09:00:00 | 20 | 0 | 747.9167 | 4.0445 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
178 | 08/08 10:00:00 | 20 | 0 | 835.0833 | 3.9897 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
179 | 08/08 11:00:00 | 20 | 0 | 878.0833 | 3.9464 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
180 | 08/08 12:00:00 | 20 | 0 | 899.5 | 3.9131 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
181 | 08/08 13:00:00 | 20 | 0 | 907 | 3.8873 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
182 | 08/08 14:00:00 | 20 | 0 | 903.6667 | 3.8618 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
183 | 08/08 15:00:00 | 20 | 0 | 887.25 | 3.8336 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
184 | 08/08 16:00:00 | 20 | 0 | 853.5 | 3.8092 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
185 | 08/08 17:00:00 | 20 | 0 | 785.6667 | 3.7952 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
186 | 08/08 18:00:00 | 20 | 0 | 636.6667 | 3.7911 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
187 | 08/08 19:00:00 | 20 | 0 | 330.4167 | 3.7935 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
188 | 08/08 20:00:00 | 20 | 0 | 31.5833 | 3.8017 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
189 | 08/08 21:00:00 | 20 | 0 | 0 | 3.8151 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
190 | 08/08 22:00:00 | 20 | 0 | 0 | 3.8325 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
191 | 08/08 23:00:00 | 20 | 0 | 0 | 3.85 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
192 | 08/08 24:00:00 | 20 | 0 | 0 | 3.8613 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
193 | 08/09 01:00:00 | 20 | 0 | 0 | 3.8635 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
194 | 08/09 02:00:00 | 20 | 0 | 0 | 3.8616 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
195 | 08/09 03:00:00 | 20 | 0 | 0 | 3.8675 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
196 | 08/09 04:00:00 | 20 | 0 | 0 | 3.889 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
197 | 08/09 05:00:00 | 20 | 0 | 0 | 3.9259 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
198 | 08/09 06:00:00 | 20 | 0 | 9.8333 | 3.9712 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
199 | 08/09 07:00:00 | 20 | 0 | 181 | 4.0111 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
200 | 08/09 08:00:00 | 20 | 0 | 551.0833 | 4.0339 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
201 | 08/09 09:00:00 | 20 | 0 | 747.9167 | 4.038 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
202 | 08/09 10:00:00 | 20 | 0 | 835.0833 | 4.0303 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
203 | 08/09 11:00:00 | 20 | 0 | 878.0833 | 4.0147 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
204 | 08/09 12:00:00 | 20 | 0 | 899.5 | 3.992 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
205 | 08/09 13:00:00 | 20 | 0 | 907 | 3.9636 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
206 | 08/09 14:00:00 | 20 | 0 | 903.6667 | 3.9282 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
207 | 08/09 15:00:00 | 20 | 0 | 887.25 | 3.8812 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
208 | 08/09 16:00:00 | 20 | 0 | 853.5 | 3.8225 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
209 | 08/09 17:00:00 | 20 | 0 | 785.6667 | 3.7557 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
210 | 08/09 18:00:00 | 20 | 0 | 636.6667 | 3.6861 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
211 | 08/09 19:00:00 | 20 | 0 | 330.4167 | 3.622 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
212 | 08/09 20:00:00 | 20 | 0 | 31.5833 | 3.5729 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
213 | 08/09 21:00:00 | 20 | 0 | 0 | 3.5443 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
214 | 08/09 22:00:00 | 20 | 0 | 0 | 3.5334 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
215 | 08/09 23:00:00 | 20 | 0 | 0 | 3.5335 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
216 | 08/09 24:00:00 | 20 | 0 | 0 | 3.5365 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
217 | 08/10 01:00:00 | 20 | 0 | 0 | 3.5354 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
218 | 08/10 02:00:00 | 20 | 0 | 0 | 3.5228 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
219 | 08/10 03:00:00 | 20 | 0 | 0 | 3.496 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
220 | 08/10 04:00:00 | 20 | 0 | 0 | 3.4588 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
221 | 08/10 05:00:00 | 20 | 0 | 0 | 3.4169 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
222 | 08/10 06:00:00 | 20 | 0 | 9.8333 | 3.3782 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
223 | 08/10 07:00:00 | 20 | 0 | 181 | 3.3501 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
224 | 08/10 08:00:00 | 20 | 0 | 551.0833 | 3.3358 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
225 | 08/10 09:00:00 | 20 | 0 | 747.9167 | 3.3337 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
226 | 08/10 10:00:00 | 20 | 0 | 835.0833 | 3.3396 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
227 | 08/10 11:00:00 | 20 | 0 | 878.0833 | 3.3497 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
228 | 08/10 12:00:00 | 20 | 0 | 899.5 | 3.3617 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
229 | 08/10 13:00:00 | 20 | 0 | 907 | 3.3734 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
230 | 08/10 14:00:00 | 20 | 0 | 903.6667 | 3.3847 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
231 | 08/10 15:00:00 | 20 | 0 | 887.25 | 3.4027 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
232 | 08/10 16:00:00 | 20 | 0 | 853.5 | 3.4384 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
233 | 08/10 17:00:00 | 20 | 0 | 785.6667 | 3.4913 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
234 | 08/10 18:00:00 | 20 | 0 | 636.6667 | 3.547 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
235 | 08/10 19:00:00 | 20 | 0 | 330.4167 | 3.5929 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
236 | 08/10 20:00:00 | 20 | 0 | 31.5833 | 3.621 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
237 | 08/10 21:00:00 | 20 | 0 | 0 | 3.6333 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
238 | 08/10 22:00:00 | 20 | 0 | 0 | 3.6398 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
239 | 08/10 23:00:00 | 20 | 0 | 0 | 3.6479 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
240 | 08/10 24:00:00 | 20 | 0 | 0 | 3.6613 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
241 | 08/11 01:00:00 | 20 | 0 | 0 | 3.6822 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
242 | 08/11 02:00:00 | 20 | 0 | 0 | 3.7105 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
243 | 08/11 03:00:00 | 20 | 0 | 0 | 3.7419 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
244 | 08/11 04:00:00 | 20 | 0 | 0 | 3.7686 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
245 | 08/11 05:00:00 | 20 | 0 | 0 | 3.7878 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
246 | 08/11 06:00:00 | 20 | 0 | 0 | 3.8016 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
247 | 08/11 07:00:00 | 20 | 0 | 181 | 3.8099 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
248 | 08/11 08:00:00 | 20 | 0 | 551.0833 | 3.8064 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
249 | 08/11 09:00:00 | 20 | 0 | 747.9167 | 3.7864 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
250 | 08/11 10:00:00 | 20 | 0 | 835.0833 | 3.7544 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
251 | 08/11 11:00:00 | 20 | 0 | 878.0833 | 3.7179 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
252 | 08/11 12:00:00 | 20 | 0 | 899.5 | 3.6834 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
253 | 08/11 13:00:00 | 20 | 0 | 907 | 3.6574 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
254 | 08/11 14:00:00 | 20 | 0 | 903.6667 | 3.6434 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
255 | 08/11 15:00:00 | 20 | 0 | 887.25 | 3.6387 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
256 | 08/11 16:00:00 | 20 | 0 | 853.5 | 3.6393 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
257 | 08/11 17:00:00 | 20 | 0 | 785.6667 | 3.6444 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
258 | 08/11 18:00:00 | 20 | 0 | 636.6667 | 3.6525 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
259 | 08/11 19:00:00 | 20 | 0 | 330.4167 | 3.6638 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
260 | 08/11 20:00:00 | 20 | 0 | 31.5833 | 3.6856 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
261 | 08/11 21:00:00 | 20 | 0 | 0 | 3.7316 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
262 | 08/11 22:00:00 | 20 | 0 | 0 | 3.8079 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
263 | 08/11 23:00:00 | 20 | 0 | 0 | 3.9027 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
264 | 08/11 24:00:00 | 20 | 0 | 0 | 4.0003 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
265 | 08/12 01:00:00 | 20 | 0 | 0 | 4.0938 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
266 | 08/12 02:00:00 | 20 | 0 | 0 | 4.1801 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
267 | 08/12 03:00:00 | 20 | 0 | 0 | 4.2558 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
268 | 08/12 04:00:00 | 20 | 0 | 0 | 4.317 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
269 | 08/12 05:00:00 | 20 | 0 | 0 | 4.359 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
270 | 08/12 06:00:00 | 20 | 0 | 0 | 4.378 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
271 | 08/12 07:00:00 | 20 | 0 | 181 | 4.3714 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
272 | 08/12 08:00:00 | 20 | 0 | 551.0833 | 4.3377 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
273 | 08/12 09:00:00 | 20 | 0 | 747.9167 | 4.2788 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
274 | 08/12 10:00:00 | 20 | 0 | 835.0833 | 4.2044 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
275 | 08/12 11:00:00 | 20 | 0 | 878.0833 | 4.1299 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
276 | 08/12 12:00:00 | 20 | 0 | 899.5 | 4.0683 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
277 | 08/12 13:00:00 | 20 | 0 | 907 | 4.0191 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
278 | 08/12 14:00:00 | 20 | 0 | 903.6667 | 3.9731 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
279 | 08/12 15:00:00 | 20 | 0 | 887.25 | 3.9215 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
280 | 08/12 16:00:00 | 20 | 0 | 853.5 | 3.8596 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
281 | 08/12 17:00:00 | 20 | 0 | 785.6667 | 3.7921 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
282 | 08/12 18:00:00 | 20 | 0 | 636.6667 | 3.7294 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
283 | 08/12 19:00:00 | 20 | 0 | 330.4167 | 3.6766 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
284 | 08/12 20:00:00 | 20 | 0 | 31.5833 | 3.6389 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
285 | 08/12 21:00:00 | 20 | 0 | 0 | 3.6244 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
286 | 08/12 22:00:00 | 20 | 0 | 0 | 3.6349 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
287 | 08/12 23:00:00 | 20 | 0 | 0 | 3.6669 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
288 | 08/12 24:00:00 | 20 | 0 | 0 | 3.7152 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
289 | 08/13 01:00:00 | 20 | 0 | 0 | 3.7777 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
290 | 08/13 02:00:00 | 20 | 0 | 0 | 3.8522 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
291 | 08/13 03:00:00 | 20 | 0 | 0 | 3.932 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
292 | 08/13 04:00:00 | 20 | 0 | 0 | 4.0065 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
293 | 08/13 05:00:00 | 20 | 0 | 0 | 4.0643 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
294 | 08/13 06:00:00 | 20 | 0 | 0 | 4.1008 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
295 | 08/13 07:00:00 | 20 | 0 | 181 | 4.1221 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
296 | 08/13 08:00:00 | 20 | 0 | 551.0833 | 4.1355 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
297 | 08/13 09:00:00 | 20 | 0 | 747.9167 | 4.1462 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
298 | 08/13 10:00:00 | 20 | 0 | 835.0833 | 4.1555 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
299 | 08/13 11:00:00 | 20 | 0 | 878.0833 | 4.1643 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
300 | 08/13 12:00:00 | 20 | 0 | 899.5 | 4.1711 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
301 | 08/13 13:00:00 | 20 | 0 | 907 | 4.1695 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
302 | 08/13 14:00:00 | 20 | 0 | 903.6667 | 4.1572 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
303 | 08/13 15:00:00 | 20 | 0 | 887.25 | 4.1428 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
304 | 08/13 16:00:00 | 20 | 0 | 853.5 | 4.1346 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
305 | 08/13 17:00:00 | 20 | 0 | 785.6667 | 4.1306 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
306 | 08/13 18:00:00 | 20 | 0 | 636.6667 | 4.1262 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
307 | 08/13 19:00:00 | 20 | 0 | 330.4167 | 4.12 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
308 | 08/13 20:00:00 | 20 | 0 | 31.5833 | 4.1107 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
309 | 08/13 21:00:00 | 20 | 0 | 0 | 4.1001 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
310 | 08/13 22:00:00 | 20 | 0 | 0 | 4.0947 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
311 | 08/13 23:00:00 | 20 | 0 | 0 | 4.0976 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
312 | 08/13 24:00:00 | 20 | 0 | 0 | 4.1041 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
313 | 08/14 01:00:00 | 20 | 0 | 0 | 4.1069 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
314 | 08/14 02:00:00 | 20 | 0 | 0 | 4.1052 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
315 | 08/14 03:00:00 | 20 | 0 | 0 | 4.0979 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
316 | 08/14 04:00:00 | 20 | 0 | 0 | 4.0842 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
317 | 08/14 05:00:00 | 20 | 0 | 0 | 4.0696 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
318 | 08/14 06:00:00 | 20 | 0 | 0 | 4.0598 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
319 | 08/14 07:00:00 | 20 | 0 | 181 | 4.0573 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
320 | 08/14 08:00:00 | 20 | 0 | 551.0833 | 4.0657 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
321 | 08/14 09:00:00 | 20 | 0 | 747.9167 | 4.0836 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
322 | 08/14 10:00:00 | 20 | 0 | 835.0833 | 4.1057 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
323 | 08/14 11:00:00 | 20 | 0 | 878.0833 | 4.1275 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
324 | 08/14 12:00:00 | 20 | 0 | 899.5 | 4.1511 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
325 | 08/14 13:00:00 | 20 | 0 | 907 | 4.1835 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
326 | 08/14 14:00:00 | 20 | 0 | 903.6667 | 4.2305 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
327 | 08/14 15:00:00 | 20 | 0 | 887.25 | 4.2896 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
328 | 08/14 16:00:00 | 20 | 0 | 853.5 | 4.3497 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
329 | 08/14 17:00:00 | 20 | 0 | 785.6667 | 4.3983 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
330 | 08/14 18:00:00 | 20 | 0 | 636.6667 | 4.4264 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
331 | 08/14 19:00:00 | 20 | 0 | 330.4167 | 4.4324 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
332 | 08/14 20:00:00 | 20 | 0 | 31.5833 | 4.4223 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
333 | 08/14 21:00:00 | 20 | 0 | 0 | 4.4034 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
334 | 08/14 22:00:00 | 20 | 0 | 0 | 4.3806 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
335 | 08/14 23:00:00 | 20 | 0 | 0 | 4.3566 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0
| 08/14 24:00:00 | 20 | 0 | 0 | 4.334 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 20 | 20 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 335 hrs | Average >>> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 453599.7988
[13 empty] | 335 hrs | Average-all surfaces >>> | [7 empty] | 2.0507 | 2699.999
[13 empty] | 168 hrs | Average >>> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 168 hrs | Average-all surfaces >>> | [7 empty] | 2.0507

## EPlus 100 Rad
EnergyPlus Results for ASHRAE 1052RP Analytical Test IntHeatGain
Step change in internal load
2700 W for 168 hours, 100% radiative
Hour | Date/Time | Environment:Outdoor Dry Bulb [C](Hourly) | Environment:Diffuse Solar [W/m2](Hourly) | Environment:Direct Solar [W/m2](Hourly) | ZONE ONE:Zone/Sys Sensible Heating Energy[J](Hourly) | ZONE ONE:Zone/Sys Sensible Cooling Energy[J](Hourly) | ZONE ONE:Mean Air Temperature[C](Hourly) | ZONE ONE:Zone-Total Radiant Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Convective Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Lost Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Radiant Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Convective Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Lost Heat Gain[J](Hourly) | EnergyPlus - 100% Radiative | ZONE SURFACE NORTH:Surface Outside Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE NORTH:Surface Ext Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE SOUTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE EAST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE WEST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE CEILING:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE FLOOR:Surface Int Convection Coeff[W/m2-K](Hourly) | EnergyPlus - 100% Radiative
1 | 08/01 01:00:00 | 20 | 0 | 0 | 0 | 2961363.1677 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 24.9523 | 23.9666 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 822.6009
2 | 08/01 02:00:00 | 20 | 0 | 0 | 0 | 4031835.2052 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 26.7425 | 26.5218 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1119.9542
3 | 08/01 03:00:00 | 20 | 0 | 0 | 0 | 4642602.5212 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 27.7639 | 27.6208 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1289.6118
4 | 08/01 04:00:00 | 20 | 0 | 0 | 0 | 5070178.1433 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 28.4789 | 28.3737 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1408.3828
5 | 08/01 05:00:00 | 20 | 0 | 0 | 0 | 5398522.4244 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 29.028 | 28.9448 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1499.5896
6 | 08/01 06:00:00 | 20 | 0 | 9.8333 | 0 | 5666485.2708 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 29.4761 | 29.4067 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1574.0237
7 | 08/01 07:00:00 | 20 | 0 | 181 | 0 | 5895588.4367 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 29.8593 | 29.7989 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1637.6635
8 | 08/01 08:00:00 | 20 | 0 | 551.0833 | 0 | 6098459.443 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 30.1985 | 30.1444 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1694.0165
9 | 08/01 09:00:00 | 20 | 0 | 747.9167 | 0 | 6282686.6477 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 30.5066 | 30.4571 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1745.1907
10 | 08/01 10:00:00 | 20 | 0 | 835.0833 | 0 | 6452897.8497 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 30.7913 | 30.7452 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1792.4716
11 | 08/01 11:00:00 | 20 | 0 | 878.0833 | 0 | 6611962.9987 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 31.0573 | 31.0141 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1836.6564
12 | 08/01 12:00:00 | 20 | 0 | 899.5 | 0 | 6761705.2611 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 31.3077 | 31.2669 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1878.2515
13 | 08/01 13:00:00 | 20 | 0 | 907 | 0 | 6903323.3985 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 31.5445 | 31.5059 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1917.5898
14 | 08/01 14:00:00 | 20 | 0 | 903.6667 | 0 | 7037379.4771 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 31.7687 | 31.7322 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1954.8276
15 | 08/01 15:00:00 | 20 | 0 | 887.25 | 0 | 7164732.9362 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 31.9817 | 31.9469 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1990.2036
16 | 08/01 16:00:00 | 20 | 0 | 853.5 | 0 | 7286040.8186 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 32.1845 | 32.1514 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2023.9002
17 | 08/01 17:00:00 | 20 | 0 | 785.6667 | 0 | 7401529.4573 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 32.3777 | 32.3461 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2055.9804
18 | 08/01 18:00:00 | 20 | 0 | 636.6667 | 0 | 7511504.5224 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 32.5616 | 32.5315 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2086.529
19 | 08/01 19:00:00 | 20 | 0 | 330.4167 | 0 | 7616246.0899 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 32.7367 | 32.7081 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2115.6239
20 | 08/01 20:00:00 | 20 | 0 | 32.4167 | 0 | 7716012.5223 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 32.9036 | 32.8763 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2143.3368
21 | 08/01 21:00:00 | 20 | 0 | 0 | 0 | 7811044.9396 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.0625 | 33.0366 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2169.7347
22 | 08/01 22:00:00 | 20 | 0 | 0 | 0 | 7901570.2932 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.2139 | 33.1892 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2194.8806
23 | 08/01 23:00:00 | 20 | 0 | 0 | 0 | 7987803.3381 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.3581 | 33.3346 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2218.8343
24 | 08/01 24:00:00 | 20 | 0 | 0 | 0 | 8069947.94 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.4955 | 33.473 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2241.6522
25 | 08/02 01:00:00 | 20 | 0 | 0 | 0 | 8148197.9674 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.6263 | 33.605 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2263.3883
26 | 08/02 02:00:00 | 20 | 0 | 0 | 0 | 8222737.9513 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.751 | 33.7306 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2284.0939
27 | 08/02 03:00:00 | 20 | 0 | 0 | 0 | 8293743.6352 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.8697 | 33.8503 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2303.8177
28 | 08/02 04:00:00 | 20 | 0 | 0 | 0 | 8361382.451 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 33.9828 | 33.9644 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2322.6062
29 | 08/02 05:00:00 | 20 | 0 | 0 | 0 | 8425813.9296 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.0906 | 34.073 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2340.5039
30 | 08/02 06:00:00 | 20 | 0 | 9.8333 | 0 | 8487190.0652 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.1932 | 34.1765 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2357.5528
31 | 08/02 07:00:00 | 20 | 0 | 181 | 0 | 8545655.6667 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.291 | 34.275 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2373.7932
32 | 08/02 08:00:00 | 20 | 0 | 551.0833 | 0 | 8601348.7028 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.3841 | 34.3689 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2389.2635
33 | 08/02 09:00:00 | 20 | 0 | 747.9167 | 0 | 8654400.6233 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.4729 | 34.4584 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2404.0002
34 | 08/02 10:00:00 | 20 | 0 | 835.0833 | 0 | 8704936.6541 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.5574 | 34.5436 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2418.038
35 | 08/02 11:00:00 | 20 | 0 | 878.0833 | 0 | 8753076.0796 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.6379 | 34.6247 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2431.41
36 | 08/02 12:00:00 | 20 | 0 | 899.5 | 0 | 8798932.5388 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.7146 | 34.702 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2444.1479
37 | 08/02 13:00:00 | 20 | 0 | 907 | 0 | 8842614.2922 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.7876 | 34.7757 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2456.2817
38 | 08/02 14:00:00 | 20 | 0 | 903.6667 | 0 | 8884224.4649 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.8572 | 34.8458 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2467.8401
39 | 08/02 15:00:00 | 20 | 0 | 887.25 | 0 | 8923861.2805 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.9235 | 34.9127 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2478.8504
40 | 08/02 16:00:00 | 20 | 0 | 853.5 | 0 | 8961618.3041 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 34.9866 | 34.9763 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2489.3384
41 | 08/02 17:00:00 | 20 | 0 | 785.6667 | 0 | 8997444.375 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.0465 | 35.0367 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2499.2901
42 | 08/02 18:00:00 | 20 | 0 | 636.6667 | 0 | 9031446.1758 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.1034 | 35.0942 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2508.735
43 | 08/02 19:00:00 | 20 | 0 | 330.4167 | 0 | 9063898.6355 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.1577 | 35.1488 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2517.7496
44 | 08/02 20:00:00 | 20 | 0 | 32.4167 | 0 | 9094922.992 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.2096 | 35.2011 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2526.3675
45 | 08/02 21:00:00 | 20 | 0 | 0 | 0 | 9124503.8766 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.259 | 35.2509 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2534.5844
46 | 08/02 22:00:00 | 20 | 0 | 0 | 0 | 9152696.6138 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.3062 | 35.2985 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2542.4157
47 | 08/02 23:00:00 | 20 | 0 | 0 | 0 | 9179561.1998 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.3511 | 35.3438 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2549.8781
48 | 08/02 24:00:00 | 20 | 0 | 0 | 0 | 9205157.4484 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.3939 | 35.3869 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2556.9882
49 | 08/03 01:00:00 | 20 | 0 | 0 | 0 | 9229543.6524 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.4347 | 35.428 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2563.7621
50 | 08/03 02:00:00 | 20 | 0 | 0 | 0 | 9252776.0779 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.4735 | 35.4672 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2570.2156
51 | 08/03 03:00:00 | 20 | 0 | 0 | 0 | 9274908.7533 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.5105 | 35.5045 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2576.3635
52 | 08/03 04:00:00 | 20 | 0 | 0 | 0 | 9295993.4105 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.5458 | 35.54 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2582.2204
53 | 08/03 05:00:00 | 20 | 0 | 0 | 0 | 9316079.4992 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.5794 | 35.5739 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2587.7999
54 | 08/03 06:00:00 | 20 | 0 | 9.8333 | 0 | 9335214.2193 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.6114 | 35.6062 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2593.1151
55 | 08/03 07:00:00 | 20 | 0 | 181 | 0 | 9353442.5769 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.6419 | 35.6369 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2598.1785
56 | 08/03 08:00:00 | 20 | 0 | 551.0833 | 0 | 9370807.4577 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.6709 | 35.6662 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2603.0021
57 | 08/03 09:00:00 | 20 | 0 | 747.9167 | 0 | 9387349.7287 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.6986 | 35.6941 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2607.5971
58 | 08/03 10:00:00 | 20 | 0 | 835.0833 | 0 | 9403108.3354 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.7249 | 35.7206 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2611.9745
59 | 08/03 11:00:00 | 20 | 0 | 878.0833 | 0 | 9418120.3796 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.75 | 35.7459 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2616.1445
60 | 08/03 12:00:00 | 20 | 0 | 899.5 | 0 | 9432421.2214 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.774 | 35.77 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2620.117
61 | 08/03 13:00:00 | 20 | 0 | 907 | 0 | 9446044.5715 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.7967 | 35.793 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2623.9013
62 | 08/03 14:00:00 | 20 | 0 | 903.6667 | 0 | 9459022.548 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.8184 | 35.8149 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2627.5063
63 | 08/03 15:00:00 | 20 | 0 | 887.25 | 0 | 9471385.7341 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.8391 | 35.8357 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2630.9405
64 | 08/03 16:00:00 | 20 | 0 | 853.5 | 0 | 9483163.2566 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.8588 | 35.8556 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2634.212
65 | 08/03 17:00:00 | 20 | 0 | 785.6667 | 0 | 9494382.8552 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.8776 | 35.8745 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2637.3286
66 | 08/03 18:00:00 | 20 | 0 | 636.6667 | 0 | 9505070.9538 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.8954 | 35.8925 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2640.2975
67 | 08/03 19:00:00 | 20 | 0 | 330.4167 | 0 | 9515252.727 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9125 | 35.9097 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2643.1258
68 | 08/03 20:00:00 | 20 | 0 | 32.4167 | 0 | 9524952.1528 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9287 | 35.926 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2645.82
69 | 08/03 21:00:00 | 20 | 0 | 0 | 0 | 9534044.8845 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9439 | 35.9414 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2648.3458
70 | 08/03 22:00:00 | 20 | 0 | 0 | 0 | 9542702.593 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9584 | 35.956 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2650.7507
71 | 08/03 23:00:00 | 20 | 0 | 0 | 0 | 9551046.0627 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9723 | 35.9701 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2653.0684
72 | 08/03 24:00:00 | 20 | 0 | 0 | 0 | 9558958.174 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9856 | 35.9835 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2655.2662
73 | 08/04 01:00:00 | 20 | 0 | 0 | 0 | 9566509.9172 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 35.9982 | 35.9961 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2657.3639
74 | 08/04 02:00:00 | 20 | 0 | 0 | 0 | 9573539.5275 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0099 | 36.008 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2659.3165
75 | 08/04 03:00:00 | 20 | 0 | 0 | 0 | 9580376.6047 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0214 | 36.0195 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2661.2157
76 | 08/04 04:00:00 | 20 | 0 | 0 | 0 | 9586923.0756 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0323 | 36.0305 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2663.0342
77 | 08/04 05:00:00 | 20 | 0 | 0 | 0 | 9593174.799 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0428 | 36.0411 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2664.7708
78 | 08/04 06:00:00 | 20 | 0 | 9.8333 | 0 | 9599139.4191 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0528 | 36.0511 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2666.4276
79 | 08/04 07:00:00 | 20 | 0 | 181 | 0 | 9604827.348 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0623 | 36.0607 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2668.0076
80 | 08/04 08:00:00 | 20 | 0 | 551.0833 | 0 | 9610249.8679 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0713 | 36.0699 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2669.5139
81 | 08/04 09:00:00 | 20 | 0 | 747.9167 | 0 | 9615418.4465 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.08 | 36.0786 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2670.9496
82 | 08/04 10:00:00 | 20 | 0 | 835.0833 | 0 | 9620344.4264 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0882 | 36.0869 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2672.3179
83 | 08/04 11:00:00 | 20 | 0 | 878.0833 | 0 | 9625038.8762 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.0961 | 36.0948 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2673.6219
84 | 08/04 12:00:00 | 20 | 0 | 899.5 | 0 | 9629512.5 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1036 | 36.1023 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2674.8646
85 | 08/04 13:00:00 | 20 | 0 | 907 | 0 | 9633775.5693 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1107 | 36.1095 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2676.0488
86 | 08/04 14:00:00 | 20 | 0 | 903.6667 | 0 | 9637837.901 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1175 | 36.1164 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2677.1772
87 | 08/04 15:00:00 | 20 | 0 | 887.25 | 0 | 9641708.8893 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1239 | 36.1229 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2678.2525
88 | 08/04 16:00:00 | 20 | 0 | 853.5 | 0 | 9645397.5233 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1301 | 36.1291 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2679.2771
89 | 08/04 17:00:00 | 20 | 0 | 785.6667 | 0 | 9648912.3819 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.136 | 36.135 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2680.2534
90 | 08/04 18:00:00 | 20 | 0 | 636.6667 | 0 | 9652261.6421 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1416 | 36.1407 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2681.1838
91 | 08/04 19:00:00 | 20 | 0 | 330.4167 | 0 | 9655453.0912 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1469 | 36.1461 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2682.0703
92 | 08/04 20:00:00 | 20 | 0 | 32.4167 | 0 | 9658494.1491 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.152 | 36.1512 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2682.915
93 | 08/04 21:00:00 | 20 | 0 | 0 | 0 | 9661391.8895 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1569 | 36.1561 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2683.72
94 | 08/04 22:00:00 | 20 | 0 | 0 | 0 | 9664153.0611 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1615 | 36.1607 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2684.487
95 | 08/04 23:00:00 | 20 | 0 | 0 | 0 | 9666784.1078 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1659 | 36.1652 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2685.2178
96 | 08/04 24:00:00 | 20 | 0 | 0 | 0 | 9669291.1714 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1701 | 36.1694 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2685.9142
97 | 08/05 01:00:00 | 20 | 0 | 0 | 0 | 9671680.1079 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1741 | 36.1734 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2686.5778
98 | 08/05 02:00:00 | 20 | 0 | 0 | 0 | 9673956.5002 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1779 | 36.1773 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2687.2101
99 | 08/05 03:00:00 | 20 | 0 | 0 | 0 | 9676125.6649 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1815 | 36.1809 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2687.8127
100 | 08/05 04:00:00 | 20 | 0 | 0 | 0 | 9678192.671 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.185 | 36.1844 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2688.3869
101 | 08/05 05:00:00 | 20 | 0 | 0 | 0 | 9680162.3416 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1883 | 36.1877 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2688.934
102 | 08/05 06:00:00 | 20 | 0 | 9.8333 | 0 | 9682039.2502 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1914 | 36.1909 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2689.4553
103 | 08/05 07:00:00 | 20 | 0 | 181 | 0 | 9683827.7403 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1944 | 36.1939 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2689.9522
104 | 08/05 08:00:00 | 20 | 0 | 551.0833 | 0 | 9685531.943 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.1972 | 36.1968 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2690.4255
105 | 08/05 09:00:00 | 20 | 0 | 747.9167 | 0 | 9687155.8025 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2 | 36.1995 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2690.8766
106 | 08/05 10:00:00 | 20 | 0 | 835.0833 | 0 | 9688703.0993 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2025 | 36.2021 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2691.3064
107 | 08/05 11:00:00 | 20 | 0 | 878.0833 | 0 | 9690177.4478 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.205 | 36.2046 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2691.716
108 | 08/05 12:00:00 | 20 | 0 | 899.5 | 0 | 9691582.2894 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2074 | 36.207 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.1062
109 | 08/05 13:00:00 | 20 | 0 | 907 | 0 | 9692920.9032 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2096 | 36.2092 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.478
110 | 08/05 14:00:00 | 20 | 0 | 903.6667 | 0 | 9694196.4192 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2117 | 36.2114 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.8323
111 | 08/05 15:00:00 | 20 | 0 | 887.25 | 0 | 9695411.823 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2138 | 36.2134 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.17
112 | 08/05 16:00:00 | 20 | 0 | 853.5 | 0 | 9696569.9648 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2157 | 36.2154 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.4917
113 | 08/05 17:00:00 | 20 | 0 | 785.6667 | 0 | 9697673.5676 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2175 | 36.2172 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.7982
114 | 08/05 18:00:00 | 20 | 0 | 636.6667 | 0 | 9698725.2165 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2193 | 36.219 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.0903
115 | 08/05 19:00:00 | 20 | 0 | 330.4167 | 0 | 9699727.3624 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.221 | 36.2207 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.3687
116 | 08/05 20:00:00 | 20 | 0 | 32.4167 | 0 | 9700682.3332 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2226 | 36.2223 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.634
117 | 08/05 21:00:00 | 20 | 0 | 0 | 0 | 9701592.3382 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2241 | 36.2238 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.8868
118 | 08/05 22:00:00 | 20 | 0 | 0 | 0 | 9702459.4785 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2255 | 36.2253 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.1276
119 | 08/05 23:00:00 | 20 | 0 | 0 | 0 | 9703285.7514 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2269 | 36.2267 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.3572
120 | 08/05 24:00:00 | 20 | 0 | 0 | 0 | 9704073.0606 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2282 | 36.228 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.5759
121 | 08/06 01:00:00 | 20 | 0 | 0 | 0 | 9704823.2409 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2295 | 36.2293 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.7842
122 | 08/06 02:00:00 | 20 | 0 | 0 | 0 | 9705538.0664 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2307 | 36.2305 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.9828
123 | 08/06 03:00:00 | 20 | 0 | 0 | 0 | 9706219.2163 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2318 | 36.2316 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.172
124 | 08/06 04:00:00 | 20 | 0 | 0 | 0 | 9706868.2565 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2329 | 36.2327 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.3523
125 | 08/06 05:00:00 | 20 | 0 | 0 | 0 | 9707486.6683 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.234 | 36.2338 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.5241
126 | 08/06 06:00:00 | 20 | 0 | 9.8333 | 0 | 9708075.8921 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2349 | 36.2348 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.6877
127 | 08/06 07:00:00 | 20 | 0 | 181 | 0 | 9708637.3294 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2359 | 36.2357 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.8437
128 | 08/06 08:00:00 | 20 | 0 | 551.0833 | 0 | 9709172.3111 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2368 | 36.2366 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.9923
129 | 08/06 09:00:00 | 20 | 0 | 747.9167 | 0 | 9709682.0836 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2376 | 36.2375 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.1339
130 | 08/06 10:00:00 | 20 | 0 | 835.0833 | 0 | 9710167.8206 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2384 | 36.2383 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.2688
131 | 08/06 11:00:00 | 20 | 0 | 878.0833 | 0 | 9710630.6497 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2392 | 36.2391 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.3974
132 | 08/06 12:00:00 | 20 | 0 | 899.5 | 0 | 9711071.6695 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2399 | 36.2398 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.5199
133 | 08/06 13:00:00 | 20 | 0 | 907 | 0 | 9711491.9315 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2406 | 36.2405 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.6366
134 | 08/06 14:00:00 | 20 | 0 | 903.6667 | 0 | 9711892.4201 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2413 | 36.2412 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.7479
135 | 08/06 15:00:00 | 20 | 0 | 887.25 | 0 | 9712274.0537 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.242 | 36.2419 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.8539
136 | 08/06 16:00:00 | 20 | 0 | 853.5 | 0 | 9712637.7043 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2426 | 36.2425 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.9549
137 | 08/06 17:00:00 | 20 | 0 | 785.6667 | 0 | 9712984.2126 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2431 | 36.243 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.0512
138 | 08/06 18:00:00 | 20 | 0 | 636.6667 | 0 | 9713314.3859 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2437 | 36.2436 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.1429
139 | 08/06 19:00:00 | 20 | 0 | 330.4167 | 0 | 9713629.0043 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2442 | 36.2441 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.2303
140 | 08/06 20:00:00 | 20 | 0 | 32.4167 | 0 | 9713928.8237 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2447 | 36.2446 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.3136
141 | 08/06 21:00:00 | 20 | 0 | 0 | 0 | 9714214.5716 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2452 | 36.2451 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.3929
142 | 08/06 22:00:00 | 20 | 0 | 0 | 0 | 9714486.9286 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2457 | 36.2456 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.4686
143 | 08/06 23:00:00 | 20 | 0 | 0 | 0 | 9714746.52 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2461 | 36.246 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.5407
144 | 08/06 24:00:00 | 20 | 0 | 0 | 0 | 9714993.9242 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2465 | 36.2464 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.6094
145 | 08/07 01:00:00 | 20 | 0 | 0 | 0 | 9715229.6855 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2469 | 36.2468 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.6749
146 | 08/07 02:00:00 | 20 | 0 | 0 | 0 | 9715454.334 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2473 | 36.2472 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.7373
147 | 08/07 03:00:00 | 20 | 0 | 0 | 0 | 9715668.3762 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2476 | 36.2476 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.7968
148 | 08/07 04:00:00 | 20 | 0 | 0 | 0 | 9715872.2896 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.248 | 36.2479 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.8534
149 | 08/07 05:00:00 | 20 | 0 | 0 | 0 | 9716066.5335 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2483 | 36.2482 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.9074
150 | 08/07 06:00:00 | 20 | 0 | 9.8333 | 0 | 9716251.5815 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2486 | 36.2486 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.9588
151 | 08/07 07:00:00 | 20 | 0 | 181 | 0 | 9716427.9158 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2489 | 36.2489 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.0078
152 | 08/07 08:00:00 | 20 | 0 | 551.0833 | 0 | 9716595.9847 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2492 | 36.2491 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.0544
153 | 08/07 09:00:00 | 20 | 0 | 747.9167 | 0 | 9716756.1928 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2495 | 36.2494 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.0989
154 | 08/07 10:00:00 | 20 | 0 | 835.0833 | 0 | 9716908.909 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2497 | 36.2497 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.1414
155 | 08/07 11:00:00 | 20 | 0 | 878.0833 | 0 | 9717054.4689 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.25 | 36.2499 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.1818
156 | 08/07 12:00:00 | 20 | 0 | 899.5 | 0 | 9717193.195 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2502 | 36.2501 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.2203
157 | 08/07 13:00:00 | 20 | 0 | 907 | 0 | 9717325.4057 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2504 | 36.2504 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.2571
158 | 08/07 14:00:00 | 20 | 0 | 903.6667 | 0 | 9717451.3959 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2506 | 36.2506 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.2921
159 | 08/07 15:00:00 | 20 | 0 | 887.25 | 0 | 9717571.4313 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2508 | 36.2508 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3254
160 | 08/07 16:00:00 | 20 | 0 | 853.5 | 0 | 9717685.7801 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.251 | 36.251 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3572
161 | 08/07 17:00:00 | 20 | 0 | 785.6667 | 0 | 9717794.7183 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2512 | 36.2512 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3874
162 | 08/07 18:00:00 | 20 | 0 | 636.6667 | 0 | 9717898.5022 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2514 | 36.2513 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4163
163 | 08/07 19:00:00 | 20 | 0 | 330.4167 | 0 | 9717997.3648 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2515 | 36.2515 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4437
164 | 08/07 20:00:00 | 20 | 0 | 31.5833 | 0 | 9718091.5323 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2517 | 36.2517 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4699
165 | 08/07 21:00:00 | 20 | 0 | 0 | 0 | 9718181.2378 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2518 | 36.2518 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4948
166 | 08/07 22:00:00 | 20 | 0 | 0 | 0 | 9718266.7095 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.252 | 36.252 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5185
167 | 08/07 23:00:00 | 20 | 0 | 0 | 0 | 9718348.1479 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2521 | 36.2521 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5412
168 | 08/07 24:00:00 | 20 | 0 | 0 | 0 | 9718425.727 | 20 | 9720000 | 0 | 9720000 | 0 | 0 | 36.2522 | 36.2522 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5627
169 | 08/08 01:00:00 | 20 | 0 | 0 | 0 | 6757138.3398 | 20 | 0 | 0 | 0 | 0 | 0 | 31.3 | 32.2857 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1876.9829
170 | 08/08 02:00:00 | 20 | 0 | 0 | 0 | 5686738.4296 | 20 | 0 | 0 | 0 | 0 | 0 | 29.51 | 29.7307 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1579.6496
171 | 08/08 03:00:00 | 20 | 0 | 0 | 0 | 5076038.8587 | 20 | 0 | 0 | 0 | 0 | 0 | 28.4887 | 28.6318 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1410.0108
172 | 08/08 04:00:00 | 20 | 0 | 0 | 0 | 4648527.3875 | 20 | 0 | 0 | 0 | 0 | 0 | 27.7738 | 27.879 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1291.2576
173 | 08/08 05:00:00 | 20 | 0 | 0 | 0 | 4320244.1037 | 20 | 0 | 0 | 0 | 0 | 0 | 27.2248 | 27.308 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1200.0678
174 | 08/08 06:00:00 | 20 | 0 | 9.8333 | 0 | 4052339.319 | 20 | 0 | 0 | 0 | 0 | 0 | 26.7768 | 26.8462 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1125.6498
175 | 08/08 07:00:00 | 20 | 0 | 181 | 0 | 3823291.4551 | 20 | 0 | 0 | 0 | 0 | 0 | 26.3937 | 26.4541 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1062.0254
176 | 08/08 08:00:00 | 20 | 0 | 551.0833 | 0 | 3620473.1218 | 20 | 0 | 0 | 0 | 0 | 0 | 26.0546 | 26.1087 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1005.687
177 | 08/08 09:00:00 | 20 | 0 | 747.9167 | 0 | 3436296.0823 | 20 | 0 | 0 | 0 | 0 | 0 | 25.7466 | 25.7961 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 954.5267
178 | 08/08 10:00:00 | 20 | 0 | 835.0833 | 0 | 3266132.658 | 20 | 0 | 0 | 0 | 0 | 0 | 25.462 | 25.508 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 907.2591
179 | 08/08 11:00:00 | 20 | 0 | 878.0833 | 0 | 3107113.0165 | 20 | 0 | 0 | 0 | 0 | 0 | 25.1961 | 25.2392 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 863.0869
180 | 08/08 12:00:00 | 20 | 0 | 899.5 | 0 | 2957414.1135 | 20 | 0 | 0 | 0 | 0 | 0 | 24.9457 | 24.9865 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 821.5039
181 | 08/08 13:00:00 | 20 | 0 | 907 | 0 | 2815837.3051 | 20 | 0 | 0 | 0 | 0 | 0 | 24.709 | 24.7475 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 782.177
182 | 08/08 14:00:00 | 20 | 0 | 903.6667 | 0 | 2681820.5523 | 20 | 0 | 0 | 0 | 0 | 0 | 24.4848 | 24.5213 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 744.9502
183 | 08/08 15:00:00 | 20 | 0 | 887.25 | 0 | 2554504.5793 | 20 | 0 | 0 | 0 | 0 | 0 | 24.2719 | 24.3067 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 709.5846
184 | 08/08 16:00:00 | 20 | 0 | 853.5 | 0 | 2433232.471 | 20 | 0 | 0 | 0 | 0 | 0 | 24.0691 | 24.1022 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 675.8979
185 | 08/08 17:00:00 | 20 | 0 | 785.6667 | 0 | 2317777.913 | 20 | 0 | 0 | 0 | 0 | 0 | 23.876 | 23.9076 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 643.8272
186 | 08/08 18:00:00 | 20 | 0 | 636.6667 | 0 | 2207835.3011 | 20 | 0 | 0 | 0 | 0 | 0 | 23.6922 | 23.7222 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 613.2876
187 | 08/08 19:00:00 | 20 | 0 | 330.4167 | 0 | 2103124.63 | 20 | 0 | 0 | 0 | 0 | 0 | 23.5171 | 23.5457 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 584.2013
188 | 08/08 20:00:00 | 20 | 0 | 31.5833 | 0 | 2003387.5927 | 20 | 0 | 0 | 0 | 0 | 0 | 23.3503 | 23.3775 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 556.4966
189 | 08/08 21:00:00 | 20 | 0 | 0 | 0 | 1908383.1274 | 20 | 0 | 0 | 0 | 0 | 0 | 23.1914 | 23.2174 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 530.1064
190 | 08/08 22:00:00 | 20 | 0 | 0 | 0 | 1817884.3543 | 20 | 0 | 0 | 0 | 0 | 0 | 23.0401 | 23.0648 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 504.9679
191 | 08/08 23:00:00 | 20 | 0 | 0 | 0 | 1731676.5955 | 20 | 0 | 0 | 0 | 0 | 0 | 22.8959 | 22.9194 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 481.0213
192 | 08/08 24:00:00 | 20 | 0 | 0 | 0 | 1649556.0714 | 20 | 0 | 0 | 0 | 0 | 0 | 22.7586 | 22.781 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 458.21
193 | 08/09 01:00:00 | 20 | 0 | 0 | 0 | 1571328.9893 | 20 | 0 | 0 | 0 | 0 | 0 | 22.6278 | 22.6491 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 436.4803
194 | 08/09 02:00:00 | 20 | 0 | 0 | 0 | 1496810.8719 | 20 | 0 | 0 | 0 | 0 | 0 | 22.5031 | 22.5235 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 415.7808
195 | 08/09 03:00:00 | 20 | 0 | 0 | 0 | 1425826.0192 | 20 | 0 | 0 | 0 | 0 | 0 | 22.3844 | 22.4038 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 396.0628
196 | 08/09 04:00:00 | 20 | 0 | 0 | 0 | 1358207.0416 | 20 | 0 | 0 | 0 | 0 | 0 | 22.2713 | 22.2898 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 377.2797
197 | 08/09 05:00:00 | 20 | 0 | 0 | 0 | 1293794.4574 | 20 | 0 | 0 | 0 | 0 | 0 | 22.1636 | 22.1812 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 359.3873
198 | 08/09 06:00:00 | 20 | 0 | 9.8333 | 0 | 1232436.3245 | 20 | 0 | 0 | 0 | 0 | 0 | 22.061 | 22.0778 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 342.3434
199 | 08/09 07:00:00 | 20 | 0 | 181 | 0 | 1173987.8867 | 20 | 0 | 0 | 0 | 0 | 0 | 21.9633 | 21.9792 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 326.1077
200 | 08/09 08:00:00 | 20 | 0 | 551.0833 | 0 | 1118311.2374 | 20 | 0 | 0 | 0 | 0 | 0 | 21.8702 | 21.8854 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 310.642
201 | 08/09 09:00:00 | 20 | 0 | 747.9167 | 0 | 1065274.9802 | 20 | 0 | 0 | 0 | 0 | 0 | 21.7815 | 21.796 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 295.9097
202 | 08/09 10:00:00 | 20 | 0 | 835.0833 | 0 | 1014753.9186 | 20 | 0 | 0 | 0 | 0 | 0 | 21.697 | 21.7108 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 281.8761
203 | 08/09 11:00:00 | 20 | 0 | 878.0833 | 0 | 966628.7817 | 20 | 0 | 0 | 0 | 0 | 0 | 21.6165 | 21.6296 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 268.508
204 | 08/09 12:00:00 | 20 | 0 | 899.5 | 0 | 920785.9557 | 20 | 0 | 0 | 0 | 0 | 0 | 21.5398 | 21.5524 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 255.7739
205 | 08/09 13:00:00 | 20 | 0 | 907 | 0 | 877117.2133 | 20 | 0 | 0 | 0 | 0 | 0 | 21.4668 | 21.4787 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 243.6437
206 | 08/09 14:00:00 | 20 | 0 | 903.6667 | 0 | 835519.458 | 20 | 0 | 0 | 0 | 0 | 0 | 21.3972 | 21.4086 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 232.0887
207 | 08/09 15:00:00 | 20 | 0 | 887.25 | 0 | 795894.4804 | 20 | 0 | 0 | 0 | 0 | 0 | 21.331 | 21.3418 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 221.0818
208 | 08/09 16:00:00 | 20 | 0 | 853.5 | 0 | 758148.7205 | 20 | 0 | 0 | 0 | 0 | 0 | 21.2679 | 21.2782 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 210.5969
209 | 08/09 17:00:00 | 20 | 0 | 785.6667 | 0 | 722333.3059 | 20 | 0 | 0 | 0 | 0 | 0 | 21.208 | 21.2178 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 200.6481
210 | 08/09 18:00:00 | 20 | 0 | 636.6667 | 0 | 688341.5893 | 20 | 0 | 0 | 0 | 0 | 0 | 21.1511 | 21.1604 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 191.206
211 | 08/09 19:00:00 | 20 | 0 | 330.4167 | 0 | 655898.7412 | 20 | 0 | 0 | 0 | 0 | 0 | 21.0969 | 21.1058 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 182.1941
212 | 08/09 20:00:00 | 20 | 0 | 31.5833 | 0 | 624883.5714 | 20 | 0 | 0 | 0 | 0 | 0 | 21.045 | 21.0535 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 173.5788
213 | 08/09 21:00:00 | 20 | 0 | 0 | 0 | 595311.4525 | 20 | 0 | 0 | 0 | 0 | 0 | 20.9955 | 21.0036 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 165.3643
214 | 08/09 22:00:00 | 20 | 0 | 0 | 0 | 567127.086 | 20 | 0 | 0 | 0 | 0 | 0 | 20.9484 | 20.9561 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 157.5353
215 | 08/09 23:00:00 | 20 | 0 | 0 | 0 | 540270.4973 | 20 | 0 | 0 | 0 | 0 | 0 | 20.9035 | 20.9108 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 150.0751
216 | 08/09 24:00:00 | 20 | 0 | 0 | 0 | 514681.8789 | 20 | 0 | 0 | 0 | 0 | 0 | 20.8607 | 20.8677 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 142.9672
217 | 08/10 01:00:00 | 20 | 0 | 0 | 0 | 490302.9359 | 20 | 0 | 0 | 0 | 0 | 0 | 20.8199 | 20.8266 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 136.1953
218 | 08/10 02:00:00 | 20 | 0 | 0 | 0 | 467077.4075 | 20 | 0 | 0 | 0 | 0 | 0 | 20.7811 | 20.7874 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 129.7437
219 | 08/10 03:00:00 | 20 | 0 | 0 | 0 | 444951.284 | 20 | 0 | 0 | 0 | 0 | 0 | 20.7441 | 20.7501 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 123.5976
220 | 08/10 04:00:00 | 20 | 0 | 0 | 0 | 423872.8563 | 20 | 0 | 0 | 0 | 0 | 0 | 20.7088 | 20.7146 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 117.7425
221 | 08/10 05:00:00 | 20 | 0 | 0 | 0 | 403792.7045 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6753 | 20.6808 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 112.1646
222 | 08/10 06:00:00 | 20 | 0 | 9.8333 | 0 | 384663.6606 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6433 | 20.6485 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 106.851
223 | 08/10 07:00:00 | 20 | 0 | 181 | 0 | 366440.7403 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6128 | 20.6178 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 101.7891
224 | 08/10 08:00:00 | 20 | 0 | 551.0833 | 0 | 349081.0501 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5838 | 20.5885 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 96.967
225 | 08/10 09:00:00 | 20 | 0 | 747.9167 | 0 | 332543.7049 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5561 | 20.5606 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 92.3733
226 | 08/10 10:00:00 | 20 | 0 | 835.0833 | 0 | 316789.7582 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5298 | 20.5341 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 87.9972
227 | 08/10 11:00:00 | 20 | 0 | 878.0833 | 0 | 301782.1115 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5047 | 20.5088 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 83.8284
228 | 08/10 12:00:00 | 20 | 0 | 899.5 | 0 | 287485.4264 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4808 | 20.4847 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 79.8571
229 | 08/10 13:00:00 | 20 | 0 | 907 | 0 | 273866.0354 | 20 | 0 | 0 | 0 | 0 | 0 | 20.458 | 20.4617 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 76.0739
230 | 08/10 14:00:00 | 20 | 0 | 903.6667 | 0 | 260891.8528 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4363 | 20.4398 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 72.47
231 | 08/10 15:00:00 | 20 | 0 | 887.25 | 0 | 248532.2992 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4156 | 20.419 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 69.0367
232 | 08/10 16:00:00 | 20 | 0 | 853.5 | 0 | 236758.244 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3959 | 20.3991 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 65.7662
233 | 08/10 17:00:00 | 20 | 0 | 785.6667 | 0 | 225541.9503 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3772 | 20.3802 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 62.6505
234 | 08/10 18:00:00 | 20 | 0 | 636.6667 | 0 | 214856.9982 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3593 | 20.3622 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 59.6825
235 | 08/10 19:00:00 | 20 | 0 | 330.4167 | 0 | 204678.2228 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3423 | 20.3451 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 56.8551
236 | 08/10 20:00:00 | 20 | 0 | 31.5833 | 0 | 194981.6549 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3261 | 20.3287 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 54.1616
237 | 08/10 21:00:00 | 20 | 0 | 0 | 0 | 185891.6049 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3109 | 20.3134 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 51.6366
238 | 08/10 22:00:00 | 20 | 0 | 0 | 0 | 177236.4573 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2964 | 20.2988 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 49.2323
239 | 08/10 23:00:00 | 20 | 0 | 0 | 0 | 168895.4693 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2824 | 20.2847 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 46.9154
240 | 08/10 24:00:00 | 20 | 0 | 0 | 0 | 160985.7146 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2692 | 20.2713 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 44.7183
241 | 08/11 01:00:00 | 20 | 0 | 0 | 0 | 153436.2045 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2566 | 20.2587 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 42.6212
242 | 08/11 02:00:00 | 20 | 0 | 0 | 0 | 146408.6552 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2448 | 20.2468 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 40.6691
243 | 08/11 03:00:00 | 20 | 0 | 0 | 0 | 139573.563 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2334 | 20.2353 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 38.7704
244 | 08/11 04:00:00 | 20 | 0 | 0 | 0 | 133028.9571 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2225 | 20.2243 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 36.9525
245 | 08/11 05:00:00 | 20 | 0 | 0 | 0 | 126778.9715 | 20 | 0 | 0 | 0 | 0 | 0 | 20.212 | 20.2137 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 35.2164
246 | 08/11 06:00:00 | 20 | 0 | 0 | 0 | 120815.9787 | 20 | 0 | 0 | 0 | 0 | 0 | 20.202 | 20.2037 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 33.56
247 | 08/11 07:00:00 | 20 | 0 | 181 | 0 | 115129.5923 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1925 | 20.1941 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 31.9804
248 | 08/11 08:00:00 | 20 | 0 | 551.0833 | 0 | 109708.5498 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1835 | 20.1849 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 30.4746
249 | 08/11 09:00:00 | 20 | 0 | 747.9167 | 0 | 104541.3956 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1748 | 20.1762 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 29.0393
250 | 08/11 10:00:00 | 20 | 0 | 835.0833 | 0 | 99616.7929 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1666 | 20.1679 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 27.6713
251 | 08/11 11:00:00 | 20 | 0 | 878.0833 | 0 | 94923.6818 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1587 | 20.16 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 26.3677
252 | 08/11 12:00:00 | 20 | 0 | 899.5 | 0 | 90451.3742 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1513 | 20.1525 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 25.1254
253 | 08/11 13:00:00 | 20 | 0 | 907 | 0 | 86189.6003 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1441 | 20.1453 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 23.9416
254 | 08/11 14:00:00 | 20 | 0 | 903.6667 | 0 | 82128.5186 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1373 | 20.1385 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 22.8135
255 | 08/11 15:00:00 | 20 | 0 | 887.25 | 0 | 78258.7158 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1309 | 20.1319 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 21.7385
256 | 08/11 16:00:00 | 20 | 0 | 853.5 | 0 | 74571.205 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1247 | 20.1257 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 20.7142
257 | 08/11 17:00:00 | 20 | 0 | 785.6667 | 0 | 71057.4143 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1188 | 20.1198 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 19.7382
258 | 08/11 18:00:00 | 20 | 0 | 636.6667 | 0 | 67709.1689 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1132 | 20.1141 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 18.8081
259 | 08/11 19:00:00 | 20 | 0 | 330.4167 | 0 | 64518.6759 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1079 | 20.1088 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 17.9219
260 | 08/11 20:00:00 | 20 | 0 | 31.5833 | 0 | 61478.5082 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1028 | 20.1036 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 17.0774
261 | 08/11 21:00:00 | 20 | 0 | 0 | 0 | 58581.5841 | 20 | 0 | 0 | 0 | 0 | 0 | 20.098 | 20.0988 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 16.2727
262 | 08/11 22:00:00 | 20 | 0 | 0 | 0 | 55821.1529 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0934 | 20.0941 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 15.5059
263 | 08/11 23:00:00 | 20 | 0 | 0 | 0 | 53190.7868 | 20 | 0 | 0 | 0 | 0 | 0 | 20.089 | 20.0897 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 14.7752
264 | 08/11 24:00:00 | 20 | 0 | 0 | 0 | 50684.3578 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0848 | 20.0854 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 14.079
265 | 08/12 01:00:00 | 20 | 0 | 0 | 0 | 48296.0223 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0808 | 20.0814 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 13.4156
266 | 08/12 02:00:00 | 20 | 0 | 0 | 0 | 46020.2201 | 20 | 0 | 0 | 0 | 0 | 0 | 20.077 | 20.0776 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 12.7834
267 | 08/12 03:00:00 | 20 | 0 | 0 | 0 | 43851.6589 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0733 | 20.0739 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 12.181
268 | 08/12 04:00:00 | 20 | 0 | 0 | 0 | 41785.2936 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0699 | 20.0704 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 11.607
269 | 08/12 05:00:00 | 20 | 0 | 0 | 0 | 39816.3089 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0666 | 20.0671 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 11.0601
270 | 08/12 06:00:00 | 20 | 0 | 0 | 0 | 37940.1081 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0634 | 20.064 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 10.5389
271 | 08/12 07:00:00 | 20 | 0 | 181 | 0 | 36152.3097 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0605 | 20.0609 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 10.0423
272 | 08/12 08:00:00 | 20 | 0 | 551.0833 | 0 | 34448.7483 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0576 | 20.0581 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 9.5691
273 | 08/12 09:00:00 | 20 | 0 | 747.9167 | 0 | 32825.4596 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0549 | 20.0553 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 9.1182
274 | 08/12 10:00:00 | 20 | 0 | 835.0833 | 0 | 31278.6595 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0523 | 20.0527 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 8.6885
275 | 08/12 11:00:00 | 20 | 0 | 878.0833 | 0 | 29804.743 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0498 | 20.0502 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 8.2791
276 | 08/12 12:00:00 | 20 | 0 | 899.5 | 0 | 28400.2785 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0475 | 20.0479 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.889
277 | 08/12 13:00:00 | 20 | 0 | 907 | 0 | 27061.9973 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0453 | 20.0456 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.5172
278 | 08/12 14:00:00 | 20 | 0 | 903.6667 | 0 | 25786.7815 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0431 | 20.0435 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.163
279 | 08/12 15:00:00 | 20 | 0 | 887.25 | 0 | 24571.6515 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0411 | 20.0414 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.8255
280 | 08/12 16:00:00 | 20 | 0 | 853.5 | 0 | 23413.7641 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0392 | 20.0395 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.5038
281 | 08/12 17:00:00 | 20 | 0 | 785.6667 | 0 | 22310.4181 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0373 | 20.0376 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.1973
282 | 08/12 18:00:00 | 20 | 0 | 636.6667 | 0 | 21259.0507 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0356 | 20.0358 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.9053
283 | 08/12 19:00:00 | 20 | 0 | 330.4167 | 0 | 20257.2297 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0339 | 20.0342 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.627
284 | 08/12 20:00:00 | 20 | 0 | 31.5833 | 0 | 19302.6362 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0323 | 20.0325 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.3618
285 | 08/12 21:00:00 | 20 | 0 | 0 | 0 | 18393.042 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0308 | 20.031 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.1092
286 | 08/12 22:00:00 | 20 | 0 | 0 | 0 | 17526.3095 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0293 | 20.0295 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.8684
287 | 08/12 23:00:00 | 20 | 0 | 0 | 0 | 16700.4037 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0279 | 20.0282 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.639
288 | 08/12 24:00:00 | 20 | 0 | 0 | 0 | 15913.3955 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0266 | 20.0268 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.4204
289 | 08/13 01:00:00 | 20 | 0 | 0 | 0 | 15163.4595 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0254 | 20.0256 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.2121
290 | 08/13 02:00:00 | 20 | 0 | 0 | 0 | 14448.8596 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0242 | 20.0244 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.0136
291 | 08/13 03:00:00 | 20 | 0 | 0 | 0 | 13767.933 | 20 | 0 | 0 | 0 | 0 | 0 | 20.023 | 20.0232 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.8244
292 | 08/13 04:00:00 | 20 | 0 | 0 | 0 | 13119.0893 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0219 | 20.0221 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.6442
293 | 08/13 05:00:00 | 20 | 0 | 0 | 0 | 12500.8176 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0209 | 20.0211 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.4724
294 | 08/13 06:00:00 | 20 | 0 | 0 | 0 | 11911.6851 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0199 | 20.0201 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.3088
295 | 08/13 07:00:00 | 20 | 0 | 181 | 0 | 11350.3239 | 20 | 0 | 0 | 0 | 0 | 0 | 20.019 | 20.0191 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.1529
296 | 08/13 08:00:00 | 20 | 0 | 551.0833 | 0 | 10815.4217 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0181 | 20.0182 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.0043
297 | 08/13 09:00:00 | 20 | 0 | 747.9167 | 0 | 10305.7259 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0172 | 20.0174 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.8627
298 | 08/13 10:00:00 | 20 | 0 | 835.0833 | 0 | 9820.0474 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0164 | 20.0166 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.7278
299 | 08/13 11:00:00 | 20 | 0 | 878.0833 | 0 | 9357.2549 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0156 | 20.0158 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.5992
300 | 08/13 12:00:00 | 20 | 0 | 899.5 | 0 | 8916.2693 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0149 | 20.015 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.4767
301 | 08/13 13:00:00 | 20 | 0 | 907 | 0 | 8496.0607 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0142 | 20.0143 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.36
302 | 08/13 14:00:00 | 20 | 0 | 903.6667 | 0 | 8095.6406 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0135 | 20.0136 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.2488
303 | 08/13 15:00:00 | 20 | 0 | 887.25 | 0 | 7714.0619 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0129 | 20.013 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.1428
304 | 08/13 16:00:00 | 20 | 0 | 853.5 | 0 | 7350.4308 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0123 | 20.0124 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.0418
305 | 08/13 17:00:00 | 20 | 0 | 785.6667 | 0 | 7003.9087 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0117 | 20.0118 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.9455
306 | 08/13 18:00:00 | 20 | 0 | 636.6667 | 0 | 6673.6946 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0112 | 20.0113 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.8538
307 | 08/13 19:00:00 | 20 | 0 | 330.4167 | 0 | 6359.0201 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0106 | 20.0107 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.7664
308 | 08/13 20:00:00 | 20 | 0 | 31.5833 | 0 | 6059.1589 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0101 | 20.0102 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.6831
309 | 08/13 21:00:00 | 20 | 0 | 0 | 0 | 5773.4291 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0097 | 20.0097 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.6037
310 | 08/13 22:00:00 | 20 | 0 | 0 | 0 | 5501.1821 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0092 | 20.0093 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.5281
311 | 08/13 23:00:00 | 20 | 0 | 0 | 0 | 5241.7865 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0088 | 20.0088 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.4561
312 | 08/13 24:00:00 | 20 | 0 | 0 | 0 | 4994.6289 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0084 | 20.0084 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.3874
313 | 08/14 01:00:00 | 20 | 0 | 0 | 0 | 4759.1254 | 20 | 0 | 0 | 0 | 0 | 0 | 20.008 | 20.008 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.322
314 | 08/14 02:00:00 | 20 | 0 | 0 | 0 | 4534.7254 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0076 | 20.0076 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.2596
315 | 08/14 03:00:00 | 20 | 0 | 0 | 0 | 4320.9098 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0072 | 20.0073 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.2003
316 | 08/14 04:00:00 | 20 | 0 | 0 | 0 | 4117.1826 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0069 | 20.0069 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.1437
317 | 08/14 05:00:00 | 20 | 0 | 0 | 0 | 3923.0684 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0066 | 20.0066 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.0897
318 | 08/14 06:00:00 | 20 | 0 | 0 | 0 | 3738.1111 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0063 | 20.0063 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.0384
319 | 08/14 07:00:00 | 20 | 0 | 181 | 0 | 3561.8745 | 20 | 0 | 0 | 0 | 0 | 0 | 20.006 | 20.006 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.98941
320 | 08/14 08:00:00 | 20 | 0 | 551.0833 | 0 | 3393.9477 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0057 | 20.0057 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.94276
321 | 08/14 09:00:00 | 20 | 0 | 747.9167 | 0 | 3233.9466 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0054 | 20.0055 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.89832
322 | 08/14 10:00:00 | 20 | 0 | 835.0833 | 0 | 3081.5065 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0052 | 20.0052 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.85597
323 | 08/14 11:00:00 | 20 | 0 | 878.0833 | 0 | 2936.2775 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0049 | 20.005 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.81563
324 | 08/14 12:00:00 | 20 | 0 | 899.5 | 0 | 2797.9186 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0047 | 20.0047 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.7772
325 | 08/14 13:00:00 | 20 | 0 | 907 | 0 | 2666.0856 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0045 | 20.0045 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.74058
326 | 08/14 14:00:00 | 20 | 0 | 903.6667 | 0 | 2540.4397 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0042 | 20.0043 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.70568
327 | 08/14 15:00:00 | 20 | 0 | 887.25 | 0 | 2420.6688 | 20 | 0 | 0 | 0 | 0 | 0 | 20.004 | 20.0041 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.67241
328 | 08/14 16:00:00 | 20 | 0 | 853.5 | 0 | 2306.4933 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0039 | 20.0039 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.64069
329 | 08/14 17:00:00 | 20 | 0 | 785.6667 | 0 | 2197.6596 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0037 | 20.0037 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.61046
330 | 08/14 18:00:00 | 20 | 0 | 636.6667 | 0 | 2093.9334 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0035 | 20.0035 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.58165
331 | 08/14 19:00:00 | 20 | 0 | 330.4167 | 0 | 1995.0919 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0033 | 20.0034 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.55419
332 | 08/14 20:00:00 | 20 | 0 | 31.5833 | 0 | 1900.9195 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0032 | 20.0032 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.52803
333 | 08/14 21:00:00 | 20 | 0 | 0 | 0 | 1811.2024 | 20 | 0 | 0 | 0 | 0 | 0 | 20.003 | 20.0031 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.50311
334 | 08/14 22:00:00 | 20 | 0 | 0 | 0 | 1725.7364 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0029 | 20.0029 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.47937
[13 empty] | 335 hrs | Average >>> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 335 hrs | Average-all surfaces >>> | [7 empty] | 2.0507 | 453589.9705
2699.5627
[13 empty] | 168 hrs | Average >>> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 168 hrs | [8 empty] | 2.0507

## EPlus 50 Rad
EnergyPlus Results for ASHRAE 1052RP Analytical Test IntHeatGain
Step change in internal load
2700 W for 168 hours, 50% radiative
Hour | Date/Time | Environment:Outdoor Dry Bulb [C](Hourly) | Environment:Diffuse Solar [W/m2](Hourly) | Environment:Direct Solar [W/m2](Hourly) | ZONE ONE:Zone/Sys Sensible Heating Energy[J](Hourly) | ZONE ONE:Zone/Sys Sensible Cooling Energy[J](Hourly) | ZONE ONE:Mean Air Temperature[C](Hourly) | ZONE ONE:Zone-Total Radiant Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Convective Heat Gain[J](Hourly) | ZONE ONE:Zone-Total Lost Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Radiant Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Convective Heat Gain[J](Hourly) | ZONE ONE:Other Eq-Lost Heat Gain[J](Hourly) | EnergyPlus - 50% Radiative | ZONE SURFACE NORTH:Surface Outside Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE NORTH:Surface Ext Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE SOUTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE EAST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE WEST:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE CEILING:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE FLOOR:Surface Int Convection Coeff[W/m2-K](Hourly) | EnergyPlus - 50% Radiative
1 | 08/01 01:00:00 | 20 | 0 | 0 | 0 | 6340629.0424 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 22.4761 | 21.9832 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1761.2858
2 | 08/01 02:00:00 | 20 | 0 | 0 | 0 | 6875631.4349 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 23.3708 | 23.2605 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1909.8976
3 | 08/01 03:00:00 | 20 | 0 | 0 | 0 | 7181011.5523 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 23.8815 | 23.8098 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1994.7254
4 | 08/01 04:00:00 | 20 | 0 | 0 | 0 | 7394972.6159 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 24.2393 | 24.1866 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2054.1591
5 | 08/01 05:00:00 | 20 | 0 | 0 | 0 | 7559183.0535 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 24.5139 | 24.4723 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2099.7731
6 | 08/01 06:00:00 | 20 | 0 | 9.8333 | 0 | 7692857.3557 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 24.7374 | 24.7028 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2136.9048
7 | 08/01 07:00:00 | 20 | 0 | 181 | 0 | 7807257.3722 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 24.9287 | 24.8986 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2168.6826
8 | 08/01 08:00:00 | 20 | 0 | 551.0833 | 0 | 7908664.6659 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.0983 | 25.0713 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2196.8513
9 | 08/01 09:00:00 | 20 | 0 | 747.9167 | 0 | 8000771.507 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.2524 | 25.2276 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2222.4365
10 | 08/01 10:00:00 | 20 | 0 | 835.0833 | 0 | 8085878.6796 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.3947 | 25.3717 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2246.0774
11 | 08/01 11:00:00 | 20 | 0 | 878.0833 | 0 | 8165416.4937 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.5277 | 25.5061 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2268.1712
12 | 08/01 12:00:00 | 20 | 0 | 899.5 | 0 | 8240294.5813 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.6529 | 25.6325 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2288.9707
13 | 08/01 13:00:00 | 20 | 0 | 907 | 0 | 8311111.4518 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.7713 | 25.752 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2308.6421
14 | 08/01 14:00:00 | 20 | 0 | 903.6667 | 0 | 8378279.2989 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.8837 | 25.8653 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2327.2998
15 | 08/01 15:00:00 | 20 | 0 | 887.25 | 0 | 8442098.0993 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 25.9904 | 25.973 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2345.0272
16 | 08/01 16:00:00 | 20 | 0 | 853.5 | 0 | 8502799.4862 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.0919 | 26.0753 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2361.8887
17 | 08/01 17:00:00 | 20 | 0 | 785.6667 | 0 | 8560572.6637 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.1885 | 26.1727 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2377.9369
18 | 08/01 18:00:00 | 20 | 0 | 636.6667 | 0 | 8615579.7101 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.2805 | 26.2655 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2393.2166
19 | 08/01 19:00:00 | 20 | 0 | 330.4167 | 0 | 8667964.6326 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.3681 | 26.3538 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2407.768
20 | 08/01 20:00:00 | 20 | 0 | 32.4167 | 0 | 8717858.7292 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.4515 | 26.4379 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2421.6274
21 | 08/01 21:00:00 | 20 | 0 | 0 | 0 | 8765383.7878 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.531 | 26.518 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2434.8288
22 | 08/01 22:00:00 | 20 | 0 | 0 | 0 | 8810654.0175 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.6067 | 26.5944 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2447.4039
23 | 08/01 23:00:00 | 20 | 0 | 0 | 0 | 8853777.2349 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.6788 | 26.6671 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2459.3826
24 | 08/01 24:00:00 | 20 | 0 | 0 | 0 | 8894855.6296 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.7475 | 26.7363 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2470.7932
25 | 08/02 01:00:00 | 20 | 0 | 0 | 0 | 8933986.2886 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.813 | 26.8023 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2481.6629
26 | 08/02 02:00:00 | 20 | 0 | 0 | 0 | 8971261.5781 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.8753 | 26.8651 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2492.0171
27 | 08/02 03:00:00 | 20 | 0 | 0 | 0 | 9006543.3705 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.9343 | 26.9247 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2501.8176
28 | 08/02 04:00:00 | 20 | 0 | 0 | 0 | 9040093.8964 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 26.9904 | 26.9813 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2511.1372
29 | 08/02 05:00:00 | 20 | 0 | 0 | 0 | 9072203.143 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.0441 | 27.0353 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2520.0564
30 | 08/02 06:00:00 | 20 | 0 | 9.8333 | 0 | 9102844.699 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.0954 | 27.087 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2528.568
31 | 08/02 07:00:00 | 20 | 0 | 181 | 0 | 9132055.2841 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.1442 | 27.1362 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2536.682
32 | 08/02 08:00:00 | 20 | 0 | 551.0833 | 0 | 9159893.0111 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.1908 | 27.1832 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2544.4147
33 | 08/02 09:00:00 | 20 | 0 | 747.9167 | 0 | 9186418.235 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.2351 | 27.2279 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2551.7828
34 | 08/02 10:00:00 | 20 | 0 | 835.0833 | 0 | 9211690.5363 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.2774 | 27.2705 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2558.8029
35 | 08/02 11:00:00 | 20 | 0 | 878.0833 | 0 | 9235767.7641 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.3177 | 27.3111 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2565.491
36 | 08/02 12:00:00 | 20 | 0 | 899.5 | 0 | 9258705.6532 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.356 | 27.3497 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2571.8627
37 | 08/02 13:00:00 | 20 | 0 | 907 | 0 | 9280557.6566 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.3926 | 27.3866 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2577.9327
38 | 08/02 14:00:00 | 20 | 0 | 903.6667 | 0 | 9301374.899 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.4274 | 27.4217 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2583.7152
39 | 08/02 15:00:00 | 20 | 0 | 887.25 | 0 | 9321206.2112 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.4605 | 27.4551 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2589.2239
40 | 08/02 16:00:00 | 20 | 0 | 853.5 | 0 | 9340098.188 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.4921 | 27.487 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2594.4717
41 | 08/02 17:00:00 | 20 | 0 | 785.6667 | 0 | 9358095.2579 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.5222 | 27.5173 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2599.4709
42 | 08/02 18:00:00 | 20 | 0 | 636.6667 | 0 | 9375239.7725 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.5509 | 27.5462 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2604.2333
43 | 08/02 19:00:00 | 20 | 0 | 330.4167 | 0 | 9391572.0985 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.5782 | 27.5737 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2608.77
44 | 08/02 20:00:00 | 20 | 0 | 32.4167 | 0 | 9407130.7067 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.6042 | 27.6 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2613.0919
45 | 08/02 21:00:00 | 20 | 0 | 0 | 0 | 9421952.2526 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.629 | 27.625 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2617.209
46 | 08/02 22:00:00 | 20 | 0 | 0 | 0 | 9436071.6572 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.6526 | 27.6488 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2621.131
47 | 08/02 23:00:00 | 20 | 0 | 0 | 0 | 9449522.1841 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.6751 | 27.6714 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2624.8673
48 | 08/02 24:00:00 | 20 | 0 | 0 | 0 | 9462335.5124 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.6965 | 27.693 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2628.4265
49 | 08/03 01:00:00 | 20 | 0 | 0 | 0 | 9474541.8158 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.717 | 27.7136 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2631.8172
50 | 08/03 02:00:00 | 20 | 0 | 0 | 0 | 9486169.8489 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.7364 | 27.7332 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2635.0472
51 | 08/03 03:00:00 | 20 | 0 | 0 | 0 | 9497247.0155 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.7549 | 27.7519 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2638.1242
52 | 08/03 04:00:00 | 20 | 0 | 0 | 0 | 9507799.4207 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.7726 | 27.7697 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2641.0554
53 | 08/03 05:00:00 | 20 | 0 | 0 | 0 | 9517851.9213 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.7894 | 27.7866 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2643.8478
54 | 08/03 06:00:00 | 20 | 0 | 9.8333 | 0 | 9527428.1921 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8054 | 27.8028 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2646.5078
55 | 08/03 07:00:00 | 20 | 0 | 181 | 0 | 9536332.9289 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8203 | 27.8179 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2648.9814
56 | 08/03 08:00:00 | 20 | 0 | 551.0833 | 0 | 9544945.0955 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8347 | 27.8323 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2651.3736
57 | 08/03 09:00:00 | 20 | 0 | 747.9167 | 0 | 9553185.4114 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8485 | 27.8462 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2653.6626
58 | 08/03 10:00:00 | 20 | 0 | 835.0833 | 0 | 9561032.1441 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8616 | 27.8594 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2655.8423
59 | 08/03 11:00:00 | 20 | 0 | 878.0833 | 0 | 9568297.9253 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8737 | 27.8718 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2657.8605
60 | 08/03 12:00:00 | 20 | 0 | 899.5 | 0 | 9575342.7506 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8855 | 27.8836 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2659.8174
61 | 08/03 13:00:00 | 20 | 0 | 907 | 0 | 9582115.6598 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.8969 | 27.895 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2661.6988
62 | 08/03 14:00:00 | 20 | 0 | 903.6667 | 0 | 9588588.4427 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9077 | 27.9059 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2663.4968
63 | 08/03 15:00:00 | 20 | 0 | 887.25 | 0 | 9594766.177 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.918 | 27.9163 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2665.2128
64 | 08/03 16:00:00 | 20 | 0 | 853.5 | 0 | 9600658.5233 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9279 | 27.9263 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2666.8496
65 | 08/03 17:00:00 | 20 | 0 | 785.6667 | 0 | 9606276.5957 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9373 | 27.9357 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2668.4102
66 | 08/03 18:00:00 | 20 | 0 | 636.6667 | 0 | 9611631.9634 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9462 | 27.9448 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2669.8978
67 | 08/03 19:00:00 | 20 | 0 | 330.4167 | 0 | 9616736.1998 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9547 | 27.9534 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2671.3156
68 | 08/03 20:00:00 | 20 | 0 | 32.4167 | 0 | 9621600.6491 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9629 | 27.9616 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2672.6668
69 | 08/03 21:00:00 | 20 | 0 | 0 | 0 | 9626236.3046 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9706 | 27.9694 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2673.9545
70 | 08/03 22:00:00 | 20 | 0 | 0 | 0 | 9630653.7544 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.978 | 27.9768 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2675.1816
71 | 08/03 23:00:00 | 20 | 0 | 0 | 0 | 9634863.1725 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9851 | 27.9839 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2676.3509
72 | 08/03 24:00:00 | 20 | 0 | 0 | 0 | 9638874.308 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9918 | 27.9907 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2677.4651
73 | 08/04 01:00:00 | 20 | 0 | 0 | 0 | 9642696.4779 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 27.9982 | 27.9971 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2678.5268
74 | 08/04 02:00:00 | 20 | 0 | 0 | 0 | 9646338.5694 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0043 | 28.0033 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2679.5385
75 | 08/04 03:00:00 | 20 | 0 | 0 | 0 | 9649809.0533 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0101 | 28.0091 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2680.5025
76 | 08/04 04:00:00 | 20 | 0 | 0 | 0 | 9653116.0031 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0156 | 28.0147 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2681.4211
77 | 08/04 05:00:00 | 20 | 0 | 0 | 0 | 9656267.1132 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0209 | 28.02 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2682.2964
78 | 08/04 06:00:00 | 20 | 0 | 9.8333 | 0 | 9659269.7252 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0259 | 28.0251 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2683.1305
79 | 08/04 07:00:00 | 20 | 0 | 181 | 0 | 9662130.8482 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0307 | 28.0299 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2683.9252
80 | 08/04 08:00:00 | 20 | 0 | 551.0833 | 0 | 9664857.1627 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0352 | 28.0345 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2684.6825
81 | 08/04 09:00:00 | 20 | 0 | 747.9167 | 0 | 9667455.0295 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0396 | 28.0389 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2685.4042
82 | 08/04 10:00:00 | 20 | 0 | 835.0833 | 0 | 9669930.5087 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0437 | 28.043 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2686.0918
83 | 08/04 11:00:00 | 20 | 0 | 878.0833 | 0 | 9672289.3703 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0477 | 28.047 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2686.747
84 | 08/04 12:00:00 | 20 | 0 | 899.5 | 0 | 9674537.1018 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0514 | 28.0508 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2687.3714
85 | 08/04 13:00:00 | 20 | 0 | 907 | 0 | 9676678.927 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.055 | 28.0544 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2687.9664
86 | 08/04 14:00:00 | 20 | 0 | 903.6667 | 0 | 9678719.8345 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0584 | 28.0578 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2688.5333
87 | 08/04 15:00:00 | 20 | 0 | 887.25 | 0 | 9680664.5905 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0617 | 28.0611 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2689.0735
88 | 08/04 16:00:00 | 20 | 0 | 853.5 | 0 | 9682517.7266 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0648 | 28.0642 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2689.5883
89 | 08/04 17:00:00 | 20 | 0 | 785.6667 | 0 | 9684283.5505 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0677 | 28.0672 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2690.0788
90 | 08/04 18:00:00 | 20 | 0 | 636.6667 | 0 | 9685966.1708 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0705 | 28.0701 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2690.5462
91 | 08/04 19:00:00 | 20 | 0 | 330.4167 | 0 | 9687569.5123 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0732 | 28.0728 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2690.9915
92 | 08/04 20:00:00 | 20 | 0 | 32.4167 | 0 | 9689097.3175 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0758 | 28.0753 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2691.4159
93 | 08/04 21:00:00 | 20 | 0 | 0 | 0 | 9690553.151 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0782 | 28.0778 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2691.8203
94 | 08/04 22:00:00 | 20 | 0 | 0 | 0 | 9691940.4018 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0805 | 28.0801 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.2057
95 | 08/04 23:00:00 | 20 | 0 | 0 | 0 | 9693262.2835 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0827 | 28.0824 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.5729
96 | 08/04 24:00:00 | 20 | 0 | 0 | 0 | 9694521.8573 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0848 | 28.0845 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2692.9227
97 | 08/05 01:00:00 | 20 | 0 | 0 | 0 | 9695722.0541 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0868 | 28.0865 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.2561
98 | 08/05 02:00:00 | 20 | 0 | 0 | 0 | 9696865.6856 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0888 | 28.0884 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.5738
99 | 08/05 03:00:00 | 20 | 0 | 0 | 0 | 9697955.436 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0906 | 28.0903 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2693.8765
100 | 08/05 04:00:00 | 20 | 0 | 0 | 0 | 9698993.8509 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0923 | 28.092 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.165
101 | 08/05 05:00:00 | 20 | 0 | 0 | 0 | 9699983.3471 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.094 | 28.0937 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.4398
102 | 08/05 06:00:00 | 20 | 0 | 9.8333 | 0 | 9700926.2311 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0955 | 28.0953 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.7017
103 | 08/05 07:00:00 | 20 | 0 | 181 | 0 | 9701824.7072 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.097 | 28.0968 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2694.9513
104 | 08/05 08:00:00 | 20 | 0 | 551.0833 | 0 | 9702680.8706 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0985 | 28.0982 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.1891
105 | 08/05 09:00:00 | 20 | 0 | 747.9167 | 0 | 9703496.7087 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.0998 | 28.0996 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.4158
106 | 08/05 10:00:00 | 20 | 0 | 835.0833 | 0 | 9704274.1119 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1011 | 28.1009 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.6317
107 | 08/05 11:00:00 | 20 | 0 | 878.0833 | 0 | 9705014.8813 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1024 | 28.1022 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2695.8375
108 | 08/05 12:00:00 | 20 | 0 | 899.5 | 0 | 9705720.7412 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1036 | 28.1034 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.0335
109 | 08/05 13:00:00 | 20 | 0 | 907 | 0 | 9706393.3371 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1047 | 28.1045 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.2204
110 | 08/05 14:00:00 | 20 | 0 | 903.6667 | 0 | 9707034.2372 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1058 | 28.1056 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.3984
111 | 08/05 15:00:00 | 20 | 0 | 887.25 | 0 | 9707644.9369 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1068 | 28.1066 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.568
112 | 08/05 16:00:00 | 20 | 0 | 853.5 | 0 | 9708226.8614 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1077 | 28.1076 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.7297
113 | 08/05 17:00:00 | 20 | 0 | 785.6667 | 0 | 9708781.3647 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1087 | 28.1085 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2696.8837
114 | 08/05 18:00:00 | 20 | 0 | 636.6667 | 0 | 9709309.7306 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1096 | 28.1094 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.0305
115 | 08/05 19:00:00 | 20 | 0 | 330.4167 | 0 | 9709813.1861 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1104 | 28.1103 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.1703
116 | 08/05 20:00:00 | 20 | 0 | 32.4167 | 0 | 9710292.8988 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1112 | 28.1111 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.3036
117 | 08/05 21:00:00 | 20 | 0 | 0 | 0 | 9710749.9782 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.112 | 28.1118 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.4305
118 | 08/05 22:00:00 | 20 | 0 | 0 | 0 | 9711185.4923 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1127 | 28.1126 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.5515
119 | 08/05 23:00:00 | 20 | 0 | 0 | 0 | 9711600.4685 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1134 | 28.1133 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.6668
120 | 08/05 24:00:00 | 20 | 0 | 0 | 0 | 9711995.8827 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1141 | 28.1139 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.7766
121 | 08/06 01:00:00 | 20 | 0 | 0 | 0 | 9712372.6594 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1147 | 28.1146 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.8813
122 | 08/06 02:00:00 | 20 | 0 | 0 | 0 | 9712731.6859 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1153 | 28.1152 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2697.981
123 | 08/06 03:00:00 | 20 | 0 | 0 | 0 | 9713073.8039 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1159 | 28.1158 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.0761
124 | 08/06 04:00:00 | 20 | 0 | 0 | 0 | 9713399.8006 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1164 | 28.1163 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.1666
125 | 08/06 05:00:00 | 20 | 0 | 0 | 0 | 9713710.4238 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1169 | 28.1168 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.2529
126 | 08/06 06:00:00 | 20 | 0 | 9.8333 | 0 | 9714006.3983 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1174 | 28.1173 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.3351
127 | 08/06 07:00:00 | 20 | 0 | 181 | 0 | 9714288.4256 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1179 | 28.1178 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.4135
128 | 08/06 08:00:00 | 20 | 0 | 551.0833 | 0 | 9714557.1819 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1183 | 28.1183 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.4881
129 | 08/06 09:00:00 | 20 | 0 | 747.9167 | 0 | 9714813.3067 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1188 | 28.1187 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.5593
130 | 08/06 10:00:00 | 20 | 0 | 835.0833 | 0 | 9715057.4046 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1192 | 28.1191 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.6271
131 | 08/06 11:00:00 | 20 | 0 | 878.0833 | 0 | 9715290.049 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1196 | 28.1195 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.6917
132 | 08/06 12:00:00 | 20 | 0 | 899.5 | 0 | 9715511.7741 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1199 | 28.1199 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.7533
133 | 08/06 13:00:00 | 20 | 0 | 907 | 0 | 9715723.0786 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1203 | 28.1202 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.812
134 | 08/06 14:00:00 | 20 | 0 | 903.6667 | 0 | 9715924.4385 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1206 | 28.1206 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.8679
135 | 08/06 15:00:00 | 20 | 0 | 887.25 | 0 | 9716116.3172 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1209 | 28.1209 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.9212
136 | 08/06 16:00:00 | 20 | 0 | 853.5 | 0 | 9716299.1665 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1212 | 28.1212 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2698.972
137 | 08/06 17:00:00 | 20 | 0 | 785.6667 | 0 | 9716473.4196 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1215 | 28.1215 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.0204
138 | 08/06 18:00:00 | 20 | 0 | 636.6667 | 0 | 9716639.4849 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1218 | 28.1218 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.0665
139 | 08/06 19:00:00 | 20 | 0 | 330.4167 | 0 | 9716797.7416 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1221 | 28.122 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.1105
140 | 08/06 20:00:00 | 20 | 0 | 32.4167 | 0 | 9716948.5478 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1223 | 28.1223 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.1524
141 | 08/06 21:00:00 | 20 | 0 | 0 | 0 | 9717092.2474 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1226 | 28.1225 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.1923
142 | 08/06 22:00:00 | 20 | 0 | 0 | 0 | 9717229.1686 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1228 | 28.1228 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.2303
143 | 08/06 23:00:00 | 20 | 0 | 0 | 0 | 9717359.625 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.123 | 28.123 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.2666
144 | 08/06 24:00:00 | 20 | 0 | 0 | 0 | 9717483.9144 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1232 | 28.1232 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3011
145 | 08/07 01:00:00 | 20 | 0 | 0 | 0 | 9717602.3189 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1234 | 28.1234 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.334
146 | 08/07 02:00:00 | 20 | 0 | 0 | 0 | 9717715.1165 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1236 | 28.1236 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3653
147 | 08/07 03:00:00 | 20 | 0 | 0 | 0 | 9717822.5931 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1238 | 28.1238 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.3952
148 | 08/07 04:00:00 | 20 | 0 | 0 | 0 | 9717925.0259 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.124 | 28.1239 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4236
149 | 08/07 05:00:00 | 20 | 0 | 0 | 0 | 9718022.6671 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1241 | 28.1241 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4507
150 | 08/07 06:00:00 | 20 | 0 | 9.8333 | 0 | 9718115.7437 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1243 | 28.1243 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.4766
151 | 08/07 07:00:00 | 20 | 0 | 181 | 0 | 9718204.4598 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1244 | 28.1244 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5012
152 | 08/07 08:00:00 | 20 | 0 | 551.0833 | 0 | 9718289.0083 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1246 | 28.1246 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5247
153 | 08/07 09:00:00 | 20 | 0 | 747.9167 | 0 | 9718369.5768 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1247 | 28.1247 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5471
154 | 08/07 10:00:00 | 20 | 0 | 835.0833 | 0 | 9718446.3465 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1248 | 28.1248 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5684
155 | 08/07 11:00:00 | 20 | 0 | 878.0833 | 0 | 9718519.4917 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.125 | 28.1249 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.5887
156 | 08/07 12:00:00 | 20 | 0 | 899.5 | 0 | 9718589.1728 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1251 | 28.1251 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6081
157 | 08/07 13:00:00 | 20 | 0 | 907 | 0 | 9718655.5416 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1252 | 28.1252 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6265
158 | 08/07 14:00:00 | 20 | 0 | 903.6667 | 0 | 9718718.7522 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1253 | 28.1253 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6441
159 | 08/07 15:00:00 | 20 | 0 | 887.25 | 0 | 9718778.962 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1254 | 28.1254 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6608
160 | 08/07 16:00:00 | 20 | 0 | 853.5 | 0 | 9718836.3175 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1255 | 28.1255 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6768
161 | 08/07 17:00:00 | 20 | 0 | 785.6667 | 0 | 9718890.9524 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1256 | 28.1256 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.6919
162 | 08/07 18:00:00 | 20 | 0 | 636.6667 | 0 | 9718942.9921 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1257 | 28.1257 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7064
163 | 08/07 19:00:00 | 20 | 0 | 330.4167 | 0 | 9718992.5597 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1258 | 28.1257 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7202
164 | 08/07 20:00:00 | 20 | 0 | 31.5833 | 0 | 9719039.7812 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1258 | 28.1258 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7333
165 | 08/07 21:00:00 | 20 | 0 | 0 | 0 | 9719084.7754 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1259 | 28.1259 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7458
166 | 08/07 22:00:00 | 20 | 0 | 0 | 0 | 9719127.6492 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.126 | 28.126 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7577
167 | 08/07 23:00:00 | 20 | 0 | 0 | 0 | 9719168.5067 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.126 | 28.126 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.769
168 | 08/07 24:00:00 | 20 | 0 | 0 | 0 | 9719207.456 | 20 | 4860000 | 4860000 | 4860000 | 4860000 | 0 | 28.1261 | 28.1261 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2699.7798
169 | 08/08 01:00:00 | 20 | 0 | 0 | 0 | 3378614.4942 | 20 | 0 | 0 | 0 | 0 | 0 | 25.6501 | 26.1429 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 938.504
170 | 08/08 02:00:00 | 20 | 0 | 0 | 0 | 2843648.3941 | 20 | 0 | 0 | 0 | 0 | 0 | 24.7555 | 24.8657 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 789.9023
171 | 08/08 03:00:00 | 20 | 0 | 0 | 0 | 2538302.4428 | 20 | 0 | 0 | 0 | 0 | 0 | 24.2448 | 24.3164 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 705.084
172 | 08/08 04:00:00 | 20 | 0 | 0 | 0 | 2324373.7841 | 20 | 0 | 0 | 0 | 0 | 0 | 23.8871 | 23.9397 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 645.6594
173 | 08/08 05:00:00 | 20 | 0 | 0 | 0 | 2160194.1246 | 20 | 0 | 0 | 0 | 0 | 0 | 23.6125 | 23.6541 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 600.0539
174 | 08/08 06:00:00 | 20 | 0 | 9.8333 | 0 | 2026548.9937 | 20 | 0 | 0 | 0 | 0 | 0 | 23.389 | 23.4236 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 562.9303
175 | 08/08 07:00:00 | 20 | 0 | 181 | 0 | 1912176.7362 | 20 | 0 | 0 | 0 | 0 | 0 | 23.1978 | 23.2279 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 531.1602
176 | 08/08 08:00:00 | 20 | 0 | 551.0833 | 0 | 1810795.8719 | 20 | 0 | 0 | 0 | 0 | 0 | 23.0282 | 23.0553 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 502.9989
177 | 08/08 09:00:00 | 20 | 0 | 747.9167 | 0 | 1718714.191 | 20 | 0 | 0 | 0 | 0 | 0 | 22.8742 | 22.899 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 477.4206
178 | 08/08 10:00:00 | 20 | 0 | 835.0833 | 0 | 1633630.9812 | 20 | 0 | 0 | 0 | 0 | 0 | 22.7319 | 22.755 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 453.7864
179 | 08/08 11:00:00 | 20 | 0 | 878.0833 | 0 | 1554115.9995 | 20 | 0 | 0 | 0 | 0 | 0 | 22.599 | 22.6206 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 431.6989
180 | 08/08 12:00:00 | 20 | 0 | 899.5 | 0 | 1479259.6821 | 20 | 0 | 0 | 0 | 0 | 0 | 22.4738 | 22.4942 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 410.9055
181 | 08/08 13:00:00 | 20 | 0 | 907 | 0 | 1408463.5733 | 20 | 0 | 0 | 0 | 0 | 0 | 22.3554 | 22.3747 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 391.2399
182 | 08/08 14:00:00 | 20 | 0 | 903.6667 | 0 | 1341315.5174 | 20 | 0 | 0 | 0 | 0 | 0 | 22.2431 | 22.2614 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 372.5876
183 | 08/08 15:00:00 | 20 | 0 | 887.25 | 0 | 1277515.5827 | 20 | 0 | 0 | 0 | 0 | 0 | 22.1364 | 22.1538 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 354.8654
184 | 08/08 16:00:00 | 20 | 0 | 853.5 | 0 | 1216832.1876 | 20 | 0 | 0 | 0 | 0 | 0 | 22.0349 | 22.0515 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 338.0089
185 | 08/08 17:00:00 | 20 | 0 | 785.6667 | 0 | 1159076.1548 | 20 | 0 | 0 | 0 | 0 | 0 | 21.9383 | 21.9541 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 321.9656
186 | 08/08 18:00:00 | 20 | 0 | 636.6667 | 0 | 1104085.4122 | 20 | 0 | 0 | 0 | 0 | 0 | 21.8464 | 21.8614 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 306.6904
187 | 08/08 19:00:00 | 20 | 0 | 330.4167 | 0 | 1051715.9723 | 20 | 0 | 0 | 0 | 0 | 0 | 21.7588 | 21.7731 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 292.1433
188 | 08/08 20:00:00 | 20 | 0 | 31.5833 | 0 | 1001836.5707 | 20 | 0 | 0 | 0 | 0 | 0 | 21.6754 | 21.689 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 278.2879
189 | 08/08 21:00:00 | 20 | 0 | 0 | 0 | 954325.4691 | 20 | 0 | 0 | 0 | 0 | 0 | 21.5959 | 21.6089 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 265.0904
190 | 08/08 22:00:00 | 20 | 0 | 0 | 0 | 909068.5196 | 20 | 0 | 0 | 0 | 0 | 0 | 21.5202 | 21.5326 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 252.519
191 | 08/08 23:00:00 | 20 | 0 | 0 | 0 | 865957.9611 | 20 | 0 | 0 | 0 | 0 | 0 | 21.4482 | 21.4599 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 240.5439
192 | 08/08 24:00:00 | 20 | 0 | 0 | 0 | 824891.6487 | 20 | 0 | 0 | 0 | 0 | 0 | 21.3795 | 21.3907 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 229.1366
193 | 08/09 01:00:00 | 20 | 0 | 0 | 0 | 785772.5318 | 20 | 0 | 0 | 0 | 0 | 0 | 21.3141 | 21.3247 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 218.2701
194 | 08/09 02:00:00 | 20 | 0 | 0 | 0 | 748508.2801 | 20 | 0 | 0 | 0 | 0 | 0 | 21.2517 | 21.2619 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 207.919
195 | 08/09 03:00:00 | 20 | 0 | 0 | 0 | 713236.9801 | 20 | 0 | 0 | 0 | 0 | 0 | 21.1928 | 21.2024 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 198.1214
196 | 08/09 04:00:00 | 20 | 0 | 0 | 0 | 679696.4641 | 20 | 0 | 0 | 0 | 0 | 0 | 21.1367 | 21.1458 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 188.8046
197 | 08/09 05:00:00 | 20 | 0 | 0 | 0 | 647596.8215 | 20 | 0 | 0 | 0 | 0 | 0 | 21.083 | 21.0918 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 179.888
198 | 08/09 06:00:00 | 20 | 0 | 9.8333 | 0 | 616964.4502 | 20 | 0 | 0 | 0 | 0 | 0 | 21.0318 | 21.0401 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 171.379
199 | 08/09 07:00:00 | 20 | 0 | 181 | 0 | 587762.633 | 20 | 0 | 0 | 0 | 0 | 0 | 20.9829 | 20.9909 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 163.2674
200 | 08/09 08:00:00 | 20 | 0 | 551.0833 | 0 | 559933.2549 | 20 | 0 | 0 | 0 | 0 | 0 | 20.9364 | 20.944 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 155.537
201 | 08/09 09:00:00 | 20 | 0 | 747.9167 | 0 | 533415.9586 | 20 | 0 | 0 | 0 | 0 | 0 | 20.892 | 20.8993 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 148.1711
202 | 08/09 10:00:00 | 20 | 0 | 835.0833 | 0 | 508151.1809 | 20 | 0 | 0 | 0 | 0 | 0 | 20.8498 | 20.8567 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 141.1531
203 | 08/09 11:00:00 | 20 | 0 | 878.0833 | 0 | 484081.1023 | 20 | 0 | 0 | 0 | 0 | 0 | 20.8095 | 20.8161 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 134.467
204 | 08/09 12:00:00 | 20 | 0 | 899.5 | 0 | 461150.0226 | 20 | 0 | 0 | 0 | 0 | 0 | 20.7712 | 20.7774 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 128.0972
205 | 08/09 13:00:00 | 20 | 0 | 907 | 0 | 439304.5173 | 20 | 0 | 0 | 0 | 0 | 0 | 20.7347 | 20.7406 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 122.029
206 | 08/09 14:00:00 | 20 | 0 | 903.6667 | 0 | 418493.4747 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6999 | 20.7055 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 116.2482
207 | 08/09 15:00:00 | 20 | 0 | 887.25 | 0 | 398668.0677 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6667 | 20.6721 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 110.7411
208 | 08/09 16:00:00 | 20 | 0 | 853.5 | 0 | 379781.7068 | 20 | 0 | 0 | 0 | 0 | 0 | 20.6351 | 20.6403 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 105.4949
209 | 08/09 17:00:00 | 20 | 0 | 785.6667 | 0 | 361789.969 | 20 | 0 | 0 | 0 | 0 | 0 | 20.605 | 20.6099 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 100.4972
210 | 08/09 18:00:00 | 20 | 0 | 636.6667 | 0 | 344650.5041 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5764 | 20.581 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 95.7363
211 | 08/09 19:00:00 | 20 | 0 | 330.4167 | 0 | 328322.9517 | 20 | 0 | 0 | 0 | 0 | 0 | 20.5491 | 20.5535 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 91.2008
212 | 08/09 20:00:00 | 20 | 0 | 31.5833 | 0 | 312768.8646 | 20 | 0 | 0 | 0 | 0 | 0 | 20.523 | 20.5273 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 86.8802
213 | 08/09 21:00:00 | 20 | 0 | 0 | 0 | 297951.6209 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4983 | 20.5023 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 82.7643
214 | 08/09 22:00:00 | 20 | 0 | 0 | 0 | 283836.333 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4747 | 20.4785 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 78.8434
215 | 08/09 23:00:00 | 20 | 0 | 0 | 0 | 270389.7571 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4522 | 20.4558 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 75.1083
216 | 08/09 24:00:00 | 20 | 0 | 0 | 0 | 257580.2166 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4308 | 20.4343 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 71.5501
217 | 08/10 01:00:00 | 20 | 0 | 0 | 0 | 245377.5332 | 20 | 0 | 0 | 0 | 0 | 0 | 20.4103 | 20.4137 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 68.1604
218 | 08/10 02:00:00 | 20 | 0 | 0 | 0 | 233752.956 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3909 | 20.3941 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 64.9314
219 | 08/10 03:00:00 | 20 | 0 | 0 | 0 | 222679.0925 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3724 | 20.3754 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 61.8553
220 | 08/10 04:00:00 | 20 | 0 | 0 | 0 | 212129.843 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3547 | 20.3576 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 58.925
221 | 08/10 05:00:00 | 20 | 0 | 0 | 0 | 202080.3451 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3379 | 20.3407 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 56.1334
222 | 08/10 06:00:00 | 20 | 0 | 9.8333 | 0 | 192506.9236 | 20 | 0 | 0 | 0 | 0 | 0 | 20.3219 | 20.3245 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 53.4741
223 | 08/10 07:00:00 | 20 | 0 | 181 | 0 | 183604.827 | 20 | 0 | 0 | 0 | 0 | 0 | 20.307 | 20.3094 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 51.0013
224 | 08/10 08:00:00 | 20 | 0 | 551.0833 | 0 | 174995.2061 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2926 | 20.295 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 48.6098
225 | 08/10 09:00:00 | 20 | 0 | 747.9167 | 0 | 166757.3205 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2789 | 20.2811 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 46.3215
226 | 08/10 10:00:00 | 20 | 0 | 835.0833 | 0 | 158912.9015 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2658 | 20.268 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 44.1425
227 | 08/10 11:00:00 | 20 | 0 | 878.0833 | 0 | 151649.2697 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2536 | 20.2555 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 42.1248
228 | 08/10 12:00:00 | 20 | 0 | 899.5 | 0 | 144606.5361 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2418 | 20.2438 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 40.1685
229 | 08/10 13:00:00 | 20 | 0 | 907 | 0 | 137835.6447 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2305 | 20.2324 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 38.2877
230 | 08/10 14:00:00 | 20 | 0 | 903.6667 | 0 | 131364.8004 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2197 | 20.2215 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 36.4902
231 | 08/10 15:00:00 | 20 | 0 | 887.25 | 0 | 125188.9172 | 20 | 0 | 0 | 0 | 0 | 0 | 20.2094 | 20.211 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 34.7747
232 | 08/10 16:00:00 | 20 | 0 | 853.5 | 0 | 119298.3231 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1995 | 20.2011 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 33.1384
233 | 08/10 17:00:00 | 20 | 0 | 785.6667 | 0 | 113681.9114 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1901 | 20.1916 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 31.5783
234 | 08/10 18:00:00 | 20 | 0 | 636.6667 | 0 | 108328.1311 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1812 | 20.1826 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 30.0911
235 | 08/10 19:00:00 | 20 | 0 | 330.4167 | 0 | 103225.4199 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1726 | 20.174 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 28.6737
236 | 08/10 20:00:00 | 20 | 0 | 31.5833 | 0 | 98362.4328 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1645 | 20.1658 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 27.3229
237 | 08/10 21:00:00 | 20 | 0 | 0 | 0 | 93728.1625 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1567 | 20.158 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 26.0356
238 | 08/10 22:00:00 | 20 | 0 | 0 | 0 | 89312.0026 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1494 | 20.1506 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 24.8089
239 | 08/10 23:00:00 | 20 | 0 | 0 | 0 | 85103.7795 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1423 | 20.1435 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 23.6399
240 | 08/10 24:00:00 | 20 | 0 | 0 | 0 | 81093.7527 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1356 | 20.1367 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 22.526
241 | 08/11 01:00:00 | 20 | 0 | 0 | 0 | 77272.6103 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1292 | 20.1303 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 21.4646
242 | 08/11 02:00:00 | 20 | 0 | 0 | 0 | 73631.4721 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1231 | 20.1241 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 20.4532
243 | 08/11 03:00:00 | 20 | 0 | 0 | 0 | 70161.8772 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1173 | 20.1183 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 19.4894
244 | 08/11 04:00:00 | 20 | 0 | 0 | 0 | 66855.758 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1118 | 20.1127 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 18.571
245 | 08/11 05:00:00 | 20 | 0 | 0 | 0 | 63705.4197 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1065 | 20.1074 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 17.6959
246 | 08/11 06:00:00 | 20 | 0 | 0 | 0 | 60703.5232 | 20 | 0 | 0 | 0 | 0 | 0 | 20.1015 | 20.1023 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 16.8621
247 | 08/11 07:00:00 | 20 | 0 | 181 | 0 | 57843.0743 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0967 | 20.0975 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 16.0675
248 | 08/11 08:00:00 | 20 | 0 | 551.0833 | 0 | 55117.4146 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0922 | 20.0929 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 15.3104
249 | 08/11 09:00:00 | 20 | 0 | 747.9167 | 0 | 52520.1993 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0878 | 20.0885 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 14.5889
250 | 08/11 10:00:00 | 20 | 0 | 835.0833 | 0 | 50045.3816 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0837 | 20.0844 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 13.9015
251 | 08/11 11:00:00 | 20 | 0 | 878.0833 | 0 | 47687.1935 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0797 | 20.0804 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 13.2464
252 | 08/11 12:00:00 | 20 | 0 | 899.5 | 0 | 45440.1262 | 20 | 0 | 0 | 0 | 0 | 0 | 20.076 | 20.0766 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 12.6223
253 | 08/11 13:00:00 | 20 | 0 | 907 | 0 | 43298.9335 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0724 | 20.073 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 12.0275
254 | 08/11 14:00:00 | 20 | 0 | 903.6667 | 0 | 41258.624 | 20 | 0 | 0 | 0 | 0 | 0 | 20.069 | 20.0696 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 11.4607
255 | 08/11 15:00:00 | 20 | 0 | 887.25 | 0 | 39314.4484 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0657 | 20.0663 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 10.9207
256 | 08/11 16:00:00 | 20 | 0 | 853.5 | 0 | 37461.8837 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0626 | 20.0632 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 10.4061
257 | 08/11 17:00:00 | 20 | 0 | 785.6667 | 0 | 35696.6121 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0597 | 20.0602 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 9.9157
258 | 08/11 18:00:00 | 20 | 0 | 636.6667 | 0 | 34014.5163 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0569 | 20.0573 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 9.4485
259 | 08/11 19:00:00 | 20 | 0 | 330.4167 | 0 | 32411.6793 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0542 | 20.0546 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 9.0032
260 | 08/11 20:00:00 | 20 | 0 | 31.5833 | 0 | 30884.3759 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0516 | 20.0521 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 8.579
261 | 08/11 21:00:00 | 20 | 0 | 0 | 0 | 29429.0564 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0492 | 20.0496 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 8.1747
262 | 08/11 22:00:00 | 20 | 0 | 0 | 0 | 28042.3278 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0469 | 20.0473 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.7895
263 | 08/11 23:00:00 | 20 | 0 | 0 | 0 | 26720.947 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0447 | 20.045 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.4225
264 | 08/11 24:00:00 | 20 | 0 | 0 | 0 | 25461.8196 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0426 | 20.0429 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 7.0727
265 | 08/12 01:00:00 | 20 | 0 | 0 | 0 | 24262.0023 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0406 | 20.0409 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.7394
266 | 08/12 02:00:00 | 20 | 0 | 0 | 0 | 23118.7025 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0387 | 20.039 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.4219
267 | 08/12 03:00:00 | 20 | 0 | 0 | 0 | 22029.2675 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0368 | 20.0371 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 6.1192
268 | 08/12 04:00:00 | 20 | 0 | 0 | 0 | 20991.1706 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0351 | 20.0354 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.8309
269 | 08/12 05:00:00 | 20 | 0 | 0 | 0 | 20002.0019 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0334 | 20.0337 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.5561
270 | 08/12 06:00:00 | 20 | 0 | 0 | 0 | 19059.4586 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0319 | 20.0321 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.2943
271 | 08/12 07:00:00 | 20 | 0 | 181 | 0 | 18161.3361 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0304 | 20.0306 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 5.0448
272 | 08/12 08:00:00 | 20 | 0 | 551.0833 | 0 | 17305.528 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0289 | 20.0292 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.8071
273 | 08/12 09:00:00 | 20 | 0 | 747.9167 | 0 | 16490.0283 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0276 | 20.0278 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.5806
274 | 08/12 10:00:00 | 20 | 0 | 835.0833 | 0 | 15712.9305 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0263 | 20.0265 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.3647
275 | 08/12 11:00:00 | 20 | 0 | 878.0833 | 0 | 14972.4294 | 20 | 0 | 0 | 0 | 0 | 0 | 20.025 | 20.0252 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 4.159
276 | 08/12 12:00:00 | 20 | 0 | 899.5 | 0 | 14266.8141 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0239 | 20.0241 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.963
277 | 08/12 13:00:00 | 20 | 0 | 907 | 0 | 13594.451 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0227 | 20.0229 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.7762
278 | 08/12 14:00:00 | 20 | 0 | 903.6667 | 0 | 12953.7752 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0217 | 20.0218 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.5983
279 | 08/12 15:00:00 | 20 | 0 | 887.25 | 0 | 12343.2922 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0206 | 20.0208 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.4287
280 | 08/12 16:00:00 | 20 | 0 | 853.5 | 0 | 11761.5768 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0197 | 20.0198 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.2671
281 | 08/12 17:00:00 | 20 | 0 | 785.6667 | 0 | 11207.2749 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0187 | 20.0189 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 3.1131
282 | 08/12 18:00:00 | 20 | 0 | 636.6667 | 0 | 10679.0961 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0179 | 20.018 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.9664
283 | 08/12 19:00:00 | 20 | 0 | 330.4167 | 0 | 10175.8071 | 20 | 0 | 0 | 0 | 0 | 0 | 20.017 | 20.0172 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.8266
284 | 08/12 20:00:00 | 20 | 0 | 31.5833 | 0 | 9696.2319 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0162 | 20.0163 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.6934
285 | 08/12 21:00:00 | 20 | 0 | 0 | 0 | 9239.25 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0155 | 20.0156 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.5665
286 | 08/12 22:00:00 | 20 | 0 | 0 | 0 | 8803.7926 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0147 | 20.0148 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.4455
287 | 08/12 23:00:00 | 20 | 0 | 0 | 0 | 8388.8385 | 20 | 0 | 0 | 0 | 0 | 0 | 20.014 | 20.0141 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.3302
288 | 08/12 24:00:00 | 20 | 0 | 0 | 0 | 7993.4144 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0134 | 20.0135 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.2204
289 | 08/13 01:00:00 | 20 | 0 | 0 | 0 | 7616.6003 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0127 | 20.0128 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.1157
290 | 08/13 02:00:00 | 20 | 0 | 0 | 0 | 7257.5324 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0121 | 20.0122 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 2.016
291 | 08/13 03:00:00 | 20 | 0 | 0 | 0 | 6915.3906 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0116 | 20.0117 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.9209
292 | 08/13 04:00:00 | 20 | 0 | 0 | 0 | 6589.3808 | 20 | 0 | 0 | 0 | 0 | 0 | 20.011 | 20.0111 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.8304
293 | 08/13 05:00:00 | 20 | 0 | 0 | 0 | 6278.7352 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0105 | 20.0106 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.7441
294 | 08/13 06:00:00 | 20 | 0 | 0 | 0 | 5982.7211 | 20 | 0 | 0 | 0 | 0 | 0 | 20.01 | 20.0101 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.6619
295 | 08/13 07:00:00 | 20 | 0 | 181 | 0 | 5700.6444 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0095 | 20.0096 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.5835
296 | 08/13 08:00:00 | 20 | 0 | 551.0833 | 0 | 5431.849 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0091 | 20.0092 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.5088
297 | 08/13 09:00:00 | 20 | 0 | 747.9167 | 0 | 5175.7151 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0087 | 20.0087 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.4377
298 | 08/13 10:00:00 | 20 | 0 | 835.0833 | 0 | 4931.6494 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0082 | 20.0083 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.3699
299 | 08/13 11:00:00 | 20 | 0 | 878.0833 | 0 | 4699.083 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0079 | 20.0079 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.3053
300 | 08/13 12:00:00 | 20 | 0 | 899.5 | 0 | 4477.4781 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0075 | 20.0075 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.2437
301 | 08/13 13:00:00 | 20 | 0 | 907 | 0 | 4266.3263 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0071 | 20.0072 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.1851
302 | 08/13 14:00:00 | 20 | 0 | 903.6667 | 0 | 4065.1367 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0068 | 20.0069 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.1292
303 | 08/13 15:00:00 | 20 | 0 | 887.25 | 0 | 3873.4305 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0065 | 20.0065 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.076
304 | 08/13 16:00:00 | 20 | 0 | 853.5 | 0 | 3690.7524 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0062 | 20.0062 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 1.0252
305 | 08/13 17:00:00 | 20 | 0 | 785.6667 | 0 | 3516.6782 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0059 | 20.0059 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.97686
306 | 08/13 18:00:00 | 20 | 0 | 636.6667 | 0 | 3350.8129 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0056 | 20.0056 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.93078
307 | 08/13 19:00:00 | 20 | 0 | 330.4167 | 0 | 3192.7805 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0053 | 20.0054 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.88688
308 | 08/13 20:00:00 | 20 | 0 | 31.5833 | 0 | 3042.2149 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0051 | 20.0051 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.84506
309 | 08/13 21:00:00 | 20 | 0 | 0 | 0 | 2898.7644 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0048 | 20.0049 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.80521
310 | 08/13 22:00:00 | 20 | 0 | 0 | 0 | 2762.0937 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0046 | 20.0047 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.76725
311 | 08/13 23:00:00 | 20 | 0 | 0 | 0 | 2631.8799 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0044 | 20.0044 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.73108
312 | 08/13 24:00:00 | 20 | 0 | 0 | 0 | 2507.8093 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0042 | 20.0042 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.69661
313 | 08/14 01:00:00 | 20 | 0 | 0 | 0 | 2389.578 | 20 | 0 | 0 | 0 | 0 | 0 | 20.004 | 20.004 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.66377
314 | 08/14 02:00:00 | 20 | 0 | 0 | 0 | 2276.8984 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0038 | 20.0038 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.63247
315 | 08/14 03:00:00 | 20 | 0 | 0 | 0 | 2169.5062 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0036 | 20.0037 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.60264
316 | 08/14 04:00:00 | 20 | 0 | 0 | 0 | 2067.1594 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0035 | 20.0035 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.57421
317 | 08/14 05:00:00 | 20 | 0 | 0 | 0 | 1969.6323 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0033 | 20.0033 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.54712
318 | 08/14 06:00:00 | 20 | 0 | 0 | 0 | 1876.7057 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0031 | 20.0032 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.52131
319 | 08/14 07:00:00 | 20 | 0 | 181 | 0 | 1788.165 | 20 | 0 | 0 | 0 | 0 | 0 | 20.003 | 20.003 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.49671
320 | 08/14 08:00:00 | 20 | 0 | 551.0833 | 0 | 1703.8114 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0028 | 20.0029 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.47328
321 | 08/14 09:00:00 | 20 | 0 | 747.9167 | 0 | 1623.4555 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0027 | 20.0027 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.45096
322 | 08/14 10:00:00 | 20 | 0 | 835.0833 | 0 | 1546.9071 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0026 | 20.0026 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.4297
323 | 08/14 11:00:00 | 20 | 0 | 878.0833 | 0 | 1473.9808 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0025 | 20.0025 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.40944
324 | 08/14 12:00:00 | 20 | 0 | 899.5 | 0 | 1404.5001 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0023 | 20.0024 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.39014
325 | 08/14 13:00:00 | 20 | 0 | 907 | 0 | 1338.2945 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0022 | 20.0023 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.37175
326 | 08/14 14:00:00 | 20 | 0 | 903.6667 | 0 | 1275.199 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0021 | 20.0021 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.35422
327 | 08/14 15:00:00 | 20 | 0 | 887.25 | 0 | 1215.0583 | 20 | 0 | 0 | 0 | 0 | 0 | 20.002 | 20.002 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.33752
328 | 08/14 16:00:00 | 20 | 0 | 853.5 | 0 | 1157.7269 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0019 | 20.002 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.32159
329 | 08/14 17:00:00 | 20 | 0 | 785.6667 | 0 | 1103.0684 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0018 | 20.0019 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.30641
330 | 08/14 18:00:00 | 20 | 0 | 636.6667 | 0 | 1050.9564 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0018 | 20.0018 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.29193
331 | 08/14 19:00:00 | 20 | 0 | 330.4167 | 0 | 1001.2789 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0017 | 20.0017 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.27813
332 | 08/14 20:00:00 | 20 | 0 | 31.5833 | 0 | 953.9342 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0016 | 20.0016 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.26498
333 | 08/14 21:00:00 | 20 | 0 | 0 | 0 | 908.8296 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0015 | 20.0015 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.25245
334 | 08/14 22:00:00 | 20 | 0 | 0 | 0 | 865.8645 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0014 | 20.0015 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.24052
335 | 08/14 23:00:00 | 20 | 0 | 0 | 0 | 824.9324 | 20 | 0 | 0 | 0 | 0 | 0 | 20.0014 | 20.0014 | 3.076 | 0 | 3.076 | 3.076 | 3.076 | 3.076 | 3.076 | 0 | 0.22915
[13 empty] | 335 hrs | Average >> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 335 hrs | Average-all surfaces >> | [7 empty] | 2.0507 | 453595.0269
2699.7798
[13 empty] | 168 hrs | Average >> |  | 0 |  | 3.076 | 3.076 | 3.076 | 3.076 | 0
[13 empty] | 168 hrs | Average-all surfaces >> | [7 empty] | 2.0507

## ASHRAE 100 Rad
ASHRAE 1052RP Toolkit Test IntHeatGain
Data taken from T:\LB301-NET\ASHRAE 1052RP\1052 Toolkit Output
Step change in internal load
2700 W for 168 hours, 100% radiative
Hour | Time | ASHRAE 1052RP - 100% Radiative | Flux | ASHRAE 1052RP - 100% Radiative
1 | 0 | 20 | 0 | 0
2 | 3600 | 25.709 | 17.5609 | 948.2911
3 | 7200 | 27.1696 | 22.0538 | 1190.905
4 | 10800 | 28.0721 | 24.8296 | 1340.8006
5 | 14400 | 28.721 | 26.8258 | 1448.5953
6 | 18000 | 29.2283 | 28.3862 | 1532.8546
7 | 21600 | 29.6491 | 29.6805 | 1602.7481
8 | 25200 | 30.014 | 30.803 | 1663.3616
9 | 28800 | 30.3408 | 31.8082 | 1717.6421
10 | 32400 | 30.6399 | 32.7284 | 1767.3352
11 | 36000 | 30.9178 | 33.5832 | 1813.4946
12 | 39600 | 31.1784 | 34.3847 | 1856.7726
13 | 43200 | 31.4241 | 35.1405 | 1897.5873
14 | 46800 | 31.6567 | 35.8559 | 1936.2189
15 | 50400 | 31.8773 | 36.5346 | 1972.8659
16 | 54000 | 32.0869 | 37.1792 | 2007.678
17 | 57600 | 32.2861 | 37.7921 | 2040.7749
18 | 61200 | 32.4757 | 38.3751 | 2072.2571
19 | 64800 | 32.656 | 38.9299 | 2102.2127
20 | 68400 | 32.8276 | 39.4578 | 2130.7213
21 | 72000 | 32.991 | 39.9603 | 2157.8557
22 | 75600 | 33.1465 | 40.4386 | 2183.6841
23 | 79200 | 33.2945 | 40.8939 | 2208.2704
24 | 82800 | 33.4354 | 41.3273 | 2231.6749
25 | 86400 | 33.5695 | 41.7399 | 2253.9548
26 | 90000 | 33.6972 | 42.1327 | 2275.1643
27 | 93600 | 33.8188 | 42.5066 | 2295.355
28 | 97200 | 33.9345 | 42.8625 | 2314.5759
29 | 100800 | 34.0447 | 43.2014 | 2332.8736
30 | 104400 | 34.1495 | 43.5239 | 2350.2925
31 | 108000 | 34.2494 | 43.831 | 2366.8747
32 | 111600 | 34.3444 | 44.1233 | 2382.6605
33 | 115200 | 34.4349 | 44.4016 | 2397.6882
34 | 118800 | 34.521 | 44.6666 | 2411.9941
35 | 122400 | 34.603 | 44.9188 | 2425.6129
36 | 126000 | 34.681 | 45.1588 | 2438.5777
37 | 129600 | 34.7553 | 45.3874 | 2450.9198
38 | 133200 | 34.8261 | 45.605 | 2462.6691
39 | 136800 | 34.8934 | 45.8121 | 2473.8541
40 | 140400 | 34.9575 | 46.0093 | 2484.5019
41 | 144000 | 35.0185 | 46.197 | 2494.6384
42 | 147600 | 35.0766 | 46.3757 | 2504.288
43 | 151200 | 35.1319 | 46.5458 | 2513.4741
44 | 154800 | 35.1846 | 46.7078 | 2522.2191
45 | 158400 | 35.2347 | 46.8619 | 2530.5441
46 | 162000 | 35.2824 | 47.0087 | 2538.4692
47 | 165600 | 35.3278 | 47.1484 | 2546.0137
48 | 169200 | 35.3711 | 47.2814 | 2553.1959
49 | 172800 | 35.4122 | 47.408 | 2560.0331
50 | 176400 | 35.4514 | 47.5286 | 2566.542
51 | 180000 | 35.4887 | 47.6433 | 2572.7382
52 | 183600 | 35.5242 | 47.7525 | 2578.6369
53 | 187200 | 35.558 | 47.8565 | 2584.2522
54 | 190800 | 35.5902 | 47.9555 | 2589.5979
55 | 194400 | 35.6209 | 48.0498 | 2594.6868
56 | 198000 | 35.65 | 48.1395 | 2599.5313
57 | 201600 | 35.6778 | 48.2249 | 2604.1432
58 | 205200 | 35.7042 | 48.3062 | 2608.5335
59 | 208800 | 35.7294 | 48.3836 | 2612.713
60 | 212400 | 35.7533 | 48.4573 | 2616.6918
61 | 216000 | 35.7761 | 48.5274 | 2620.4794
62 | 219600 | 35.7978 | 48.5942 | 2624.0852
63 | 223200 | 35.8185 | 48.6577 | 2627.5178
64 | 226800 | 35.8382 | 48.7182 | 2630.7855
65 | 230400 | 35.8569 | 48.7759 | 2633.8963
66 | 234000 | 35.8747 | 48.8307 | 2636.8576
67 | 237600 | 35.8917 | 48.8829 | 2639.6768
68 | 241200 | 35.9079 | 48.9326 | 2642.3605
69 | 244800 | 35.9232 | 48.9799 | 2644.9154
70 | 248400 | 35.9379 | 49.025 | 2647.3475
71 | 252000 | 35.9518 | 49.0678 | 2649.6629
72 | 255600 | 35.9651 | 49.1086 | 2651.867
73 | 259200 | 35.9777 | 49.1475 | 2653.9653
74 | 262800 | 35.9898 | 49.1845 | 2655.9628
75 | 266400 | 36.0012 | 49.2197 | 2657.8643
76 | 270000 | 36.0121 | 49.2532 | 2659.6746
77 | 273600 | 36.0225 | 49.2851 | 2661.3979
78 | 277200 | 36.0324 | 49.3155 | 2663.0384
79 | 280800 | 36.0418 | 49.3444 | 2664.6002
80 | 284400 | 36.0507 | 49.372 | 2666.0869
81 | 288000 | 36.0592 | 49.3982 | 2667.5022
82 | 291600 | 36.0673 | 49.4231 | 2668.8496
83 | 295200 | 36.0751 | 49.4469 | 2670.1322
84 | 298800 | 36.0824 | 49.4695 | 2671.3533
85 | 302400 | 36.0894 | 49.491 | 2672.5157
86 | 306000 | 36.0961 | 49.5115 | 2673.6222
87 | 309600 | 36.1024 | 49.531 | 2674.6757
88 | 313200 | 36.1085 | 49.5496 | 2675.6785
89 | 316800 | 36.1142 | 49.5673 | 2676.6332
90 | 320400 | 36.1197 | 49.5841 | 2677.542
91 | 324000 | 36.1249 | 49.6001 | 2678.4071
92 | 327600 | 36.1298 | 49.6154 | 2679.2308
93 | 331200 | 36.1346 | 49.6299 | 2680.0148
94 | 334800 | 36.1391 | 49.6437 | 2680.7612
95 | 338400 | 36.1433 | 49.6569 | 2681.4718
96 | 342000 | 36.1474 | 49.6694 | 2682.1482
97 | 345600 | 36.1513 | 49.6813 | 2682.7921
98 | 349200 | 36.155 | 49.6927 | 2683.4052
99 | 352800 | 36.1585 | 49.7035 | 2683.9887
100 | 356400 | 36.1618 | 49.7138 | 2684.5443
101 | 360000 | 36.165 | 49.7236 | 2685.0731
102 | 363600 | 36.168 | 49.7329 | 2685.5766
103 | 367200 | 36.1709 | 49.7418 | 2686.0559
104 | 370800 | 36.1737 | 49.7502 | 2686.5122
105 | 374400 | 36.1763 | 49.7583 | 2686.9465
106 | 378000 | 36.1788 | 49.7659 | 2687.36
107 | 381600 | 36.1811 | 49.7732 | 2687.7536
108 | 385200 | 36.1834 | 49.7802 | 2688.1284
109 | 388800 | 36.1856 | 49.7868 | 2688.4851
110 | 392400 | 36.1876 | 49.793 | 2688.8247
111 | 396000 | 36.1895 | 49.799 | 2689.148
112 | 399600 | 36.1914 | 49.8047 | 2689.4557
113 | 403200 | 36.1932 | 49.8102 | 2689.7487
114 | 406800 | 36.1948 | 49.8153 | 2690.0276
115 | 410400 | 36.1964 | 49.8202 | 2690.2931
116 | 414000 | 36.198 | 49.8249 | 2690.5459
117 | 417600 | 36.1994 | 49.8294 | 2690.7865
118 | 421200 | 36.2008 | 49.8336 | 2691.0156
119 | 424800 | 36.2021 | 49.8377 | 2691.2336
120 | 428400 | 36.2033 | 49.8415 | 2691.4412
121 | 432000 | 36.2045 | 49.8452 | 2691.6388
122 | 435600 | 36.2057 | 49.8486 | 2691.827
123 | 439200 | 36.2068 | 49.852 | 2692.0061
124 | 442800 | 36.2078 | 49.8551 | 2692.1766
125 | 446400 | 36.2088 | 49.8581 | 2692.3389
126 | 450000 | 36.2097 | 49.861 | 2692.4934
127 | 453600 | 36.2106 | 49.8637 | 2692.6404
128 | 457200 | 36.2114 | 49.8663 | 2692.7805
129 | 460800 | 36.2122 | 49.8688 | 2692.9138
130 | 464400 | 36.213 | 49.8711 | 2693.0407
131 | 468000 | 36.2137 | 49.8734 | 2693.1615
132 | 471600 | 36.2144 | 49.8755 | 2693.2765
133 | 475200 | 36.2151 | 49.8775 | 2693.3859
134 | 478800 | 36.2157 | 49.8794 | 2693.4902
135 | 482400 | 36.2163 | 49.8813 | 2693.5894
136 | 486000 | 36.2169 | 49.883 | 2693.6838
137 | 489600 | 36.2174 | 49.8847 | 2693.7737
138 | 493200 | 36.2179 | 49.8863 | 2693.8593
139 | 496800 | 36.2184 | 49.8878 | 2693.9408
140 | 500400 | 36.2189 | 49.8892 | 2694.0184
141 | 504000 | 36.2193 | 49.8906 | 2694.0922
142 | 507600 | 36.2197 | 49.8919 | 2694.1625
143 | 511200 | 36.2201 | 49.8931 | 2694.2294
144 | 514800 | 36.2205 | 49.8943 | 2694.2932
145 | 518400 | 36.2209 | 49.8954 | 2694.3538
146 | 522000 | 36.2212 | 49.8965 | 2694.4115
147 | 525600 | 36.2216 | 49.8975 | 2694.4665
148 | 529200 | 36.2219 | 49.8985 | 2694.5188
149 | 532800 | 36.2222 | 49.8994 | 2694.5686
150 | 536400 | 36.2225 | 49.9003 | 2694.616
151 | 540000 | 36.2227 | 49.9011 | 2694.6612
152 | 543600 | 36.223 | 49.9019 | 2694.7042
153 | 547200 | 36.2232 | 49.9027 | 2694.7451
154 | 550800 | 36.2235 | 49.9034 | 2694.784
155 | 554400 | 36.2237 | 49.9041 | 2694.8211
156 | 558000 | 36.2239 | 49.9047 | 2694.8564
157 | 561600 | 36.2241 | 49.9054 | 2694.89
158 | 565200 | 36.2243 | 49.906 | 2694.922
159 | 568800 | 36.2245 | 49.9065 | 2694.9524
160 | 572400 | 36.2247 | 49.9071 | 2694.9814
161 | 576000 | 36.2248 | 49.9076 | 2695.009
162 | 579600 | 36.225 | 49.9081 | 2695.0353
163 | 583200 | 36.2251 | 49.9085 | 2695.0603
164 | 586800 | 36.2253 | 49.909 | 2695.0841
165 | 590400 | 36.2254 | 49.9094 | 2695.1067
166 | 594000 | 36.2255 | 49.9098 | 2695.1283
167 | 597600 | 36.2257 | 49.9102 | 2695.1488
168 | 601200 | 36.2258 | 49.9105 | 2695.1684
169 | 604800 | 36.2259 | 49.9109 | 2695.187
170 | 608400 | 30.517 | 32.3503 | 1746.9136
171 | 612000 | 29.0565 | 27.8577 | 1504.3166
172 | 615600 | 28.1542 | 25.0822 | 1354.4371
173 | 619200 | 27.5053 | 23.0863 | 1246.6577
174 | 622800 | 26.9981 | 21.5262 | 1162.4129
175 | 626400 | 26.5774 | 20.2321 | 1092.5332
176 | 630000 | 26.2126 | 19.1099 | 1031.9329
177 | 633600 | 25.8859 | 18.1049 | 977.6649
178 | 637200 | 25.5868 | 17.1849 | 927.9839
179 | 640800 | 25.3089 | 16.3303 | 881.8358
180 | 644400 | 25.0485 | 15.529 | 838.5686
181 | 648000 | 24.8028 | 14.7734 | 797.7642
182 | 651600 | 24.5703 | 14.0582 | 759.1425
183 | 655200 | 24.3497 | 13.3797 | 722.5048
184 | 658800 | 24.1402 | 12.7352 | 687.7016
185 | 662400 | 23.941 | 12.1225 | 654.6132
186 | 666000 | 23.7515 | 11.5396 | 623.139
187 | 669600 | 23.5712 | 10.985 | 593.1911
188 | 673200 | 23.3996 | 10.4572 | 564.6899
189 | 676800 | 23.2363 | 9.9549 | 537.5624
190 | 680400 | 23.0808 | 9.4767 | 511.7406
191 | 684000 | 22.9329 | 9.0215 | 487.1606
192 | 687600 | 22.792 | 8.5882 | 463.7621
193 | 691200 | 22.6579 | 8.1757 | 441.4879
194 | 694800 | 22.5302 | 7.783 | 420.2838
195 | 698400 | 22.4087 | 7.4092 | 400.0983
196 | 702000 | 22.293 | 7.0534 | 380.8823
197 | 705600 | 22.1829 | 6.7146 | 362.5893
198 | 709200 | 22.0781 | 6.3921 | 345.1749
199 | 712800 | 21.9783 | 6.0851 | 328.5969
200 | 716400 | 21.8832 | 5.7929 | 312.8152
201 | 720000 | 21.7928 | 5.5147 | 297.7914
202 | 723600 | 21.7067 | 5.2498 | 283.4891
203 | 727200 | 21.6247 | 4.9977 | 269.8738
204 | 730800 | 21.5467 | 4.7576 | 256.9124
205 | 734400 | 21.4724 | 4.5291 | 244.5734
206 | 738000 | 21.4017 | 4.3116 | 232.8271
207 | 741600 | 21.3344 | 4.1045 | 221.645
208 | 745200 | 21.2703 | 3.9074 | 210.9999
209 | 748800 | 21.2093 | 3.7197 | 200.866
210 | 752400 | 21.1512 | 3.5411 | 191.2189
211 | 756000 | 21.0959 | 3.371 | 182.0351
212 | 759600 | 21.0433 | 3.2091 | 173.2924
213 | 763200 | 20.9932 | 3.055 | 164.9695
214 | 766800 | 20.9455 | 2.9083 | 157.0464
215 | 770400 | 20.9001 | 2.7686 | 149.5038
216 | 774000 | 20.8568 | 2.6356 | 142.3235
217 | 777600 | 20.8157 | 2.509 | 135.488
218 | 781200 | 20.7765 | 2.3885 | 128.9809
219 | 784800 | 20.7392 | 2.2738 | 122.7862
220 | 788400 | 20.7037 | 2.1646 | 116.8891
221 | 792000 | 20.6699 | 2.0607 | 111.2751
222 | 795600 | 20.6377 | 1.9617 | 105.9308
223 | 799200 | 20.6071 | 1.8675 | 100.8432
224 | 802800 | 20.578 | 1.7778 | 96
225 | 806400 | 20.5502 | 1.6924 | 91.3893
226 | 810000 | 20.5238 | 1.6111 | 87.0001
227 | 813600 | 20.4986 | 1.5337 | 82.8217
228 | 817200 | 20.4747 | 1.4601 | 78.8439
229 | 820800 | 20.4519 | 1.3899 | 75.0572
230 | 824400 | 20.4302 | 1.3232 | 71.4524
231 | 828000 | 20.4095 | 1.2596 | 68.0207
232 | 831600 | 20.3898 | 1.1991 | 64.7538
233 | 835200 | 20.3711 | 1.1416 | 61.6439
234 | 838800 | 20.3533 | 1.0867 | 58.6832
235 | 842400 | 20.3363 | 1.0345 | 55.8648
236 | 846000 | 20.3202 | 0.9848 | 53.1818
237 | 849600 | 20.3048 | 0.9375 | 50.6276
238 | 853200 | 20.2902 | 0.8925 | 48.196
239 | 856800 | 20.2762 | 0.8497 | 45.8813
240 | 860400 | 20.263 | 0.8088 | 43.6777
241 | 864000 | 20.2503 | 0.77 | 41.58
242 | 867600 | 20.2383 | 0.733 | 39.583
243 | 871200 | 20.2269 | 0.6978 | 37.6819
244 | 874800 | 20.216 | 0.6643 | 35.8721
245 | 878400 | 20.2056 | 0.6324 | 34.1493
246 | 882000 | 20.1957 | 0.602 | 32.5092
247 | 885600 | 20.1863 | 0.5731 | 30.9478
248 | 889200 | 20.1774 | 0.5456 | 29.4615
249 | 892800 | 20.1688 | 0.5194 | 28.0465
250 | 896400 | 20.1607 | 0.4944 | 26.6995
251 | 900000 | 20.153 | 0.4707 | 25.4172
252 | 903600 | 20.1457 | 0.4481 | 24.1964
253 | 907200 | 20.1387 | 0.4266 | 23.0343
254 | 910800 | 20.132 | 0.4061 | 21.9281
255 | 914400 | 20.1257 | 0.3866 | 20.8749
256 | 918000 | 20.1196 | 0.368 | 19.8723
257 | 921600 | 20.1139 | 0.3503 | 18.9179
258 | 925200 | 20.1084 | 0.3335 | 18.0093
259 | 928800 | 20.1032 | 0.3175 | 17.1444
260 | 932400 | 20.0983 | 0.3022 | 16.321
261 | 936000 | 20.0935 | 0.2877 | 15.5371
262 | 939600 | 20.089 | 0.2739 | 14.7909
263 | 943200 | 20.0848 | 0.2608 | 14.0805
264 | 946800 | 20.0807 | 0.2482 | 13.4043
265 | 950400 | 20.0768 | 0.2363 | 12.7605
266 | 954000 | 20.0731 | 0.225 | 12.1476
267 | 957600 | 20.0696 | 0.2142 | 11.5642
268 | 961200 | 20.0663 | 0.2039 | 11.0088
269 | 964800 | 20.0631 | 0.1941 | 10.4801
270 | 968400 | 20.0601 | 0.1848 | 9.9767
271 | 972000 | 20.0572 | 0.1759 | 9.4976
272 | 975600 | 20.0544 | 0.1674 | 9.0414
273 | 979200 | 20.0518 | 0.1594 | 8.6072
274 | 982800 | 20.0493 | 0.1517 | 8.1938
275 | 986400 | 20.047 | 0.1444 | 7.8003
276 | 990000 | 20.0447 | 0.1375 | 7.4257
277 | 993600 | 20.0426 | 0.1309 | 7.069
278 | 997200 | 20.0405 | 0.1246 | 6.7295
279 | 1000800 | 20.0386 | 0.1186 | 6.4063
280 | 1004400 | 20.0367 | 0.1129 | 6.0986
281 | 1008000 | 20.035 | 0.1075 | 5.8057
282 | 1011600 | 20.0333 | 0.1023 | 5.5269
283 | 1015200 | 20.0317 | 0.0974 | 5.2614
284 | 1018800 | 20.0302 | 0.0928 | 5.0087
285 | 1022400 | 20.0287 | 0.0883 | 4.7682
286 | 1026000 | 20.0273 | 0.0841 | 4.5392
287 | 1029600 | 20.026 | 0.08 | 4.3212
288 | 1033200 | 20.0248 | 0.0762 | 4.1136
289 | 1036800 | 20.0236 | 0.0725 | 3.9161
290 | 1040400 | 20.0224 | 0.069 | 3.728
291 | 1044000 | 20.0214 | 0.0657 | 3.5489
292 | 1047600 | 20.0203 | 0.0626 | 3.3785
293 | 1051200 | 20.0194 | 0.0596 | 3.2162
294 | 1054800 | 20.0184 | 0.0567 | 3.0618
295 | 1058400 | 20.0175 | 0.054 | 2.9147
296 | 1062000 | 20.0167 | 0.0514 | 2.7747
297 | 1065600 | 20.0159 | 0.0489 | 2.6415
298 | 1069200 | 20.0151 | 0.0466 | 2.5146
299 | 1072800 | 20.0144 | 0.0443 | 2.3938
300 | 1076400 | 20.0137 | 0.0422 | 2.2789
301 | 1080000 | 20.0131 | 0.0402 | 2.1694
302 | 1083600 | 20.0124 | 0.0382 | 2.0652
303 | 1087200 | 20.0118 | 0.0364 | 1.966
304 | 1090800 | 20.0113 | 0.0347 | 1.8716
305 | 1094400 | 20.0107 | 0.033 | 1.7817
306 | 1098000 | 20.0102 | 0.0314 | 1.6961
307 | 1101600 | 20.0097 | 0.0299 | 1.6147
308 | 1105200 | 20.0093 | 0.0285 | 1.5371
309 | 1108800 | 20.0088 | 0.0271 | 1.4633
310 | 1112400 | 20.0084 | 0.0258 | 1.393
311 | 1116000 | 20.008 | 0.0246 | 1.3261
312 | 1119600 | 20.0076 | 0.0234 | 1.2624
313 | 1123200 | 20.0072 | 0.0223 | 1.2018
314 | 1126800 | 20.0069 | 0.0212 | 1.1441
315 | 1130400 | 20.0066 | 0.0202 | 1.0891
316 | 1134000 | 20.0062 | 0.0192 | 1.0368
317 | 1137600 | 20.0059 | 0.0183 | 0.987
318 | 1141200 | 20.0057 | 0.0174 | 0.9396
319 | 1144800 | 20.0054 | 0.0166 | 0.8945
320 | 1148400 | 20.0051 | 0.0158 | 0.8515
321 | 1152000 | 20.0049 | 0.015 | 0.8106
322 | 1155600 | 20.0046 | 0.0143 | 0.7717
323 | 1159200 | 20.0044 | 0.0136 | 0.7346
324 | 1162800 | 20.0042 | 0.013 | 0.6994
325 | 1166400 | 20.004 | 0.0123 | 0.6658
326 | 1170000 | 20.0038 | 0.0117 | 0.6338
327 | 1173600 | 20.0036 | 0.0112 | 0.6034
328 | 1177200 | 20.0035 | 0.0106 | 0.5744
329 | 1180800 | 20.0033 | 0.0101 | 0.5468
330 | 1184400 | 20.0031 | 0.0096 | 0.5205
331 | 1188000 | 20.003 | 0.0092 | 0.4955
332 | 1191600 | 20.0028 | 0.0087 | 0.4717
333 | 1195200 | 20.0027 | 0.0083 | 0.4491
334 | 1198800 | 20.0026 | 0.0079 | 0.4275
335 | 1202400 | 20.0025 | 0.0075 | 0.407
336 | 1206000 | 20.0023 | 0.0072 | 0.3874
337 | 1209600 | 20.0022 | 0.0068 | 0.3688

## ASHRAE 50 Rad
ASHRAE 1052RP Toolkit Test IntHeatGain
Data taken from T:\LB301-NET\ASHRAE 1052RP\1052 Toolkit Output
Step change in internal load
2700 W for 168 hours, 50% radiative
Hour | Time | ASHRAE 1052RP - 50% Radiative | Flux | ASHRAE 1052RP - 50% Radiative
1 | 0 | 20 | 0 | 1350
2 | 3600 | 22.849 | 8.7635 | 1823.2289
3 | 7200 | 23.5793 | 11.0099 | 1944.5359
4 | 10800 | 24.0305 | 12.3978 | 2019.4836
5 | 14400 | 24.355 | 13.3959 | 2073.381
6 | 18000 | 24.6086 | 14.1761 | 2115.5106
7 | 21600 | 24.819 | 14.8233 | 2150.4574
8 | 25200 | 25.0015 | 15.3845 | 2180.7642
9 | 28800 | 25.1649 | 15.8871 | 2207.9044
10 | 32400 | 25.3144 | 16.3472 | 2232.7509
11 | 36000 | 25.4534 | 16.7746 | 2255.8306
12 | 39600 | 25.5837 | 17.1754 | 2277.4697
13 | 43200 | 25.7065 | 17.5533 | 2297.877
14 | 46800 | 25.8228 | 17.911 | 2317.1928
15 | 50400 | 25.9331 | 18.2503 | 2335.5163
16 | 54000 | 26.0379 | 18.5726 | 2352.9224
17 | 57600 | 26.1375 | 18.8791 | 2369.4708
18 | 61200 | 26.2323 | 19.1706 | 2385.2119
19 | 64800 | 26.3225 | 19.448 | 2400.1897
20 | 68400 | 26.4083 | 19.7119 | 2414.444
21 | 72000 | 26.49 | 19.9632 | 2428.0112
22 | 75600 | 26.5677 | 20.2023 | 2440.9254
23 | 79200 | 26.6417 | 20.43 | 2453.2185
24 | 82800 | 26.7122 | 20.6467 | 2464.9208
25 | 86400 | 26.7793 | 20.853 | 2476.0608
26 | 90000 | 26.8431 | 21.0494 | 2486.6655
27 | 93600 | 26.9039 | 21.2363 | 2496.7609
28 | 97200 | 26.9617 | 21.4143 | 2506.3713
29 | 100800 | 27.0168 | 21.5837 | 2515.5202
30 | 104400 | 27.0692 | 21.745 | 2524.2296
31 | 108000 | 27.1192 | 21.8985 | 2532.5207
32 | 111600 | 27.1667 | 22.0447 | 2540.4136
33 | 115200 | 27.2119 | 22.1838 | 2547.9274
34 | 118800 | 27.255 | 22.3163 | 2555.0804
35 | 122400 | 27.296 | 22.4424 | 2561.8898
36 | 126000 | 27.335 | 22.5624 | 2568.3722
37 | 129600 | 27.3721 | 22.6767 | 2574.5432
38 | 133200 | 27.4075 | 22.7855 | 2580.4179
39 | 136800 | 27.4412 | 22.8891 | 2586.0104
40 | 140400 | 27.4732 | 22.9877 | 2591.3343
41 | 144000 | 27.5037 | 23.0815 | 2596.4025
42 | 147600 | 27.5328 | 23.1709 | 2601.2273
43 | 151200 | 27.5604 | 23.2559 | 2605.8204
44 | 154800 | 27.5868 | 23.3369 | 2610.1929
45 | 158400 | 27.6118 | 23.414 | 2614.3554
46 | 162000 | 27.6357 | 23.4874 | 2618.318
47 | 165600 | 27.6584 | 23.5572 | 2622.0902
48 | 169200 | 27.68 | 23.6237 | 2625.6813
49 | 172800 | 27.7006 | 23.687 | 2629.0999
50 | 176400 | 27.7202 | 23.7473 | 2632.3543
51 | 180000 | 27.7388 | 23.8047 | 2635.4525
52 | 183600 | 27.7566 | 23.8593 | 2638.4018
53 | 187200 | 27.7735 | 23.9113 | 2641.2095
54 | 190800 | 27.7896 | 23.9608 | 2643.8823
55 | 194400 | 27.8049 | 24.0079 | 2646.4268
56 | 198000 | 27.8195 | 24.0528 | 2648.849
57 | 201600 | 27.8334 | 24.0955 | 2651.1549
58 | 205200 | 27.8466 | 24.1361 | 2653.3501
59 | 208800 | 27.8592 | 24.1748 | 2655.4399
60 | 212400 | 27.8711 | 24.2117 | 2657.4292
61 | 216000 | 27.8825 | 24.2467 | 2659.3231
62 | 219600 | 27.8934 | 24.2801 | 2661.1259
63 | 223200 | 27.9037 | 24.3119 | 2662.8422
64 | 226800 | 27.9136 | 24.3421 | 2664.4761
65 | 230400 | 27.9229 | 24.371 | 2666.0315
66 | 234000 | 27.9319 | 24.3984 | 2667.5122
67 | 237600 | 27.9403 | 24.4245 | 2668.9217
68 | 241200 | 27.9484 | 24.4493 | 2670.2636
69 | 244800 | 27.9561 | 24.473 | 2671.541
70 | 248400 | 27.9634 | 24.4955 | 2672.7571
71 | 252000 | 27.9704 | 24.5169 | 2673.9148
72 | 255600 | 27.977 | 24.5373 | 2675.0169
73 | 259200 | 27.9833 | 24.5568 | 2676.066
74 | 262800 | 27.9894 | 24.5753 | 2677.0647
75 | 266400 | 27.9951 | 24.5929 | 2678.0155
76 | 270000 | 28.0005 | 24.6096 | 2678.9206
77 | 273600 | 28.0057 | 24.6256 | 2679.7823
78 | 277200 | 28.0107 | 24.6408 | 2680.6026
79 | 280800 | 28.0154 | 24.6552 | 2681.3834
80 | 284400 | 28.0198 | 24.669 | 2682.1268
81 | 288000 | 28.0241 | 24.6821 | 2682.8345
82 | 291600 | 28.0282 | 24.6946 | 2683.5081
83 | 295200 | 28.032 | 24.7065 | 2684.1495
84 | 298800 | 28.0357 | 24.7178 | 2684.76
85 | 302400 | 28.0392 | 24.7285 | 2685.3412
86 | 306000 | 28.0425 | 24.7388 | 2685.8945
87 | 309600 | 28.0457 | 24.7485 | 2686.4212
88 | 313200 | 28.0487 | 24.7578 | 2686.9226
89 | 316800 | 28.0516 | 24.7667 | 2687.3999
90 | 320400 | 28.0543 | 24.7751 | 2687.8543
91 | 324000 | 28.0569 | 24.7831 | 2688.2869
92 | 327600 | 28.0594 | 24.7907 | 2688.6987
93 | 331200 | 28.0618 | 24.798 | 2689.0908
94 | 334800 | 28.064 | 24.8049 | 2689.464
95 | 338400 | 28.0661 | 24.8115 | 2689.8192
96 | 342000 | 28.0682 | 24.8177 | 2690.1575
97 | 345600 | 28.0701 | 24.8237 | 2690.4794
98 | 349200 | 28.072 | 24.8294 | 2690.7859
99 | 352800 | 28.0737 | 24.8348 | 2691.0777
100 | 356400 | 28.0754 | 24.8399 | 2691.3555
101 | 360000 | 28.077 | 24.8448 | 2691.6199
102 | 363600 | 28.0785 | 24.8495 | 2691.8717
103 | 367200 | 28.0799 | 24.8539 | 2692.1113
104 | 370800 | 28.0813 | 24.8581 | 2692.3394
105 | 374400 | 28.0826 | 24.8622 | 2692.5566
106 | 378000 | 28.0839 | 24.866 | 2692.7634
107 | 381600 | 28.0851 | 24.8696 | 2692.9602
108 | 385200 | 28.0862 | 24.8731 | 2693.1475
109 | 388800 | 28.0873 | 24.8764 | 2693.3259
110 | 392400 | 28.0883 | 24.8795 | 2693.4957
111 | 396000 | 28.0893 | 24.8825 | 2693.6573
112 | 399600 | 28.0902 | 24.8854 | 2693.8112
113 | 403200 | 28.0911 | 24.8881 | 2693.9577
114 | 406800 | 28.0919 | 24.8907 | 2694.0972
115 | 410400 | 28.0927 | 24.8931 | 2694.2299
116 | 414000 | 28.0935 | 24.8955 | 2694.3563
117 | 417600 | 28.0942 | 24.8977 | 2694.4766
118 | 421200 | 28.0949 | 24.8998 | 2694.5911
119 | 424800 | 28.0955 | 24.9019 | 2694.7002
120 | 428400 | 28.0962 | 24.9038 | 2694.804
121 | 432000 | 28.0968 | 24.9056 | 2694.9028
122 | 435600 | 28.0973 | 24.9073 | 2694.9968
123 | 439200 | 28.0979 | 24.909 | 2695.0864
124 | 442800 | 28.0984 | 24.9106 | 2695.1716
125 | 446400 | 28.0989 | 24.9121 | 2695.2528
126 | 450000 | 28.0993 | 24.9135 | 2695.33
127 | 453600 | 28.0998 | 24.9149 | 2695.4036
128 | 457200 | 28.1002 | 24.9162 | 2695.4736
129 | 460800 | 28.1006 | 24.9174 | 2695.5402
130 | 464400 | 28.101 | 24.9186 | 2695.6037
131 | 468000 | 28.1013 | 24.9197 | 2695.6641
132 | 471600 | 28.1017 | 24.9208 | 2695.7216
133 | 475200 | 28.102 | 24.9218 | 2695.7763
134 | 478800 | 28.1023 | 24.9227 | 2695.8284
135 | 482400 | 28.1026 | 24.9237 | 2695.878
136 | 486000 | 28.1029 | 24.9245 | 2695.9253
137 | 489600 | 28.1032 | 24.9254 | 2695.9702
138 | 493200 | 28.1034 | 24.9262 | 2696.013
139 | 496800 | 28.1037 | 24.9269 | 2696.0538
140 | 500400 | 28.1039 | 24.9276 | 2696.0925
141 | 504000 | 28.1041 | 24.9283 | 2696.1295
142 | 507600 | 28.1043 | 24.929 | 2696.1646
143 | 511200 | 28.1045 | 24.9296 | 2696.1981
144 | 514800 | 28.1047 | 24.9302 | 2696.2299
145 | 518400 | 28.1049 | 24.9307 | 2696.2603
146 | 522000 | 28.1051 | 24.9313 | 2696.2891
147 | 525600 | 28.1053 | 24.9318 | 2696.3166
148 | 529200 | 28.1054 | 24.9323 | 2696.3428
149 | 532800 | 28.1056 | 24.9327 | 2696.3677
150 | 536400 | 28.1057 | 24.9332 | 2696.3914
151 | 540000 | 28.1058 | 24.9336 | 2696.4139
152 | 543600 | 28.106 | 24.934 | 2696.4354
153 | 547200 | 28.1061 | 24.9344 | 2696.4559
154 | 550800 | 28.1062 | 24.9347 | 2696.4754
155 | 554400 | 28.1063 | 24.9351 | 2696.4939
156 | 558000 | 28.1064 | 24.9354 | 2696.5115
157 | 561600 | 28.1065 | 24.9357 | 2696.5283
158 | 565200 | 28.1066 | 24.936 | 2696.5443
159 | 568800 | 28.1067 | 24.9363 | 2696.5596
160 | 572400 | 28.1068 | 24.9366 | 2696.574
161 | 576000 | 28.1069 | 24.9368 | 2696.5878
162 | 579600 | 28.107 | 24.9371 | 2696.601
163 | 583200 | 28.1071 | 24.9373 | 2696.6135
164 | 586800 | 28.1071 | 24.9375 | 2696.6254
165 | 590400 | 28.1072 | 24.9377 | 2696.6367
166 | 594000 | 28.1073 | 24.9379 | 2696.6475
167 | 597600 | 28.1073 | 24.9381 | 2696.6578
168 | 601200 | 28.1074 | 24.9383 | 2696.6675
169 | 604800 | 28.1074 | 24.9385 | 1346.6769
170 | 608400 | 25.2585 | 16.1751 | 873.4568
171 | 612000 | 24.5282 | 13.9289 | 752.1583
172 | 615600 | 24.0771 | 12.5411 | 677.2185
173 | 619200 | 23.7526 | 11.5431 | 623.3288
174 | 622800 | 23.4991 | 10.7631 | 581.2065
175 | 626400 | 23.2887 | 10.116 | 546.2666
176 | 630000 | 23.1063 | 9.5549 | 515.9665
177 | 633600 | 22.9429 | 9.0525 | 488.8325
178 | 637200 | 22.7934 | 8.5924 | 463.9919
179 | 640800 | 22.6545 | 8.1651 | 440.9179
180 | 644400 | 22.5242 | 7.7645 | 419.2843
181 | 648000 | 22.4014 | 7.3867 | 398.8821
182 | 651600 | 22.2851 | 7.0291 | 379.5712
183 | 655200 | 22.1749 | 6.6899 | 361.2524
184 | 658800 | 22.0701 | 6.3676 | 343.8508
185 | 662400 | 21.9705 | 6.0612 | 327.3066
186 | 666000 | 21.8757 | 5.7698 | 311.5695
187 | 669600 | 21.7856 | 5.4925 | 296.5955
188 | 673200 | 21.6998 | 5.2286 | 282.3449
189 | 676800 | 21.6181 | 4.9774 | 268.7812
190 | 680400 | 21.5404 | 4.7383 | 255.8703
191 | 684000 | 21.4664 | 4.5107 | 243.5803
192 | 687600 | 21.396 | 4.2941 | 231.881
193 | 691200 | 21.329 | 4.0879 | 220.7439
194 | 694800 | 21.2651 | 3.8915 | 210.1419
195 | 698400 | 21.2044 | 3.7046 | 200.0491
196 | 702000 | 21.1465 | 3.5267 | 190.4412
197 | 705600 | 21.0915 | 3.3573 | 181.2947
198 | 709200 | 21.039 | 3.1961 | 172.5875
199 | 712800 | 20.9891 | 3.0426 | 164.2985
200 | 716400 | 20.9416 | 2.8964 | 156.4076
201 | 720000 | 20.8964 | 2.7573 | 148.8957
202 | 723600 | 20.8533 | 2.6249 | 141.7446
203 | 727200 | 20.8124 | 2.4988 | 134.9369
204 | 730800 | 20.7733 | 2.3788 | 128.4562
205 | 734400 | 20.7362 | 2.2646 | 122.2867
206 | 738000 | 20.7008 | 2.1558 | 116.4136
207 | 741600 | 20.6672 | 2.0523 | 110.8225
208 | 745200 | 20.6351 | 1.9537 | 105.4999
209 | 748800 | 20.6046 | 1.8599 | 100.433
210 | 752400 | 20.5756 | 1.7705 | 95.6094
211 | 756000 | 20.548 | 1.6855 | 91.0175
212 | 759600 | 20.5216 | 1.6046 | 86.6462
213 | 763200 | 20.4966 | 1.5275 | 82.4848
214 | 766800 | 20.4727 | 1.4541 | 78.5232
215 | 770400 | 20.45 | 1.3843 | 74.7519
216 | 774000 | 20.4284 | 1.3178 | 71.1618
217 | 777600 | 20.4078 | 1.2545 | 67.744
218 | 781200 | 20.3883 | 1.1943 | 64.4904
219 | 784800 | 20.3696 | 1.1369 | 61.3931
220 | 788400 | 20.3519 | 1.0823 | 58.4445
221 | 792000 | 20.335 | 1.0303 | 55.6376
222 | 795600 | 20.3189 | 0.9808 | 52.9654
223 | 799200 | 20.3036 | 0.9337 | 50.4216
224 | 802800 | 20.289 | 0.8889 | 48
225 | 806400 | 20.2751 | 0.8462 | 45.6947
226 | 810000 | 20.2619 | 0.8056 | 43.5
227 | 813600 | 20.2493 | 0.7669 | 41.4108
228 | 817200 | 20.2373 | 0.73 | 39.422
229 | 820800 | 20.2259 | 0.695 | 37.5286
230 | 824400 | 20.2151 | 0.6616 | 35.7262
231 | 828000 | 20.2048 | 0.6298 | 34.0104
232 | 831600 | 20.1949 | 0.5996 | 32.3769
233 | 835200 | 20.1856 | 0.5708 | 30.8219
234 | 838800 | 20.1766 | 0.5434 | 29.3416
235 | 842400 | 20.1682 | 0.5173 | 27.9324
236 | 846000 | 20.1601 | 0.4924 | 26.5909
237 | 849600 | 20.1524 | 0.4688 | 25.3138
238 | 853200 | 20.1451 | 0.4463 | 24.098
239 | 856800 | 20.1381 | 0.4248 | 22.9406
240 | 860400 | 20.1315 | 0.4044 | 21.8389
241 | 864000 | 20.1252 | 0.385 | 20.79
242 | 867600 | 20.1192 | 0.3665 | 19.7915
243 | 871200 | 20.1134 | 0.3489 | 18.841
244 | 874800 | 20.108 | 0.3321 | 17.9361
245 | 878400 | 20.1028 | 0.3162 | 17.0746
246 | 882000 | 20.0979 | 0.301 | 16.2546
247 | 885600 | 20.0932 | 0.2866 | 15.4739
248 | 889200 | 20.0887 | 0.2728 | 14.7307
249 | 892800 | 20.0844 | 0.2597 | 14.0232
250 | 896400 | 20.0804 | 0.2472 | 13.3497
251 | 900000 | 20.0765 | 0.2353 | 12.7086
252 | 903600 | 20.0728 | 0.224 | 12.0982
253 | 907200 | 20.0693 | 0.2133 | 11.5172
254 | 910800 | 20.066 | 0.203 | 10.964
255 | 914400 | 20.0628 | 0.1933 | 10.4375
256 | 918000 | 20.0598 | 0.184 | 9.9362
257 | 921600 | 20.0569 | 0.1752 | 9.459
258 | 925200 | 20.0542 | 0.1668 | 9.0047
259 | 928800 | 20.0516 | 0.1587 | 8.5722
260 | 932400 | 20.0491 | 0.1511 | 8.1605
261 | 936000 | 20.0468 | 0.1439 | 7.7686
262 | 939600 | 20.0445 | 0.137 | 7.3955
263 | 943200 | 20.0424 | 0.1304 | 7.0403
264 | 946800 | 20.0403 | 0.1241 | 6.7021
265 | 950400 | 20.0384 | 0.1182 | 6.3802
266 | 954000 | 20.0366 | 0.1125 | 6.0738
267 | 957600 | 20.0348 | 0.1071 | 5.7821
268 | 961200 | 20.0331 | 0.1019 | 5.5044
269 | 964800 | 20.0315 | 0.097 | 5.24
270 | 968400 | 20.03 | 0.0924 | 4.9884
271 | 972000 | 20.0286 | 0.0879 | 4.7488
272 | 975600 | 20.0272 | 0.0837 | 4.5207
273 | 979200 | 20.0259 | 0.0797 | 4.3036
274 | 982800 | 20.0247 | 0.0759 | 4.0969
275 | 986400 | 20.0235 | 0.0722 | 3.9001
276 | 990000 | 20.0224 | 0.0688 | 3.7128
277 | 993600 | 20.0213 | 0.0655 | 3.5345
278 | 997200 | 20.0203 | 0.0623 | 3.3648
279 | 1000800 | 20.0193 | 0.0593 | 3.2032
280 | 1004400 | 20.0184 | 0.0565 | 3.0493
281 | 1008000 | 20.0175 | 0.0538 | 2.9029
282 | 1011600 | 20.0166 | 0.0512 | 2.7634
283 | 1015200 | 20.0158 | 0.0487 | 2.6307
284 | 1018800 | 20.0151 | 0.0464 | 2.5044
285 | 1022400 | 20.0144 | 0.0441 | 2.3841
286 | 1026000 | 20.0137 | 0.042 | 2.2696
287 | 1029600 | 20.013 | 0.04 | 2.1606
288 | 1033200 | 20.0124 | 0.0381 | 2.0568
289 | 1036800 | 20.0118 | 0.0363 | 1.958
290 | 1040400 | 20.0112 | 0.0345 | 1.864
291 | 1044000 | 20.0107 | 0.0329 | 1.7745
292 | 1047600 | 20.0102 | 0.0313 | 1.6892
293 | 1051200 | 20.0097 | 0.0298 | 1.6081
294 | 1054800 | 20.0092 | 0.0283 | 1.5309
295 | 1058400 | 20.0088 | 0.027 | 1.4574
296 | 1062000 | 20.0084 | 0.0257 | 1.3874
297 | 1065600 | 20.008 | 0.0245 | 1.3207
298 | 1069200 | 20.0076 | 0.0233 | 1.2573
299 | 1072800 | 20.0072 | 0.0222 | 1.1969
300 | 1076400 | 20.0069 | 0.0211 | 1.1394
301 | 1080000 | 20.0065 | 0.0201 | 1.0847
302 | 1083600 | 20.0062 | 0.0191 | 1.0326
303 | 1087200 | 20.0059 | 0.0182 | 0.983
304 | 1090800 | 20.0056 | 0.0173 | 0.9358
305 | 1094400 | 20.0054 | 0.0165 | 0.8909
306 | 1098000 | 20.0051 | 0.0157 | 0.8481
307 | 1101600 | 20.0049 | 0.015 | 0.8073
308 | 1105200 | 20.0046 | 0.0142 | 0.7686
309 | 1108800 | 20.0044 | 0.0135 | 0.7317
310 | 1112400 | 20.0042 | 0.0129 | 0.6965
311 | 1116000 | 20.004 | 0.0123 | 0.6631
312 | 1119600 | 20.0038 | 0.0117 | 0.6312
313 | 1123200 | 20.0036 | 0.0111 | 0.6009
314 | 1126800 | 20.0034 | 0.0106 | 0.572
315 | 1130400 | 20.0033 | 0.0101 | 0.5446
316 | 1134000 | 20.0031 | 0.0096 | 0.5184
317 | 1137600 | 20.003 | 0.0091 | 0.4935
318 | 1141200 | 20.0028 | 0.0087 | 0.4698
319 | 1144800 | 20.0027 | 0.0083 | 0.4472
320 | 1148400 | 20.0026 | 0.0079 | 0.4258
321 | 1152000 | 20.0024 | 0.0075 | 0.4053
322 | 1155600 | 20.0023 | 0.0071 | 0.3859
323 | 1159200 | 20.0022 | 0.0068 | 0.3673
324 | 1162800 | 20.0021 | 0.0065 | 0.3497
325 | 1166400 | 20.002 | 0.0062 | 0.3329
326 | 1170000 | 20.0019 | 0.0059 | 0.3169
327 | 1173600 | 20.0018 | 0.0056 | 0.3017
328 | 1177200 | 20.0017 | 0.0053 | 0.2872
329 | 1180800 | 20.0016 | 0.0051 | 0.2734
330 | 1184400 | 20.0016 | 0.0048 | 0.2603
331 | 1188000 | 20.0015 | 0.0046 | 0.2478
332 | 1191600 | 20.0014 | 0.0044 | 0.2359
333 | 1195200 | 20.0014 | 0.0042 | 0.2245
334 | 1198800 | 20.0013 | 0.004 | 0.2138
335 | 1202400 | 20.0012 | 0.0038 | 0.2035
336 | 1206000 | 20.0012 | 0.0036 | 0.1937
337 | 1209600 | 20.0011 | 0.0034 | 0.1844

## ASHRAE 100 Conv
ASHRAE 1052RP Toolkit Test IntHeatGain
Data taken from T:\LB301-NET\ASHRAE 1052RP\1052 Toolkit Output
Step change in internal load
2700 W for 168 hours, 100% convective
Hour | Time | ASHRAE 1052RP - 100% Convective | Flux | ASHRAE 1052RP - 100% Convective
1 | 0 | 20 | 0 | 2700
2 | 3600 | 20 | 0 | 2700
3 | 7200 | 20 | 0 | 2700
4 | 10800 | 20 | 0 | 2700
5 | 14400 | 20 | 0 | 2700
6 | 18000 | 20 | 0 | 2700
7 | 21600 | 20 | 0 | 2700
8 | 25200 | 20 | 0 | 2700
9 | 28800 | 20 | 0 | 2700
10 | 32400 | 20 | 0 | 2700
11 | 36000 | 20 | 0 | 2700
12 | 39600 | 20 | 0 | 2700
13 | 43200 | 20 | 0 | 2700
14 | 46800 | 20 | 0 | 2700
15 | 50400 | 20 | 0 | 2700
16 | 54000 | 20 | 0 | 2700
17 | 57600 | 20 | 0 | 2700
18 | 61200 | 20 | 0 | 2700
19 | 64800 | 20 | 0 | 2700
20 | 68400 | 20 | 0 | 2700
21 | 72000 | 20 | 0 | 2700
22 | 75600 | 20 | 0 | 2700
23 | 79200 | 20 | 0 | 2700
24 | 82800 | 20 | 0 | 2700
25 | 86400 | 20 | 0 | 2700
26 | 90000 | 20 | 0 | 2700
27 | 93600 | 20 | 0 | 2700
28 | 97200 | 20 | 0 | 2700
29 | 100800 | 20 | 0 | 2700
30 | 104400 | 20 | 0 | 2700
31 | 108000 | 20 | 0 | 2700
32 | 111600 | 20 | 0 | 2700
33 | 115200 | 20 | 0 | 2700
34 | 118800 | 20 | 0 | 2700
35 | 122400 | 20 | 0 | 2700
36 | 126000 | 20 | 0 | 2700
37 | 129600 | 20 | 0 | 2700
38 | 133200 | 20 | 0 | 2700
39 | 136800 | 20 | 0 | 2700
40 | 140400 | 20 | 0 | 2700
41 | 144000 | 20 | 0 | 2700
42 | 147600 | 20 | 0 | 2700
43 | 151200 | 20 | 0 | 2700
44 | 154800 | 20 | 0 | 2700
45 | 158400 | 20 | 0 | 2700
46 | 162000 | 20 | 0 | 2700
47 | 165600 | 20 | 0 | 2700
48 | 169200 | 20 | 0 | 2700
49 | 172800 | 20 | 0 | 2700
50 | 176400 | 20 | 0 | 2700
51 | 180000 | 20 | 0 | 2700
52 | 183600 | 20 | 0 | 2700
53 | 187200 | 20 | 0 | 2700
54 | 190800 | 20 | 0 | 2700
55 | 194400 | 20 | 0 | 2700
56 | 198000 | 20 | 0 | 2700
57 | 201600 | 20 | 0 | 2700
58 | 205200 | 20 | 0 | 2700
59 | 208800 | 20 | 0 | 2700
60 | 212400 | 20 | 0 | 2700
61 | 216000 | 20 | 0 | 2700
62 | 219600 | 20 | 0 | 2700
63 | 223200 | 20 | 0 | 2700
64 | 226800 | 20 | 0 | 2700
65 | 230400 | 20 | 0 | 2700
66 | 234000 | 20 | 0 | 2700
67 | 237600 | 20 | 0 | 2700
68 | 241200 | 20 | 0 | 2700
69 | 244800 | 20 | 0 | 2700
70 | 248400 | 20 | 0 | 2700
71 | 252000 | 20 | 0 | 2700
72 | 255600 | 20 | 0 | 2700
73 | 259200 | 20 | 0 | 2700
74 | 262800 | 20 | 0 | 2700
75 | 266400 | 20 | 0 | 2700
76 | 270000 | 20 | 0 | 2700
77 | 273600 | 20 | 0 | 2700
78 | 277200 | 20 | 0 | 2700
79 | 280800 | 20 | 0 | 2700
80 | 284400 | 20 | 0 | 2700
81 | 288000 | 20 | 0 | 2700
82 | 291600 | 20 | 0 | 2700
83 | 295200 | 20 | 0 | 2700
84 | 298800 | 20 | 0 | 2700
85 | 302400 | 20 | 0 | 2700
86 | 306000 | 20 | 0 | 2700
87 | 309600 | 20 | 0 | 2700
88 | 313200 | 20 | 0 | 2700
89 | 316800 | 20 | 0 | 2700
90 | 320400 | 20 | 0 | 2700
91 | 324000 | 20 | 0 | 2700
92 | 327600 | 20 | 0 | 2700
93 | 331200 | 20 | 0 | 2700
94 | 334800 | 20 | 0 | 2700
95 | 338400 | 20 | 0 | 2700
96 | 342000 | 20 | 0 | 2700
97 | 345600 | 20 | 0 | 2700
98 | 349200 | 20 | 0 | 2700
99 | 352800 | 20 | 0 | 2700
100 | 356400 | 20 | 0 | 2700
101 | 360000 | 20 | 0 | 2700
102 | 363600 | 20 | 0 | 2700
103 | 367200 | 20 | 0 | 2700
104 | 370800 | 20 | 0 | 2700
105 | 374400 | 20 | 0 | 2700
106 | 378000 | 20 | 0 | 2700
107 | 381600 | 20 | 0 | 2700
108 | 385200 | 20 | 0 | 2700
109 | 388800 | 20 | 0 | 2700
110 | 392400 | 20 | 0 | 2700
111 | 396000 | 20 | 0 | 2700
112 | 399600 | 20 | 0 | 2700
113 | 403200 | 20 | 0 | 2700
114 | 406800 | 20 | 0 | 2700
115 | 410400 | 20 | 0 | 2700
116 | 414000 | 20 | 0 | 2700
117 | 417600 | 20 | 0 | 2700
118 | 421200 | 20 | 0 | 2700
119 | 424800 | 20 | 0 | 2700
120 | 428400 | 20 | 0 | 2700
121 | 432000 | 20 | 0 | 2700
122 | 435600 | 20 | 0 | 2700
123 | 439200 | 20 | 0 | 2700
124 | 442800 | 20 | 0 | 2700
125 | 446400 | 20 | 0 | 2700
126 | 450000 | 20 | 0 | 2700
127 | 453600 | 20 | 0 | 2700
128 | 457200 | 20 | 0 | 2700
129 | 460800 | 20 | 0 | 2700
130 | 464400 | 20 | 0 | 2700
131 | 468000 | 20 | 0 | 2700
132 | 471600 | 20 | 0 | 2700
133 | 475200 | 20 | 0 | 2700
134 | 478800 | 20 | 0 | 2700
135 | 482400 | 20 | 0 | 2700
136 | 486000 | 20 | 0 | 2700
137 | 489600 | 20 | 0 | 2700
138 | 493200 | 20 | 0 | 2700
139 | 496800 | 20 | 0 | 2700
140 | 500400 | 20 | 0 | 2700
141 | 504000 | 20 | 0 | 2700
142 | 507600 | 20 | 0 | 2700
143 | 511200 | 20 | 0 | 2700
144 | 514800 | 20 | 0 | 2700
145 | 518400 | 20 | 0 | 2700
146 | 522000 | 20 | 0 | 2700
147 | 525600 | 20 | 0 | 2700
148 | 529200 | 20 | 0 | 2700
149 | 532800 | 20 | 0 | 2700
150 | 536400 | 20 | 0 | 2700
151 | 540000 | 20 | 0 | 2700
152 | 543600 | 20 | 0 | 2700
153 | 547200 | 20 | 0 | 2700
154 | 550800 | 20 | 0 | 2700
155 | 554400 | 20 | 0 | 2700
156 | 558000 | 20 | 0 | 2700
157 | 561600 | 20 | 0 | 2700
158 | 565200 | 20 | 0 | 2700
159 | 568800 | 20 | 0 | 2700
160 | 572400 | 20 | 0 | 2700
161 | 576000 | 20 | 0 | 2700
162 | 579600 | 20 | 0 | 2700
163 | 583200 | 20 | 0 | 2700
164 | 586800 | 20 | 0 | 2700
165 | 590400 | 20 | 0 | 2700
166 | 594000 | 20 | 0 | 2700
167 | 597600 | 20 | 0 | 2700
168 | 601200 | 20 | 0 | 2700
169 | 604800 | 20 | 0 | 0
170 | 608400 | 20 | 0 | 0
171 | 612000 | 20 | 0 | 0
172 | 615600 | 20 | 0 | 0
173 | 619200 | 20 | 0 | 0
174 | 622800 | 20 | 0 | 0
175 | 626400 | 20 | 0 | 0
176 | 630000 | 20 | 0 | 0
177 | 633600 | 20 | 0 | 0
178 | 637200 | 20 | 0 | 0
179 | 640800 | 20 | 0 | 0
180 | 644400 | 20 | 0 | 0
181 | 648000 | 20 | 0 | 0
182 | 651600 | 20 | 0 | 0
183 | 655200 | 20 | 0 | 0
184 | 658800 | 20 | 0 | 0
185 | 662400 | 20 | 0 | 0
186 | 666000 | 20 | 0 | 0
187 | 669600 | 20 | 0 | 0
188 | 673200 | 20 | 0 | 0
189 | 676800 | 20 | 0 | 0
190 | 680400 | 20 | 0 | 0
191 | 684000 | 20 | 0 | 0
192 | 687600 | 20 | 0 | 0
193 | 691200 | 20 | 0 | 0
194 | 694800 | 20 | 0 | 0
195 | 698400 | 20 | 0 | 0
196 | 702000 | 20 | 0 | 0
197 | 705600 | 20 | 0 | 0
198 | 709200 | 20 | 0 | 0
199 | 712800 | 20 | 0 | 0
200 | 716400 | 20 | 0 | 0
201 | 720000 | 20 | 0 | 0
202 | 723600 | 20 | 0 | 0
203 | 727200 | 20 | 0 | 0
204 | 730800 | 20 | 0 | 0
205 | 734400 | 20 | 0 | 0
206 | 738000 | 20 | 0 | 0
207 | 741600 | 20 | 0 | 0
208 | 745200 | 20 | 0 | 0
209 | 748800 | 20 | 0 | 0
210 | 752400 | 20 | 0 | 0
211 | 756000 | 20 | 0 | 0
212 | 759600 | 20 | 0 | 0
213 | 763200 | 20 | 0 | 0
214 | 766800 | 20 | 0 | 0
215 | 770400 | 20 | 0 | 0
216 | 774000 | 20 | 0 | 0
217 | 777600 | 20 | 0 | 0
218 | 781200 | 20 | 0 | 0
219 | 784800 | 20 | 0 | 0
220 | 788400 | 20 | 0 | 0
221 | 792000 | 20 | 0 | 0
222 | 795600 | 20 | 0 | 0
223 | 799200 | 20 | 0 | 0
224 | 802800 | 20 | 0 | 0
225 | 806400 | 20 | 0 | 0
226 | 810000 | 20 | 0 | 0
227 | 813600 | 20 | 0 | 0
228 | 817200 | 20 | 0 | 0
229 | 820800 | 20 | 0 | 0
230 | 824400 | 20 | 0 | 0
231 | 828000 | 20 | 0 | 0
232 | 831600 | 20 | 0 | 0
233 | 835200 | 20 | 0 | 0
234 | 838800 | 20 | 0 | 0
235 | 842400 | 20 | 0 | 0
236 | 846000 | 20 | 0 | 0
237 | 849600 | 20 | 0 | 0
238 | 853200 | 20 | 0 | 0
239 | 856800 | 20 | 0 | 0
240 | 860400 | 20 | 0 | 0
241 | 864000 | 20 | 0 | 0
242 | 867600 | 20 | 0 | 0
243 | 871200 | 20 | 0 | 0
244 | 874800 | 20 | 0 | 0
245 | 878400 | 20 | 0 | 0
246 | 882000 | 20 | 0 | 0
247 | 885600 | 20 | 0 | 0
248 | 889200 | 20 | 0 | 0
249 | 892800 | 20 | 0 | 0
250 | 896400 | 20 | 0 | 0
251 | 900000 | 20 | 0 | 0
252 | 903600 | 20 | 0 | 0
253 | 907200 | 20 | 0 | 0
254 | 910800 | 20 | 0 | 0
255 | 914400 | 20 | 0 | 0
256 | 918000 | 20 | 0 | 0
257 | 921600 | 20 | 0 | 0
258 | 925200 | 20 | 0 | 0
259 | 928800 | 20 | 0 | 0
260 | 932400 | 20 | 0 | 0
261 | 936000 | 20 | 0 | 0
262 | 939600 | 20 | 0 | 0
263 | 943200 | 20 | 0 | 0
264 | 946800 | 20 | 0 | 0
265 | 950400 | 20 | 0 | 0
266 | 954000 | 20 | 0 | 0
267 | 957600 | 20 | 0 | 0
268 | 961200 | 20 | 0 | 0
269 | 964800 | 20 | 0 | 0
270 | 968400 | 20 | 0 | 0
271 | 972000 | 20 | 0 | 0
272 | 975600 | 20 | 0 | 0
273 | 979200 | 20 | 0 | 0
274 | 982800 | 20 | 0 | 0
275 | 986400 | 20 | 0 | 0
276 | 990000 | 20 | 0 | 0
277 | 993600 | 20 | 0 | 0
278 | 997200 | 20 | 0 | 0
279 | 1000800 | 20 | 0 | 0
280 | 1004400 | 20 | 0 | 0
281 | 1008000 | 20 | 0 | 0
282 | 1011600 | 20 | 0 | 0
283 | 1015200 | 20 | 0 | 0
284 | 1018800 | 20 | 0 | 0
285 | 1022400 | 20 | 0 | 0
286 | 1026000 | 20 | 0 | 0
287 | 1029600 | 20 | 0 | 0
288 | 1033200 | 20 | 0 | 0
289 | 1036800 | 20 | 0 | 0
290 | 1040400 | 20 | 0 | 0
291 | 1044000 | 20 | 0 | 0
292 | 1047600 | 20 | 0 | 0
293 | 1051200 | 20 | 0 | 0
294 | 1054800 | 20 | 0 | 0
295 | 1058400 | 20 | 0 | 0
296 | 1062000 | 20 | 0 | 0
297 | 1065600 | 20 | 0 | 0
298 | 1069200 | 20 | 0 | 0
299 | 1072800 | 20 | 0 | 0
300 | 1076400 | 20 | 0 | 0
301 | 1080000 | 20 | 0 | 0
302 | 1083600 | 20 | 0 | 0
303 | 1087200 | 20 | 0 | 0
304 | 1090800 | 20 | 0 | 0
305 | 1094400 | 20 | 0 | 0
306 | 1098000 | 20 | 0 | 0
307 | 1101600 | 20 | 0 | 0
308 | 1105200 | 20 | 0 | 0
309 | 1108800 | 20 | 0 | 0
310 | 1112400 | 20 | 0 | 0
311 | 1116000 | 20 | 0 | 0
312 | 1119600 | 20 | 0 | 0
313 | 1123200 | 20 | 0 | 0
314 | 1126800 | 20 | 0 | 0
315 | 1130400 | 20 | 0 | 0
316 | 1134000 | 20 | 0 | 0
317 | 1137600 | 20 | 0 | 0
318 | 1141200 | 20 | 0 | 0
319 | 1144800 | 20 | 0 | 0
320 | 1148400 | 20 | 0 | 0
321 | 1152000 | 20 | 0 | 0
322 | 1155600 | 20 | 0 | 0
323 | 1159200 | 20 | 0 | 0
324 | 1162800 | 20 | 0 | 0
325 | 1166400 | 20 | 0 | 0
326 | 1170000 | 20 | 0 | 0
327 | 1173600 | 20 | 0 | 0
328 | 1177200 | 20 | 0 | 0
329 | 1180800 | 20 | 0 | 0
330 | 1184400 | 20 | 0 | 0
331 | 1188000 | 20 | 0 | 0
332 | 1191600 | 20 | 0 | 0
333 | 1195200 | 20 | 0 | 0
334 | 1198800 | 20 | 0 | 0
335 | 1202400 | 20 | 0 | 0
336 | 1206000 | 20 | 0 | 0
337 | 1209600 | 20 | 0 | 0

## Comparison
Test IntHeatGain - Internal Heat Gains
| Test Parameter | Units | 1052-RP | EnergyPlus | % Diff
-100% Radiative
| 24-Hour Zone Load | W-h | 452846.083 | 453589.9705 | 0.1643%
| Peak Load | W-h | 2695.187 | 2699.5627 | 0.1624%
-50% Radiative
| 24-Hour Zone Load | W-h | 453069.0446 | 453595.0269 | 0.1161%
| Peak Load | W-h | 2696.6675 | 2699.7798 | 0.1154%
-100% Convective
| 24-Hour Zone Load | W-h | 453600 | 453599.7988 | -4.435e-05%
| Peak Load | W-h | 2700 | 2699.999 | 0%