## Data
ASHRAE Analytical Test IntRad-Test 1
EnergyPlus Results
Interior Surfaces Temperatures
|  | EnergyPlus > > > > > | [5 empty] | 1052RP > > > > >
| Aspect Ratio | EnergyPlus - Exterior Surface Interior Temperature | EnergyPlus - Zone Sensible Cooling Load | EnergyPlus - Opposite Wall Interior Surface Temperature | EnergyPlus - Side Wall, Ceiling & Floor Interior Surface Temperature | Eplus Ceiling Interior Surface Temperature | Eplus Floor Interior Surface Temperature | ASHRAE 1052RP - Exterior Surface Interior Temperature | ASHRAE 1052RP - Zone Sensible Cooling Load | ASHRAE 1052RP - Opposite Wall Interior Surface Temperature | ASHRAE 1052RP - Side Wall, Ceiling & Floor Interior Surface Temperature | 1052RP Exterior Surface Interior Temperature, K | 1052RP Zone Load (W) | 1052RP Opposite Wall Interior Surface Temperature, K | 1052RP Side Wall, Ceiling & Floor Interior Surface Temperature, K
| 1 | 32.7801 | 663.4096 | 21.2643 | 22.8875 | 22.8875 | 22.8875 | 32.7847 | 663.6646 | 21.2647 | 22.8887 | 32.7847 |  | 21.2647 | 22.8887
| 2 | 32.1741 | 719.0932 | 20.8183 | 21.8926 | 21.8926 | 21.8926 | 32.1765 | 719.613 | 20.7811 | 21.8995 | 32.1765 |  | 20.7811 | 21.8995
| 5 | 31.6068 | 771.2167 | 20.3956 | 20.9246 | 20.9246 | 20.9246 | 31.612 | 771.5441 | 20.3565 | 20.927 | 31.612 |  | 20.3565 | 20.927
| 10 | 31.3596 | 793.9296 | 20.2124 | 20.4983 | 20.4983 | 20.4983 | 31.3654 | 794.1929 | 20.1868 | 20.4991 | 31.3654 |  | 20.1868 | 20.4991
| 20 | 31.2246 | 806.3354 | 20.1105 | 20.2597 | 20.2597 | 20.2597 | 31.2306 | 806.6564 | 20.096 | 20.26 | 31.2306 |  | 20.096 | 20.26

## EPlus Interior Film Coeff
EnergyPlus Weighted Average for Interior Film Coefficient
ASHRAE Analytical Test IntRad-Test 1
| AR-1 |  |  | AR-2 |  |  | AR-5 |  |  | AR-10 |  |  | AR-20
| Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted
| Film | Factor | Film | Film | Factor | Film | Film | Factor | Film | Film | Factor | Film | Film | Factor | Film
Surface | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff
South | 2.88 | 1 | 2.88 | 2.84 | 1 | 2.84 | 2.81 | 1 | 2.81 | 2.8 | 1 | 2.8 | 2.79 | 1 | 2.79
North | 2.88 | 1 | 2.88 | 2.84 | 1 | 2.84 | 2.81 | 1 | 2.81 | 2.8 | 1 | 2.8 | 2.79 | 1 | 2.79
East | 2.88 | 1 | 2.88 | 2.84 | 2 | 5.68 | 2.81 | 5 | 14.05 | 2.8 | 10 | 28 | 2.79 | 20 | 55.8
West | 2.88 | 1 | 2.88 | 2.84 | 2 | 5.68 | 2.81 | 5 | 14.05 | 2.8 | 10 | 28 | 2.79 | 20 | 55.8
Ceiling | 2.88 | 1 | 2.88 | 2.84 | 2 | 5.68 | 2.81 | 5 | 14.05 | 2.8 | 10 | 28 | 2.79 | 20 | 55.8
Floor | 2.88 | 1 | 2.88 | 2.84 | 2 | 5.68 | 2.81 | 5 | 14.05 | 2.8 | 10 | 28 | 2.79 | 20 | 55.8
Sum |  |  | 17.28 |  |  | 28.4 |  |  | 61.82 |  |  | 117.6 |  |  | 228.78
Weighted Average |  |  | 2.88 |  |  | 2.84 |  |  | 2.81 |  |  | 2.8 |  |  | 2.79

## Comparison
Test IntLWRad - Interior Long Wave Radiation, Test 1
| Test Parameter | Units | 1052-RP | EnergyPlus | % Diff
-Exterior Wall Interior Temp
| AP=1 | C | 32.7847 | 32.7801 | -0.01415%
| AP=2 | C | 32.1765 | 32.1741 | -0.007555%
| AP=5 | C | 31.612 | 31.6068 | -0.01628%
| AP=10 | C | 31.3654 | 31.3596 | -0.01853%
| AP=20 | C | 31.2306 | 31.2246 | -0.01911%
-Opposite Wall Interior Temp
| AP=1 | C | 21.2647 | 21.2643 | -0.001555%
| AP=2 | C | 20.7811 | 20.8183 | 0.1793%
| AP=5 | C | 20.3565 | 20.3956 | 0.1923%
| AP=10 | C | 20.1868 | 20.2124 | 0.1268%
| AP=20 | C | 20.096 | 20.1105 | 0.07216%
-Other Surfaces Interior Temp
| AP=1 | C | 22.8887 | 22.8875 | -0.005313%
| AP=2 | C | 21.8995 | 21.8926 | -0.03149%
| AP=5 | C | 20.927 | 20.9246 | -0.01122%
| AP=10 | C | 20.4991 | 20.4983 | -0.003685%
| AP=20 | C | 20.26 | 20.2597 | -0.001314%
-Zone Sensible Cooling Load
| AP=1 | W-h | 663.6646 | 663.4096 | -0.03842%
| AP=2 | W-h | 719.613 | 719.0932 | -0.07223%
| AP=5 | W-h | 771.5441 | 771.2167 | -0.04243%
| AP=10 | W-h | 794.1929 | 793.9296 | -0.03316%
| AP=20 | W-h | 806.6564 | 806.3354 | -0.0398%