## Data
ASHRAE Analytical Test IntRad-Test 3
EnergyPlus Results
Interior Surfaces Temperatures
|  | EnergyPlus > > > > > | [5 empty] | 1052RP > > > > >
| Aspect Ratio | EnergyPlus - Exterior Surface Interior Temperature | EnergyPlus - Zone Sensible Cooling Load | EnergyPlus - Opposite Wall Interior Surface Temperature | EnergyPlus - Side Wall, Ceiling & Floor Interior Surface Temperature | Eplus Ceiling Interior Surface Temperature | Eplus Floor Interior Surface Temperature | ASHRAE 1052RP - Exterior Surface Interior Temperature | ASHRAE 1052RP - Zone Sensible Cooling Load | ASHRAE 1052RP - Opposite Wall Interior Surface Temperature | ASHRAE 1052RP - Side Wall, Ceiling & Floor Interior Surface Temperature | 1052RP Exterior Surface Interior Temperature, K | 1052RP Zone Load (W) | 1052RP Opposite Wall Interior Surface Temperature, K | 1052RP Side Wall, Ceiling & Floor Interior Surface Temperature, K
| 1 | 31.9821 | 736.7365 | 23.2883 | 23.2883 | 23.2883 | 23.2883 | 31.9869 | 737.0479 | 23.2889 | 23.2899 | 31.9869 |  | 23.2889 | 23.2899
| 2 | 31.6056 | 771.3273 | 21.9469 | 22.0257 | 22.0257 | 22.0257 | 31.6474 | 768.2828 | 21.8169 | 22.0742 | 31.6474 |  | 21.8169 | 22.0742
| 5 | 31.2893 | 800.39 | 20.8732 | 20.9358 | 20.9358 | 20.9358 | 31.3466 | 795.9512 | 20.7416 | 20.9692 | 31.3466 |  | 20.7416 | 20.9692
| 10 | 31.1613 | 812.1524 | 20.4549 | 20.4929 | 20.4929 | 20.4929 | 31.2201 | 807.5566 | 20.3705 | 20.5114 | 31.2201 |  | 20.3705 | 20.5114
| 20 | 31.0921 | 818.5091 | 20.2324 | 20.2532 | 20.2532 | 20.2532 | 31.1542 | 813.6665 | 20.1854 | 20.2633 | 31.1542 |  | 20.1854 | 20.2633
Load values are manually entered
because of the way the CSV file is structured

## EPlus Interior Film Coeff
EnergyPlus Weighted Average for Interior Film Coefficient
ASHRAE Analytical Test IntRad-Test 3
| AR-1 |  |  | AR-2 |  |  | AR-5 |  |  | AR-10 |  |  | AR-20
| Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted | Int. | Area | Weighted
| Film | Factor | Film | Film | Factor | Film | Film | Factor | Film | Film | Factor | Film | Film | Factor | Film
Surface | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff | Coeff |  | Coeff
South | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88
North | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88 | 2.88 | 1 | 2.88
East | 2.88 | 1 | 2.88 | 2.88 | 2 | 5.76 | 2.88 | 5 | 14.4 | 2.88 | 10 | 28.8 | 2.88 | 20 | 57.6
West | 2.88 | 1 | 2.88 | 2.88 | 2 | 5.76 | 2.88 | 5 | 14.4 | 2.88 | 10 | 28.8 | 2.88 | 20 | 57.6
Ceiling | 2.88 | 1 | 2.88 | 2.88 | 2 | 5.76 | 2.88 | 5 | 14.4 | 2.88 | 10 | 28.8 | 2.88 | 20 | 57.6
Floor | 2.88 | 1 | 2.88 | 2.88 | 2 | 5.76 | 2.88 | 5 | 14.4 | 2.88 | 10 | 28.8 | 2.88 | 20 | 57.6
Sum |  |  | 17.28 |  |  | 28.8 |  |  | 63.36 |  |  | 120.96 |  |  | 236.16
Weighted Average |  |  | 2.88 |  |  | 2.88 |  |  | 2.88 |  |  | 2.88 |  |  | 2.88

## Comparison
Test IntLWRad - Interior Long Wave Radiation, Test 3
| Test Parameter | Units | 1052-RP | EnergyPlus | % Diff
-Exterior Wall Interior Temp
| AP=1 | C | 31.9869 | 31.9821 | -0.01512%
| AP=2 | C | 31.6474 | 31.6056 | -0.132%
| AP=5 | C | 31.3466 | 31.2893 | -0.1826%
| AP=10 | C | 31.2201 | 31.1613 | -0.1884%
| AP=20 | C | 31.1542 | 31.0921 | -0.1993%
-Opposite Wall Interior Temp
| AP=1 | C | 23.2889 | 23.2883 | -0.002699%
| AP=2 | C | 21.8169 | 21.9469 | 0.5958%
| AP=5 | C | 20.7416 | 20.8732 | 0.6342%
| AP=10 | C | 20.3705 | 20.4549 | 0.4148%
| AP=20 | C | 20.1854 | 20.2324 | 0.2326%
-Other Surfaces Interior Temp
| AP=1 | C | 23.2899 | 23.2883 | -0.007023%
| AP=2 | C | 22.0742 | 22.0257 | -0.2198%
| AP=5 | C | 20.9692 | 20.9358 | -0.1593%
| AP=10 | C | 20.5114 | 20.4929 | -0.09002%
| AP=20 | C | 20.2633 | 20.2532 | -0.05001%
-Zone Sensible Cooling Load
| AP=1 | W-h | 737.0479 | 736.7365 | -0.04225%
| AP=2 | W-h | 768.2828 | 771.3273 | 0.3963%
| AP=5 | W-h | 795.9512 | 800.39 | 0.5577%
| AP=10 | W-h | 807.5566 | 812.1524 | 0.5691%
| AP=20 | W-h | 813.6665 | 818.5091 | 0.5952%