## EPlus 10cm Wood
EnergyPlus Results for ASHRAE 1052RP Analytical Test TC2
Step change in outdoor temperature
10 cm Wood
Date/Time | Hour of Year | Outdoor Dry Bulb Temperature | Environment:Diffuse Solar [W/m2](Hourly) | Environment:Direct Solar [W/m2](Hourly) | ZONE ONE:Zone/Sys Sensible Heating Energy[J](Hourly) | ZONE ONE:Zone/Sys Sensible Cooling Energy[J](Hourly) | ZONE ONE:Mean Air Temperature[C](Hourly) | EnergyPlus - Surface Inside Temperature | EnergyPlus - Surface Outside Temperature | ZONE SURFACE NORTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE NORTH:Surface Ext Convection Coeff[W/m2-K](Hourly) | EnergyPlus - Zone Sensible Cooling Load
03/31 14:00:00 | 2150 | 20 | 0 | 0 | 0.065752 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 15:00:00 | 2151 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 16:00:00 | 2152 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 17:00:00 | 2153 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 18:00:00 | 2154 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 19:00:00 | 2155 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 20:00:00 | 2156 | 20 | 0 | 0 | 0.065751 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 21:00:00 | 2157 | 20 | 0 | 0 | 0.065752 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 22:00:00 | 2158 | 20 | 0 | 0 | 0.065752 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 23:00:00 | 2159 | 20 | 0 | 0 | 0.065752 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
03/31 24:00:00 | 2160 | 20 | 0 | 0 | 0.065752 | 0 | 20 | 20 | 20 | 3.076 | 10.22 | 0
04/01 01:00:00 | 2161 | 49.1667 | 0 | 0 | 0.010225 | 198.5059 | 20 | 20.002 | 36.7774 | 3.076 | 10.22 | 0.055141
04/01 02:00:00 | 2162 | 70 | 0 | 0 | 0 | 12539.707 | 20 | 20.1258 | 53.9489 | 3.076 | 10.22 | 3.4833
04/01 03:00:00 | 2163 | 70 | 0 | 0 | 0 | 78712.2336 | 20 | 20.7898 | 57.5512 | 3.076 | 10.22 | 21.8645
04/01 04:00:00 | 2164 | 70 | 0 | 0 | 0 | 203016.8195 | 20 | 22.037 | 59.4925 | 3.076 | 10.22 | 56.3936
04/01 05:00:00 | 2165 | 70 | 0 | 0 | 0 | 351764.0326 | 20 | 23.5296 | 60.7538 | 3.076 | 10.22 | 97.7122
04/01 06:00:00 | 2166 | 70 | 0 | 0 | 0 | 499667.3168 | 20 | 25.0136 | 61.6598 | 3.076 | 10.22 | 138.7965
04/01 07:00:00 | 2167 | 70 | 0 | 0 | 0 | 635139.658 | 20 | 26.3729 | 62.353 | 3.076 | 10.22 | 176.4277
04/01 08:00:00 | 2168 | 70 | 0 | 0 | 0 | 754421.7562 | 20 | 27.5698 | 62.9051 | 3.076 | 10.22 | 209.5616
04/01 09:00:00 | 2169 | 70 | 0 | 0 | 0 | 857361.0285 | 20 | 28.6027 | 63.3557 | 3.076 | 10.22 | 238.1558
04/01 10:00:00 | 2170 | 70 | 0 | 0 | 0 | 945263.4195 | 20 | 29.4847 | 63.7287 | 3.076 | 10.22 | 262.5732
04/01 11:00:00 | 2171 | 70 | 0 | 0 | 0 | 1019834.6474 | 20 | 30.2329 | 64.04 | 3.076 | 10.22 | 283.2874
04/01 12:00:00 | 2172 | 70 | 0 | 0 | 0 | 1083002.5824 | 20 | 30.8667 | 64.301 | 3.076 | 10.22 | 300.8341
04/01 13:00:00 | 2173 | 70 | 0 | 0 | 0 | 1136393.6716 | 20 | 31.4024 | 64.5204 | 3.076 | 10.22 | 315.6649
04/01 14:00:00 | 2174 | 70 | 0 | 0 | 0 | 1181475.4384 | 20 | 31.8548 | 64.7052 | 3.076 | 10.22 | 328.1876
04/01 15:00:00 | 2175 | 70 | 0 | 0 | 0 | 1219520.7282 | 20 | 32.2365 | 64.8608 | 3.076 | 10.22 | 338.7558
04/01 16:00:00 | 2176 | 70 | 0 | 0 | 0 | 1251618.4595 | 20 | 32.5586 | 64.992 | 3.076 | 10.22 | 347.6718
04/01 17:00:00 | 2177 | 70 | 0 | 0 | 0 | 1278694.0756 | 20 | 32.8303 | 65.1026 | 3.076 | 10.22 | 355.1928
04/01 18:00:00 | 2178 | 70 | 0 | 0 | 0 | 1301500.4369 | 20 | 33.0591 | 65.1959 | 3.076 | 10.22 | 361.5279
04/01 19:00:00 | 2179 | 70 | 0 | 0 | 0 | 1320715.6382 | 20 | 33.2519 | 65.2745 | 3.076 | 10.22 | 366.8655
04/01 20:00:00 | 2180 | 70 | 0 | 0 | 0 | 1336955.675 | 20 | 33.4148 | 65.3409 | 3.076 | 10.22 | 371.3766
04/01 21:00:00 | 2181 | 70 | 0 | 0 | 0 | 1350658.2154 | 20 | 33.5523 | 65.3968 | 3.076 | 10.22 | 375.1828
04/01 22:00:00 | 2182 | 70 | 0 | 0 | 0 | 1362217.631 | 20 | 33.6683 | 65.4439 | 3.076 | 10.22 | 378.3938
04/01 23:00:00 | 2183 | 70 | 0 | 0 | 0 | 1371968.3866 | 20 | 33.7662 | 65.4837 | 3.076 | 10.22 | 381.1023
04/01 24:00:00 | 2184 | 70 | 0 | 0 | 0 | 1380193.1711 | 20 | 33.8487 | 65.5173 | 3.076 | 10.22 | 383.387
04/02 01:00:00 | 2185 | 70 | 0 | 0 | 0 | 1387130.6583 | 20 | 33.9183 | 65.5456 | 3.076 | 10.22 | 385.3141
04/02 02:00:00 | 2186 | 70 | 0 | 0 | 0 | 1392925.4366 | 20 | 33.9764 | 65.5694 | 3.076 | 10.22 | 386.9237
04/02 03:00:00 | 2187 | 70 | 0 | 0 | 0 | 1397834.4474 | 20 | 34.0257 | 65.5895 | 3.076 | 10.22 | 388.2873
04/02 04:00:00 | 2188 | 70 | 0 | 0 | 0 | 1401995.1526 | 20 | 34.0674 | 65.6065 | 3.076 | 10.22 | 389.4431
04/02 05:00:00 | 2189 | 70 | 0 | 0 | 0 | 1405509.3872 | 20 | 34.1027 | 65.6208 | 3.076 | 10.22 | 390.4193
04/02 06:00:00 | 2190 | 70 | 0 | 0 | 0 | 1408476.1496 | 20 | 34.1325 | 65.6329 | 3.076 | 10.22 | 391.2434
04/02 07:00:00 | 2191 | 70 | 0 | 0 | 0 | 1410980.1901 | 20 | 34.1576 | 65.643 | 3.076 | 10.22 | 391.9389
04/02 08:00:00 | 2192 | 70 | 0 | 0 | 0 | 1413093.4461 | 20 | 34.1788 | 65.6516 | 3.076 | 10.22 | 392.526
04/02 09:00:00 | 2193 | 70 | 0 | 0 | 0 | 1414876.7985 | 20 | 34.1967 | 65.6589 | 3.076 | 10.22 | 393.0213
04/02 10:00:00 | 2194 | 70 | 0 | 0 | 0 | 1416343.6978 | 20 | 34.2114 | 65.665 | 3.076 | 10.22 | 393.4288
04/02 11:00:00 | 2195 | 70 | 0 | 0 | 0 | 1417568.5301 | 20 | 34.2237 | 65.6701 | 3.076 | 10.22 | 393.769
04/02 12:00:00 | 2196 | 70 | 0 | 0 | 0 | 1418625.9346 | 20 | 34.2343 | 65.6745 | 3.076 | 10.22 | 394.0628
04/02 13:00:00 | 2197 | 70 | 0 | 0 | 0 | 1419530.1034 | 20 | 34.2434 | 65.6781 | 3.076 | 10.22 | 394.3139
04/02 14:00:00 | 2198 | 70 | 0 | 0 | 0 | 1420297.3794 | 20 | 34.2511 | 65.6812 | 3.076 | 10.22 | 394.527
04/02 15:00:00 | 2199 | 70 | 0 | 0 | 0 | 1420947.3382 | 20 | 34.2576 | 65.6838 | 3.076 | 10.22 | 394.7076
04/02 16:00:00 | 2200 | 70 | 0 | 0 | 0 | 1421497.4674 | 20 | 34.2631 | 65.686 | 3.076 | 10.22 | 394.8604
04/02 17:00:00 | 2201 | 70 | 0 | 0 | 0 | 1421962.9009 | 20 | 34.2678 | 65.6879 | 3.076 | 10.22 | 394.9897
04/02 18:00:00 | 2202 | 70 | 0 | 0 | 0 | 1422356.5856 | 20 | 34.2717 | 65.6894 | 3.076 | 10.22 | 395.0991
04/02 19:00:00 | 2203 | 70 | 0 | 0 | 0 | 1422689.5385 | 20 | 34.2751 | 65.6908 | 3.076 | 10.22 | 395.1915
04/02 20:00:00 | 2204 | 70 | 0 | 0 | 0 | 1422971.1081 | 20 | 34.2779 | 65.6919 | 3.076 | 10.22 | 395.2698
04/02 21:00:00 | 2205 | 70 | 0 | 0 | 0 | 1423209.2144 | 20 | 34.2803 | 65.6928 | 3.076 | 10.22 | 395.3359
04/02 22:00:00 | 2206 | 70 | 0 | 0 | 0 | 1423410.5619 | 20 | 34.2823 | 65.6936 | 3.076 | 10.22 | 395.3918
04/02 23:00:00 | 2207 | 70 | 0 | 0 | 0 | 1423580.8232 | 20 | 34.284 | 65.6943 | 3.076 | 10.22 | 395.4391
04/02 24:00:00 | 2208 | 70 | 0 | 0 | 0 | 1423724.7967 | 20 | 34.2855 | 65.6949 | 3.076 | 10.22 | 395.4791
04/03 01:00:00 | 2209 | 70 | 0 | 0 | 0 | 1423846.5406 | 20 | 34.2867 | 65.6954 | 3.076 | 10.22 | 395.5129
04/03 02:00:00 | 2210 | 70 | 0 | 0 | 0 | 1423949.4871 | 20 | 34.2877 | 65.6958 | 3.076 | 10.22 | 395.5415
04/03 03:00:00 | 2211 | 70 | 0 | 0 | 0 | 1424036.5383 | 20 | 34.2886 | 65.6961 | 3.076 | 10.22 | 395.5657
04/03 04:00:00 | 2212 | 70 | 0 | 0 | 0 | 1424110.1485 | 20 | 34.2893 | 65.6964 | 3.076 | 10.22 | 395.5862
04/03 05:00:00 | 2213 | 70 | 0 | 0 | 0 | 1424172.393 | 20 | 34.29 | 65.6966 | 3.076 | 10.22 | 395.6034
04/03 06:00:00 | 2214 | 70 | 0 | 0 | 0 | 1424225.0267 | 20 | 34.2905 | 65.6969 | 3.076 | 10.22 | 395.6181
04/03 07:00:00 | 2215 | 70 | 0 | 0 | 0 | 1424269.5335 | 20 | 34.2909 | 65.697 | 3.076 | 10.22 | 395.6304
04/03 08:00:00 | 2216 | 70 | 0 | 0 | 0 | 1424307.1682 | 20 | 34.2913 | 65.6972 | 3.076 | 10.22 | 395.6409
04/03 09:00:00 | 2217 | 70 | 0 | 0 | 0 | 1424338.992 | 20 | 34.2916 | 65.6973 | 3.076 | 10.22 | 395.6497
04/03 10:00:00 | 2218 | 70 | 0 | 0 | 0 | 1424365.9021 | 20 | 34.2919 | 65.6974 | 3.076 | 10.22 | 395.6572
04/03 11:00:00 | 2219 | 70 | 0 | 0 | 0 | 1424388.6571 | 20 | 34.2921 | 65.6975 | 3.076 | 10.22 | 395.6635
04/03 12:00:00 | 2220 | 70 | 0 | 0 | 0 | 1424407.8987 | 20 | 34.2923 | 65.6976 | 3.076 | 10.22 | 395.6689
04/03 13:00:00 | 2221 | 70 | 0 | 0 | 0 | 1424424.1693 | 20 | 34.2925 | 65.6976 | 3.076 | 10.22 | 395.6734
04/03 14:00:00 | 2222 | 70 | 0 | 0 | 0 | 1424437.9276 | 20 | 34.2926 | 65.6977 | 3.076 | 10.22 | 395.6772
04/03 15:00:00 | 2223 | 70 | 0 | 0 | 0 | 1424449.5616 | 20 | 34.2927 | 65.6977 | 3.076 | 10.22 | 395.6804
04/03 16:00:00 | 2224 | 70 | 0 | 0 | 0 | 1424459.3992 | 20 | 34.2928 | 65.6978 | 3.076 | 10.22 | 395.6832
04/03 17:00:00 | 2225 | 70 | 0 | 0 | 0 | 1424467.7179 | 20 | 34.2929 | 65.6978 | 3.076 | 10.22 | 395.6855
04/03 18:00:00 | 2226 | 70 | 0 | 0 | 0 | 1424474.7521 | 20 | 34.293 | 65.6978 | 3.076 | 10.22 | 395.6874
04/03 19:00:00 | 2227 | 70 | 0 | 0 | 0 | 1424480.7002 | 20 | 34.2931 | 65.6979 | 3.076 | 10.22 | 395.6891
04/03 20:00:00 | 2228 | 70 | 0 | 0 | 0 | 1424485.7299 | 20 | 34.2931 | 65.6979 | 3.076 | 10.22 | 395.6905
04/03 21:00:00 | 2229 | 70 | 0 | 0 | 0 | 1424489.983 | 20 | 34.2932 | 65.6979 | 3.076 | 10.22 | 395.6917
04/03 22:00:00 | 2230 | 70 | 0 | 0 | 0 | 1424493.5794 | 20 | 34.2932 | 65.6979 | 3.076 | 10.22 | 395.6927
04/03 23:00:00 | 2231 | 70 | 0 | 0 | 0 | 1424496.6205 | 20 | 34.2932 | 65.6979 | 3.076 | 10.22 | 395.6935
04/03 24:00:00 | 2232 | 70 | 0 | 0 | 0 | 1424499.192 | 20 | 34.2932 | 65.6979 | 3.076 | 10.22 | 395.6942
04/04 01:00:00 | 2233 | 70 | 0 | 0 | 0 | 1424501.3665 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6948
04/04 02:00:00 | 2234 | 70 | 0 | 0 | 0 | 1424503.2053 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6953
04/04 03:00:00 | 2235 | 70 | 0 | 0 | 0 | 1424504.7601 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6958
04/04 04:00:00 | 2236 | 70 | 0 | 0 | 0 | 1424506.0748 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6961
04/04 05:00:00 | 2237 | 70 | 0 | 0 | 0 | 1424507.1866 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6964
04/04 06:00:00 | 2238 | 70 | 0 | 0 | 0 | 1424508.1267 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6967
04/04 07:00:00 | 2239 | 70 | 0 | 0 | 0 | 1424508.9216 | 20 | 34.2933 | 65.698 | 3.076 | 10.22 | 395.6969
04/04 08:00:00 | 2240 | 70 | 0 | 0 | 0 | 1424509.5938 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6971
04/04 09:00:00 | 2241 | 70 | 0 | 0 | 0 | 1424510.1622 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6973
04/04 10:00:00 | 2242 | 70 | 0 | 0 | 0 | 1424510.6428 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6974
04/04 11:00:00 | 2243 | 70 | 0 | 0 | 0 | 1424511.0493 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6975
04/04 12:00:00 | 2244 | 70 | 0 | 0 | 0 | 1424511.3929 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6976
04/04 13:00:00 | 2245 | 70 | 0 | 0 | 0 | 1424511.6835 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6977
04/04 14:00:00 | 2246 | 70 | 0 | 0 | 0 | 1424511.9293 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6978
04/04 15:00:00 | 2247 | 70 | 0 | 0 | 0 | 1424512.1371 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6978
04/04 16:00:00 | 2248 | 70 | 0 | 0 | 0 | 1424512.3128 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6979
04/04 17:00:00 | 2249 | 70 | 0 | 0 | 0 | 1424512.4614 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6979
04/04 18:00:00 | 2250 | 70 | 0 | 0 | 0 | 1424512.587 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6979
04/04 19:00:00 | 2251 | 70 | 0 | 0 | 0 | 1424512.6932 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.698
04/04 20:00:00 | 2252 | 70 | 0 | 0 | 0 | 1424512.7831 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.698
04/04 21:00:00 | 2253 | 70 | 0 | 0 | 0 | 1424512.859 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.698
04/04 22:00:00 | 2254 | 70 | 0 | 0 | 0 | 1424512.9233 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.698
04/04 23:00:00 | 2255 | 70 | 0 | 0 | 0 | 1424512.9776 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.698
04/04 24:00:00 | 2256 | 70 | 0 | 0 | 0 | 1424513.0235 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6981
04/05 01:00:00 | 2257 | 70 | 0 | 0 | 0 | 1424513.0624 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6981
04/05 02:00:00 | 2258 | 70 | 0 | 0 | 0 | 1424513.0952 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6981
04/05 03:00:00 | 2259 | 70 | 0 | 0 | 0 | 1424513.123 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6981
04/05 04:00:00 | 2260 | 70 | 0 | 0 | 0 | 1424513.1465 | 20 | 34.2934 | 65.698 | 3.076 | 10.22 | 395.6981
[11 empty] | 48 hour cooling load | 15918.8941

## ASHRAE 10cm Wood
ASHRAE 1052RP Toolkit Test TC2
Data taken from D:\ASHRAE 1052RP OUTPUTS
10 cm Wood
| Time | External | Internal | External | Internal | External | Zone
|  | Air Temp. | ASHRAE 1052RP - Surface Inside Temperature | ASHRAE 1052RP - Surface Outside Temperature | Surface Flux | Surface Flux | ASHRAE 1052RP - Zone Sensible Cooling Load
| 2150 | 20 | 20 | 20 | 0 | 0 | 0
| 2151 | 20 | 20 | 20 | 0 | 0 | 0
| 2152 | 20 | 20 | 20 | 0 | 0 | 0
| 2153 | 20 | 20 | 20 | 0 | 0 | 0
| 2154 | 20 | 20 | 20 | 0 | 0 | 0
| 2155 | 20 | 20 | 20 | 0 | 0 | 0
| 2156 | 20 | 20 | 20 | 0 | 0 | 0
| 2157 | 20 | 20 | 20 | 0 | 0 | 0
| 2158 | 20 | 20 | 20 | 0 | 0 | 0
| 2159 | 20 | 20 | 20 | 0 | 0 | 0
| 2160 | 20 | 20 | 20 | 0 | 0 | 0
| 2161 | 70 | 20.0129 | 53.6367 | 0.039612 | 167.2334 | 0.3565
| 2162 | 70 | 20.497 | 57.6092 | 1.5286 | 126.6344 | 13.7578
| 2163 | 70 | 21.7687 | 59.6031 | 5.4405 | 106.2562 | 48.9642
| 2164 | 70 | 23.3681 | 60.866 | 10.3602 | 93.3493 | 93.2422
| 2165 | 70 | 24.9563 | 61.766 | 15.2454 | 84.1511 | 137.209
| 2166 | 70 | 26.3946 | 62.4542 | 19.6698 | 77.1177 | 177.0282
| 2167 | 70 | 27.6455 | 63.0027 | 23.5175 | 71.5119 | 211.6573
| 2168 | 70 | 28.7127 | 63.4502 | 26.8002 | 66.939 | 241.2017
| 2169 | 70 | 29.6147 | 63.8198 | 29.5748 | 63.1617 | 266.1728
| 2170 | 70 | 30.3735 | 64.1271 | 31.9089 | 60.0211 | 287.1801
| 2171 | 70 | 31.0104 | 64.3835 | 33.8679 | 57.4011 | 304.8109
| 2172 | 70 | 31.5442 | 64.5977 | 35.51 | 55.2114 | 319.5904
| 2173 | 70 | 31.9915 | 64.7769 | 36.8858 | 53.3799 | 331.9722
| 2174 | 70 | 32.3661 | 64.9269 | 38.038 | 51.8472 | 342.3419
| 2175 | 70 | 32.6797 | 65.0524 | 39.0028 | 50.5643 | 351.0253
| 2176 | 70 | 32.9423 | 65.1575 | 39.8107 | 49.4903 | 358.296
| 2177 | 70 | 33.1622 | 65.2455 | 40.4871 | 48.5912 | 364.3835
| 2178 | 70 | 33.3463 | 65.3191 | 41.0534 | 47.8384 | 369.4803
| 2179 | 70 | 33.5005 | 65.3808 | 41.5275 | 47.2082 | 373.7475
| 2180 | 70 | 33.6295 | 65.4324 | 41.9245 | 46.6806 | 377.3203
| 2181 | 70 | 33.7376 | 65.4757 | 42.2568 | 46.2388 | 380.3115
| 2182 | 70 | 33.8281 | 65.5118 | 42.5351 | 45.8689 | 382.8159
| 2183 | 70 | 33.9038 | 65.5421 | 42.7681 | 45.5593 | 384.9126
| 2184 | 70 | 33.9672 | 65.5675 | 42.9631 | 45.3 | 386.6681
| 2185 | 70 | 34.0203 | 65.5888 | 43.1264 | 45.083 | 388.1379
| 2186 | 70 | 34.0647 | 65.6065 | 43.2632 | 44.9012 | 389.3684
| 2187 | 70 | 34.102 | 65.6214 | 43.3776 | 44.7491 | 390.3986
| 2188 | 70 | 34.1331 | 65.6339 | 43.4735 | 44.6217 | 391.2612
| 2189 | 70 | 34.1592 | 65.6443 | 43.5537 | 44.5151 | 391.9834
| 2190 | 70 | 34.181 | 65.6531 | 43.6209 | 44.4258 | 392.588
| 2191 | 70 | 34.1993 | 65.6604 | 43.6771 | 44.351 | 393.0942
| 2192 | 70 | 34.2146 | 65.6665 | 43.7242 | 44.2884 | 393.518
| 2193 | 70 | 34.2275 | 65.6716 | 43.7637 | 44.236 | 393.8729
| 2194 | 70 | 34.2382 | 65.6759 | 43.7967 | 44.1921 | 394.1699
| 2195 | 70 | 34.2472 | 65.6795 | 43.8243 | 44.1554 | 394.4187
| 2196 | 70 | 34.2547 | 65.6825 | 43.8474 | 44.1247 | 394.6269
| 2197 | 70 | 34.261 | 65.685 | 43.8668 | 44.0989 | 394.8013
| 2198 | 70 | 34.2663 | 65.6871 | 43.883 | 44.0773 | 394.9472
| 2199 | 70 | 34.2707 | 65.6889 | 43.8966 | 44.0593 | 395.0695
| 2200 | 70 | 34.2744 | 65.6904 | 43.908 | 44.0442 | 395.1718
| 2201 | 70 | 34.2775 | 65.6916 | 43.9175 | 44.0315 | 395.2574
| 2202 | 70 | 34.2801 | 65.6927 | 43.9255 | 44.0209 | 395.3292
| 2203 | 70 | 34.2822 | 65.6935 | 43.9321 | 44.0121 | 395.3892
| 2204 | 70 | 34.284 | 65.6943 | 43.9377 | 44.0046 | 395.4395
| 2205 | 70 | 34.2856 | 65.6949 | 43.9424 | 43.9984 | 395.4816
| 2206 | 70 | 34.2868 | 65.6954 | 43.9463 | 43.9932 | 395.5168
| 2207 | 70 | 34.2879 | 65.6958 | 43.9496 | 43.9889 | 395.5463
| 2208 | 70 | 34.2888 | 65.6962 | 43.9523 | 43.9852 | 395.571
| 2209 | 70 | 34.2895 | 65.6965 | 43.9546 | 43.9822 | 395.5917
| 2210 | 70 | 34.2902 | 65.6967 | 43.9566 | 43.9796 | 395.609
| 2211 | 70 | 34.2907 | 65.6969 | 43.9582 | 43.9775 | 395.6235
| 2212 | 70 | 34.2911 | 65.6971 | 43.9595 | 43.9757 | 395.6357
| 2213 | 70 | 34.2915 | 65.6972 | 43.9606 | 43.9742 | 395.6458
| 2214 | 70 | 34.2918 | 65.6974 | 43.9616 | 43.9729 | 395.6543
| 2215 | 70 | 34.2921 | 65.6975 | 43.9624 | 43.9719 | 395.6615
| 2216 | 70 | 34.2923 | 65.6976 | 43.963 | 43.971 | 395.6674
| 2217 | 70 | 34.2925 | 65.6976 | 43.9636 | 43.9703 | 395.6724
| 2218 | 70 | 34.2926 | 65.6977 | 43.9641 | 43.9696 | 395.6766
| 2219 | 70 | 34.2927 | 65.6977 | 43.9645 | 43.9691 | 395.6801
| 2220 | 70 | 34.2928 | 65.6978 | 43.9648 | 43.9687 | 395.683
| 2221 | 70 | 34.2929 | 65.6978 | 43.9651 | 43.9683 | 395.6855
| 2222 | 70 | 34.293 | 65.6978 | 43.9653 | 43.968 | 395.6875
| 2223 | 70 | 34.2931 | 65.6979 | 43.9655 | 43.9678 | 395.6893
| 2224 | 70 | 34.2931 | 65.6979 | 43.9656 | 43.9676 | 395.6907
| 2225 | 70 | 34.2932 | 65.6979 | 43.9658 | 43.9674 | 395.6919
| 2226 | 70 | 34.2932 | 65.6979 | 43.9659 | 43.9672 | 395.6929
| 2227 | 70 | 34.2932 | 65.6979 | 43.966 | 43.9671 | 395.6938
| 2228 | 70 | 34.2933 | 65.6979 | 43.9661 | 43.967 | 395.6945
| 2229 | 70 | 34.2933 | 65.698 | 43.9661 | 43.9669 | 395.6951
| 2230 | 70 | 34.2933 | 65.698 | 43.9662 | 43.9668 | 395.6956
| 2231 | 70 | 34.2933 | 65.698 | 43.9662 | 43.9668 | 395.696
| 2232 | 70 | 34.2933 | 65.698 | 43.9663 | 43.9667 | 395.6963
| 2233 | 70 | 34.2933 | 65.698 | 43.9663 | 43.9667 | 395.6966
| 2234 | 70 | 34.2933 | 65.698 | 43.9663 | 43.9666 | 395.6969
| 2235 | 70 | 34.2933 | 65.698 | 43.9663 | 43.9666 | 395.6971
| 2236 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9666 | 395.6972
| 2237 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9666 | 395.6974
| 2238 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6975
| 2239 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6976
| 2240 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6977
| 2241 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6977
| 2242 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6978
| 2243 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6979
| 2244 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6979
| 2245 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.6979
| 2246 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.698
| 2247 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.698
| 2248 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.698
| 2249 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.698
| 2250 | 70 | 34.2934 | 65.698 | 43.9664 | 43.9665 | 395.698
| 2251 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.698
| 2252 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2253 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2254 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2255 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2256 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2257 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2258 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2259 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
| 2260 | 70 | 34.2934 | 65.698 | 43.9665 | 43.9665 | 395.6981
[5 empty] | 48 hour cooling load |  | 15955.4051