## EPlus Results
EnergyPlus Results for ASHRAE 1052RP Analytical Test TC3
Sinusoid change in outdoor temperature, mean=20C, swing=15C
3 layer opaque surface
Date/Time | Hour of Year | EnergyPlus - Outdoor Dry Bulb Temperature | Environment:Diffuse Solar [W/m2](Hourly) | Environment:Direct Solar [W/m2](Hourly) | ZONE ONE:Zone/Sys Sensible Heating Energy[J](Hourly) | ZONE ONE:Zone/Sys Sensible Cooling Energy[J](Hourly) | ZONE ONE:Mean Air Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Inside Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Outside Temperature[C](Hourly) | ZONE SURFACE NORTH:Surface Int Convection Coeff[W/m2-K](Hourly) | ZONE SURFACE NORTH:Surface Ext Convection Coeff[W/m2-K](Hourly) | ZONE ONE:Zone/Sys Sensible Load Energy[J](Hourly) | EnergyPlus - Zone Sensible Cooling Load
01/01 01:00:00 | 1 | 22.2167 | 0 | 0 | 132393.6435 | 0 | 20 | 18.6716 | 19.9107 | 3.076 | 10.22 | -132393.6435 | -36.776
01/01 02:00:00 | 2 | 25.9583 | 0 | 0 | 126084.4799 | 0 | 20 | 18.7349 | 23.2515 | 3.076 | 10.22 | -126084.4799 | -35.0235
01/01 03:00:00 | 3 | 29.3083 | 0 | 0 | 111118.8303 | 0 | 20 | 18.885 | 26.3931 | 3.076 | 10.22 | -111118.8303 | -30.8663
01/01 04:00:00 | 4 | 31.9417 | 0 | 0 | 88620.2404 | 0 | 20 | 19.1108 | 29.0438 | 3.076 | 10.22 | -88620.2404 | -24.6167
01/01 05:00:00 | 5 | 33.775 | 0 | 0 | 60116.3021 | 0 | 20 | 19.3968 | 31.0742 | 3.076 | 10.22 | -60116.3021 | -16.699
01/01 06:00:00 | 6 | 34.75 | 0 | 0 | 27563.4701 | 0 | 20 | 19.7234 | 32.4041 | 3.076 | 10.22 | -27563.4701 | -7.6565 | -151.638
01/01 07:00:00 | 7 | 34.65 | 0 | 0 | 1576.0757 | 8367.6287 | 20 | 20.0681 | 32.8572 | 3.076 | 10.22 | 8367.6287 | 2.3243
01/01 08:00:00 | 8 | 33.525 | 0 | 0 | 0 | 40650.8392 | 20 | 20.4079 | 32.4012 | 3.076 | 10.22 | 40650.8392 | 11.2919
01/01 09:00:00 | 9 | 31.5583 | 0 | 0 | 0 | 71717.0911 | 20 | 20.7196 | 31.1515 | 3.076 | 10.22 | 71717.0911 | 19.9214
01/01 10:00:00 | 10 | 28.7917 | 0 | 0 | 0 | 97839.5365 | 20 | 20.9817 | 29.1455 | 3.076 | 10.22 | 97839.5365 | 27.1776
01/01 11:00:00 | 11 | 25.3417 | 0 | 0 | 0 | 117245.9292 | 20 | 21.1764 | 26.4592 | 3.076 | 10.22 | 117245.9292 | 32.5683
01/01 12:00:00 | 12 | 21.5833 | 0 | 0 | 0 | 128638.6036 | 20 | 21.2907 | 23.354 | 3.076 | 10.22 | 128638.6036 | 35.7329
01/01 13:00:00 | 13 | 17.725 | 0 | 0 | 0 | 131323.4498 | 20 | 21.3177 | 20.038 | 3.076 | 10.22 | 131323.4498 | 36.4787
01/01 14:00:00 | 14 | 14 | 0 | 0 | 0 | 125050.2037 | 20 | 21.2547 | 16.7005 | 3.076 | 10.22 | 125050.2037 | 34.7362
01/01 15:00:00 | 15 | 10.6333 | 0 | 0 | 0 | 110125.6039 | 20 | 21.105 | 13.5567 | 3.076 | 10.22 | 110125.6039 | 30.5904
01/01 16:00:00 | 16 | 7.9583 | 0 | 0 | 0 | 87665.7125 | 20 | 20.8796 | 10.8722 | 3.076 | 10.22 | 87665.7125 | 24.3516
01/01 17:00:00 | 17 | 6.125 | 0 | 0 | 0 | 59190.7455 | 20 | 20.5939 | 8.8371 | 3.076 | 10.22 | 59190.7455 | 16.4419
01/01 18:00:00 | 18 | 5.2083 | 0 | 0 | 0 | 26621.4352 | 20 | 20.2671 | 7.5418 | 3.076 | 10.22 | 26621.4352 | 7.3948 | 279.0102
01/01 19:00:00 | 19 | 5.2917 | 0 | 0 | 9033.0095 | 1251.5506 | 20 | 19.9219 | 7.0896 | 3.076 | 10.22 | -9033.0095 | -2.5092
01/01 20:00:00 | 20 | 6.375 | 0 | 0 | 41664.5549 | 0 | 20 | 19.5819 | 7.5129 | 3.076 | 10.22 | -41664.5549 | -11.5735
01/01 21:00:00 | 21 | 8.3417 | 0 | 0 | 72728.7215 | 0 | 20 | 19.2702 | 8.7586 | 3.076 | 10.22 | -72728.7215 | -20.2024
01/01 22:00:00 | 22 | 11.1667 | 0 | 0 | 98872.5368 | 0 | 20 | 19.0079 | 10.7996 | 3.076 | 10.22 | -98872.5368 | -27.4646
01/01 23:00:00 | 23 | 14.6 | 0 | 0 | 118320.8694 | 0 | 20 | 18.8128 | 13.487 | 3.076 | 10.22 | -118320.8694 | -32.8669
01/01 24:00:00 | 24 | 18.375 | 0 | 0 | 129727.1892 | 0 | 20 | 18.6983 | 16.5964 | 3.076 | 10.22 | -129727.1892 | -36.0353 | -130.6519 | absolute | 561.3002
01/02 01:00:00 | 25 | 22.2167 | 0 | 0 | 132393.6435 | 0 | 20 | 18.6716 | 19.9107 | 3.076 | 10.22 | -132393.6435 | -36.776
01/02 02:00:00 | 26 | 25.9583 | 0 | 0 | 126084.4799 | 0 | 20 | 18.7349 | 23.2515 | 3.076 | 10.22 | -126084.4799 | -35.0235
01/02 03:00:00 | 27 | 29.3083 | 0 | 0 | 111118.8303 | 0 | 20 | 18.885 | 26.3931 | 3.076 | 10.22 | -111118.8303 | -30.8663
01/02 04:00:00 | 28 | 31.9417 | 0 | 0 | 88620.2404 | 0 | 20 | 19.1108 | 29.0438 | 3.076 | 10.22 | -88620.2404 | -24.6167
01/02 05:00:00 | 29 | 33.775 | 0 | 0 | 60116.3021 | 0 | 20 | 19.3968 | 31.0742 | 3.076 | 10.22 | -60116.3021 | -16.699
01/02 06:00:00 | 30 | 34.75 | 0 | 0 | 27563.4701 | 0 | 20 | 19.7234 | 32.4041 | 3.076 | 10.22 | -27563.4701 | -7.6565
01/02 07:00:00 | 31 | 34.65 | 0 | 0 | 1576.0757 | 8367.6287 | 20 | 20.0681 | 32.8572 | 3.076 | 10.22 | 8367.6287 | 2.3243
01/02 08:00:00 | 32 | 33.525 | 0 | 0 | 0 | 40650.8392 | 20 | 20.4079 | 32.4012 | 3.076 | 10.22 | 40650.8392 | 11.2919
01/02 09:00:00 | 33 | 31.5583 | 0 | 0 | 0 | 71717.0911 | 20 | 20.7196 | 31.1515 | 3.076 | 10.22 | 71717.0911 | 19.9214
01/02 10:00:00 | 34 | 28.7917 | 0 | 0 | 0 | 97839.5365 | 20 | 20.9817 | 29.1455 | 3.076 | 10.22 | 97839.5365 | 27.1776
01/02 11:00:00 | 35 | 25.3417 | 0 | 0 | 0 | 117245.9292 | 20 | 21.1764 | 26.4592 | 3.076 | 10.22 | 117245.9292 | 32.5683
01/02 12:00:00 | 36 | 21.5833 | 0 | 0 | 0 | 128638.6036 | 20 | 21.2907 | 23.354 | 3.076 | 10.22 | 128638.6036 | 35.7329
01/02 13:00:00 | 37 | 17.725 | 0 | 0 | 0 | 131323.4498 | 20 | 21.3177 | 20.038 | 3.076 | 10.22 | 131323.4498 | 36.4787
01/02 14:00:00 | 38 | 14 | 0 | 0 | 0 | 125050.2037 | 20 | 21.2547 | 16.7005 | 3.076 | 10.22 | 125050.2037 | 34.7362
01/02 15:00:00 | 39 | 10.6333 | 0 | 0 | 0 | 110125.6039 | 20 | 21.105 | 13.5567 | 3.076 | 10.22 | 110125.6039 | 30.5904
01/02 16:00:00 | 40 | 7.9583 | 0 | 0 | 0 | 87665.7125 | 20 | 20.8796 | 10.8722 | 3.076 | 10.22 | 87665.7125 | 24.3516
01/02 17:00:00 | 41 | 6.125 | 0 | 0 | 0 | 59190.7455 | 20 | 20.5939 | 8.8371 | 3.076 | 10.22 | 59190.7455 | 16.4419
01/02 18:00:00 | 42 | 5.2083 | 0 | 0 | 0 | 26621.4352 | 20 | 20.2671 | 7.5418 | 3.076 | 10.22 | 26621.4352 | 7.3948
01/02 19:00:00 | 43 | 5.2917 | 0 | 0 | 9033.0095 | 1251.5506 | 20 | 19.9219 | 7.0896 | 3.076 | 10.22 | -9033.0095 | -2.5092
01/02 20:00:00 | 44 | 6.375 | 0 | 0 | 41664.5549 | 0 | 20 | 19.5819 | 7.5129 | 3.076 | 10.22 | -41664.5549 | -11.5735
01/02 21:00:00 | 45 | 8.3417 | 0 | 0 | 72728.7215 | 0 | 20 | 19.2702 | 8.7586 | 3.076 | 10.22 | -72728.7215 | -20.2024
01/02 22:00:00 | 46 | 11.1667 | 0 | 0 | 98872.5368 | 0 | 20 | 19.0079 | 10.7996 | 3.076 | 10.22 | -98872.5368 | -27.4646
01/02 23:00:00 | 47 | 14.6 | 0 | 0 | 118320.8694 | 0 | 20 | 18.8128 | 13.487 | 3.076 | 10.22 | -118320.8694 | -32.8669
01/02 24:00:00 | 48 | 18.375 | 0 | 0 | 129727.1892 | 0 | 20 | 18.6983 | 16.5964 | 3.076 | 10.22 | -129727.1892 | -36.0353
01/03 01:00:00 | 49 | 22.2167 | 0 | 0 | 132393.6435 | 0 | 20 | 18.6716 | 19.9107 | 3.076 | 10.22 | -132393.6435 | -36.776
01/03 02:00:00 | 50 | 25.9583 | 0 | 0 | 126084.4799 | 0 | 20 | 18.7349 | 23.2515 | 3.076 | 10.22 | -126084.4799 | -35.0235
01/03 03:00:00 | 51 | 29.3083 | 0 | 0 | 111118.8303 | 0 | 20 | 18.885 | 26.3931 | 3.076 | 10.22 | -111118.8303 | -30.8663
01/03 04:00:00 | 52 | 31.9417 | 0 | 0 | 88620.2404 | 0 | 20 | 19.1108 | 29.0438 | 3.076 | 10.22 | -88620.2404 | -24.6167
01/03 05:00:00 | 53 | 33.775 | 0 | 0 | 60116.3021 | 0 | 20 | 19.3968 | 31.0742 | 3.076 | 10.22 | -60116.3021 | -16.699
01/03 06:00:00 | 54 | 34.75 | 0 | 0 | 27563.4701 | 0 | 20 | 19.7234 | 32.4041 | 3.076 | 10.22 | -27563.4701 | -7.6565
01/03 07:00:00 | 55 | 34.65 | 0 | 0 | 1576.0757 | 8367.6287 | 20 | 20.0681 | 32.8572 | 3.076 | 10.22 | 8367.6287 | 2.3243
01/03 08:00:00 | 56 | 33.525 | 0 | 0 | 0 | 40650.8392 | 20 | 20.4079 | 32.4012 | 3.076 | 10.22 | 40650.8392 | 11.2919
01/03 09:00:00 | 57 | 31.5583 | 0 | 0 | 0 | 71717.0911 | 20 | 20.7196 | 31.1515 | 3.076 | 10.22 | 71717.0911 | 19.9214
01/03 10:00:00 | 58 | 28.7917 | 0 | 0 | 0 | 97839.5365 | 20 | 20.9817 | 29.1455 | 3.076 | 10.22 | 97839.5365 | 27.1776
01/03 11:00:00 | 59 | 25.3417 | 0 | 0 | 0 | 117245.9292 | 20 | 21.1764 | 26.4592 | 3.076 | 10.22 | 117245.9292 | 32.5683
01/03 12:00:00 | 60 | 21.5833 | 0 | 0 | 0 | 128638.6036 | 20 | 21.2907 | 23.354 | 3.076 | 10.22 | 128638.6036 | 35.7329
01/03 13:00:00 | 61 | 17.725 | 0 | 0 | 0 | 131323.4498 | 20 | 21.3177 | 20.038 | 3.076 | 10.22 | 131323.4498 | 36.4787
01/03 14:00:00 | 62 | 14 | 0 | 0 | 0 | 125050.2037 | 20 | 21.2547 | 16.7005 | 3.076 | 10.22 | 125050.2037 | 34.7362
01/03 15:00:00 | 63 | 10.6333 | 0 | 0 | 0 | 110125.6039 | 20 | 21.105 | 13.5567 | 3.076 | 10.22 | 110125.6039 | 30.5904
01/03 16:00:00 | 64 | 7.9583 | 0 | 0 | 0 | 87665.7125 | 20 | 20.8796 | 10.8722 | 3.076 | 10.22 | 87665.7125 | 24.3516
01/03 17:00:00 | 65 | 6.125 | 0 | 0 | 0 | 59190.7455 | 20 | 20.5939 | 8.8371 | 3.076 | 10.22 | 59190.7455 | 16.4419
01/03 18:00:00 | 66 | 5.2083 | 0 | 0 | 0 | 26621.4352 | 20 | 20.2671 | 7.5418 | 3.076 | 10.22 | 26621.4352 | 7.3948
01/03 19:00:00 | 67 | 5.2917 | 0 | 0 | 9033.0094 | 1251.5506 | 20 | 19.9219 | 7.0896 | 3.076 | 10.22 | -9033.0094 | -2.5092
01/03 20:00:00 | 68 | 6.375 | 0 | 0 | 41664.5549 | 0 | 20 | 19.5819 | 7.5129 | 3.076 | 10.22 | -41664.5549 | -11.5735
01/03 21:00:00 | 69 | 8.3417 | 0 | 0 | 72728.7215 | 0 | 20 | 19.2702 | 8.7586 | 3.076 | 10.22 | -72728.7215 | -20.2024
01/03 22:00:00 | 70 | 11.1667 | 0 | 0 | 98872.5368 | 0 | 20 | 19.0079 | 10.7996 | 3.076 | 10.22 | -98872.5368 | -27.4646
01/03 23:00:00 | 71 | 14.6 | 0 | 0 | 118320.8694 | 0 | 20 | 18.8128 | 13.487 | 3.076 | 10.22 | -118320.8694 | -32.8669
01/03 24:00:00 | 72 | 18.375 | 0 | 0 | 129727.1892 | 0 | 20 | 18.6983 | 16.5964 | 3.076 | 10.22 | -129727.1892 | -36.0353
[7 empty] | Average over 24 hours |  |  | 3.076 | 10.22
24 hour zone load

## ASHRAE Results
ASHRAE 1052RP Toolkit Test TC3
Data taken from D:\ASHRAE 1052RP OUTPUTS
3 layer opaque surface
Sinusoidal change in outdoor temperature
| Hour | T_out_air | Load
|  | ASHRAE 1052RP - Outdoor Dry Bulb Temperature | ASHRAE 1052RP - Zone Sensible Cooling Load
| 1 | 23.8823 | -37.2136
| 2 | 27.5 | -34.2127
| 3 | 30.6066 | -28.8802
| 4 | 32.9904 | -21.5795
| 5 | 34.4889 | -12.8083
| 6 | 35 | -3.1641 | -137.8584
| 7 | 34.4889 | 6.6956
| 8 | 32.9904 | 16.099
| 9 | 30.6066 | 24.4054
| 10 | 27.5 | 31.0485
| 11 | 23.8823 | 35.5757
| 12 | 20 | 37.6786
| 13 | 16.1177 | 37.2136
| 14 | 12.5 | 34.2127
| 15 | 9.3934 | 28.8802
| 16 | 7.0096 | 21.5795
| 17 | 5.5111 | 12.8083
| 18 | 5 | 3.1641 | 289.3612
| 19 | 5.5111 | -6.6956
| 20 | 7.0096 | -16.099
| 21 | 9.3934 | -24.4054
| 22 | 12.5 | -31.0485
| 23 | 16.1177 | -35.5757
| 24 | 20 | -37.6786 | -151.5028 | absolute | 578.7224
| 25 | 23.8823 | -37.2136
| 26 | 27.5 | -34.2127
| 27 | 30.6066 | -28.8802
| 28 | 32.9904 | -21.5795
| 29 | 34.4889 | -12.8083
| 30 | 35 | -3.1641
| 31 | 34.4889 | 6.6956
| 32 | 32.9904 | 16.099
| 33 | 30.6066 | 24.4054
| 34 | 27.5 | 31.0485
| 35 | 23.8823 | 35.5757
| 36 | 20 | 37.6786
| 37 | 16.1177 | 37.2136
| 38 | 12.5 | 34.2127
| 39 | 9.3934 | 28.8802
| 40 | 7.0096 | 21.5795
| 41 | 5.5111 | 12.8083
| 42 | 5 | 3.1641
| 43 | 5.5111 | -6.6956
| 44 | 7.0096 | -16.099
| 45 | 9.3934 | -24.4054
| 46 | 12.5 | -31.0485
| 47 | 16.1177 | -35.5757
| 48 | 20 | -37.6786
| 49 | 23.8823 | -37.2136
| 50 | 27.5 | -34.2127
| 51 | 30.6066 | -28.8802
| 52 | 32.9904 | -21.5795
| 53 | 34.4889 | -12.8083
| 54 | 35 | -3.1641
| 55 | 34.4889 | 6.6956
| 56 | 32.9904 | 16.099
| 57 | 30.6066 | 24.4054
| 58 | 27.5 | 31.0485
| 59 | 23.8823 | 35.5757
| 60 | 20 | 37.6786
| 61 | 16.1177 | 37.2136
| 62 | 12.5 | 34.2127
| 63 | 9.3934 | 28.8802
| 64 | 7.0096 | 21.5795
| 65 | 5.5111 | 12.8083
| 66 | 5 | 3.1641
| 67 | 5.5111 | -6.6956
| 68 | 7.0096 | -16.099
| 69 | 9.3934 | -24.4054
| 70 | 12.5 | -31.0485
| 71 | 16.1177 | -35.5757
| 72 | 20 | -37.6786
| 73 | 23.8823 | -37.2136
| 74 | 27.5 | -34.2127
| 75 | 30.6066 | -28.8802
| 76 | 32.9904 | -21.5795
| 77 | 34.4889 | -12.8083
| 78 | 35 | -3.1641
| 79 | 34.4889 | 6.6956
| 80 | 32.9904 | 16.099
| 81 | 30.6066 | 24.4054
| 82 | 27.5 | 31.0485
| 83 | 23.8823 | 35.5757
| 84 | 20 | 37.6786
| 85 | 16.1177 | 37.2136
| 86 | 12.5 | 34.2127
| 87 | 9.3934 | 28.8802
| 88 | 7.0096 | 21.5795
| 89 | 5.5111 | 12.8083
| 90 | 5 | 3.1641
| 91 | 5.5111 | -6.6956
| 92 | 7.0096 | -16.099
| 93 | 9.3934 | -24.4054
| 94 | 12.5 | -31.0485
| 95 | 16.1177 | -35.5757
| 96 | 20 | -37.6786
| 97 | 23.8823 | -37.2136
| 98 | 27.5 | -34.2127
| 99 | 30.6066 | -28.8802
| 100 | 32.9904 | -21.5795
| 101 | 34.4889 | -12.8083
| 102 | 35 | -3.1641
| 103 | 34.4889 | 6.6956
| 104 | 32.9904 | 16.099
| 105 | 30.6066 | 24.4054
| 106 | 27.5 | 31.0485
| 107 | 23.8823 | 35.5757
| 108 | 20 | 37.6786
| 109 | 16.1177 | 37.2136
| 110 | 12.5 | 34.2127
| 111 | 9.3934 | 28.8802
| 112 | 7.0096 | 21.5795
| 113 | 5.5111 | 12.8083
| 114 | 5 | 3.1641
| 115 | 5.5111 | -6.6956
| 116 | 7.0096 | -16.099
| 117 | 9.3934 | -24.4054
| 118 | 12.5 | -31.0485
| 119 | 16.1177 | -35.5757
| 120 | 20 | -37.6786
| 121 | 23.8823 | -37.2136
| 122 | 27.5 | -34.2127
| 123 | 30.6066 | -28.8802
| 124 | 32.9904 | -21.5795
| 125 | 34.4889 | -12.8083
| 126 | 35 | -3.1641
| 127 | 34.4889 | 6.6956
| 128 | 32.9904 | 16.099
| 129 | 30.6066 | 24.4054
| 130 | 27.5 | 31.0485
| 131 | 23.8823 | 35.5757
| 132 | 20 | 37.6786
| 133 | 16.1177 | 37.2136
| 134 | 12.5 | 34.2127
| 135 | 9.3934 | 28.8802
| 136 | 7.0096 | 21.5795
| 137 | 5.5111 | 12.8083
| 138 | 5 | 3.1641
| 139 | 5.5111 | -6.6956
| 140 | 7.0096 | -16.099
| 141 | 9.3934 | -24.4054
| 142 | 12.5 | -31.0485
| 143 | 16.1177 | -35.5757
| 144 | 20 | -37.6786
| 145 | 23.8823 | -37.2136
| 146 | 27.5 | -34.2127
| 147 | 30.6066 | -28.8802
| 148 | 32.9904 | -21.5795
| 149 | 34.4889 | -12.8083
| 150 | 35 | -3.1641
| 151 | 34.4889 | 6.6956
| 152 | 32.9904 | 16.099
| 153 | 30.6066 | 24.4054
| 154 | 27.5 | 31.0485
| 155 | 23.8823 | 35.5757
| 156 | 20 | 37.6786
| 157 | 16.1177 | 37.2136
| 158 | 12.5 | 34.2127
| 159 | 9.3934 | 28.8802
| 160 | 7.0096 | 21.5795
| 161 | 5.5111 | 12.8083
| 162 | 5 | 3.1641
| 163 | 5.5111 | -6.6956
| 164 | 7.0096 | -16.099
| 165 | 9.3934 | -24.4054
| 166 | 12.5 | -31.0485
| 167 | 16.1177 | -35.5757
| 168 | 20 | -37.6786
| 169 | 23.8823 | -37.2136
| 170 | 27.5 | -34.2127
| 171 | 30.6066 | -28.8802
| 172 | 32.9904 | -21.5795
| 173 | 34.4889 | -12.8083
| 174 | 35 | -3.1641
| 175 | 34.4889 | 6.6956
| 176 | 32.9904 | 16.099
| 48 hour zone load |  | 0