## Infil-1
EnergyPlus Results for ASHRAE 1052RP Analytical Tests
1052 Toolkit Software Version 1.0
EnergyPlus Version 8.2.0
Test Infiltration-2
| Test Parameter |  |  | Units | 1052RP | EnergyPlus | % Diff
| Mass Flow Rate of Air |  |  | Kg/s | 0.1489 | 0.15057 | 1.123%
| Zone Load |  |  | W | 1510.301 | 1525.7642 | 1.024%
| Height of Neutral Pressure Zone |  |  | m | 4.9345 | 4.9326 | -0.038%
| Date/Time | Environment:Site Outdoor Air Drybulb Temperature [C](Hourly) | Environment:Site Outdoor Air Density [kg/m3](Hourly) | ZONE ONE:Zone Air Temperature [C](Hourly) | ZONE ONE:Zone Air Humidity Ratio [](Hourly) |  | Indoor Density | Den in/Den out | Exponent 1/2x | (Den Ratio)^1/2x
| 08/21 01:00:00 | 10 | 1.2375 | 20 | 0.0059205 |  | 1.1927 | 0.96379 | 0.76923 | 0.97203
|  | x | 0.65
|  | H wall | 10 | m
|  | h opening | 0.5 | m
|  |  | (H wall - h opening)/2 = |  |  | 9.75
|  |  | h NPL = | 4.9326