## Cases 195
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
Low Mass Building |  | Numbers in red are changes made to conform with ASHRAE Standard 140P; only ESP results shown for this case
BESTEST Case | 195
Description | Solid Conduction Problem
Rectangular box of low mass construction
No windows, internal load or infiltration
Constant 20C setpoint
Annual Heating (MWh)
BESTEST Minimum | 4.167
BESTEST Maximum | 4.167
BESTEST Mean | 4.167
E-Plus | 4.3574
Difference, % | 4.569%
EnergyPlus Within Range | NO
Annual Cooling (MWh)
BESTEST Minimum | 0.414
BESTEST Maximum | 0.414
BESTEST Mean | 0.414
E-Plus | 0.41216
Difference, % | -0.4452%
EnergyPlus Within Range | NO
Peak Heating (KW)
BESTEST Minimum | 2.004
BESTEST Maximum | 2.004
BESTEST Mean | 2.004
E-Plus | 2.0902
Difference, % | 4.302%
EnergyPlus Within Range | NO
Peak Cooling (KW)
BESTEST Minimum | 0.651
BESTEST Maximum | 0.651
BESTEST Mean | 0.651
E-Plus | 0.72935
Difference, % | 12.04%
EnergyPlus Within Range | NO
Checks using peak heating day (internal load = 0.2 kW with 60% radiant, infiltration = 0.5 ACH)
Internal load
Infiltration
Total
Internal + Infiltration
Checks using peak cooling day (internal load = 0.2 kW with 60% radiant, infiltration = 0.5 ACH)
Internal load
Infiltration
Total
Internal + Infiltration
Checks using annual heating load
Internal load
Infiltration
Total
Internal + Infiltration
Checks using annual cooling load
Internal load
Infiltration
Total
Internal + Infiltration

## Cases 600
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
Low Mass Building |  | Numbers in red are changes made to conform with ASHRAE Standard 140P
BESTEST Case | 600 |  | 610 | 620 | 630 | 640 | 650
Description | Basic Heat Transfer Problem |  | South Shade Problem | East/West Incid./Trans. Problem | East/West Shade Problem | Setback Problem | Night Ventilation Problem
| Windows on South wall |  | Same as 600 with | Windows on East & West wall | Same as 620 with | Same as 600 | Same as 600
| 200 w internal load |  | 1.0M overhang on South Wall | 200 w internal load | 1.0M overhang & fins on | Setback Thermostat | Vent air 1800-700 hrs
| 0.5 ACH infiltration |  |  | 0.5 ACH infiltration | windows from roof to | Cooling 27C, all hours | Cooling 27C, 700-1800 hrs
| H/C Setpoint 20C/27C |  |  | H/C Setpoint 20C/27C | ground | Heating 10C, 2300 to 0700 | Heating, always off
Heating 20C, 0700 to 2300
Annual Heating (MWh)
BESTEST Minimum | 4.296 |  | 4.355 | 4.613 | 5.05 | 2.751 | 0
BESTEST Maximum | 5.709 |  | 5.786 | 5.944 | 6.469 | 3.803 | 0
BESTEST Mean | 5.09 |  | 5.146 | 5.407 | 5.783 | 3.207 | 0
E-Plus | 4.3784 |  | 4.4215 | 4.5502 | 4.8814 | 2.6843 | 0
Difference, % | -13.98% |  | -14.08% | -15.85% | -15.59% | -16.3% | #DIV/0!
EnergyPlus Within Range | YES |  | YES | NO | NO | NO | YES
Annual Cooling (MWh)
BESTEST Minimum | 6.137 |  | 3.915 | 3.417 | 2.129 | 5.952 | 4.816
BESTEST Maximum | 7.964 |  | 5.778 | 5.004 | 3.701 | 7.811 | 6.545
BESTEST Mean | 6.832 |  | 4.964 | 4.218 | 2.832 | 6.592 | 5.482
E-Plus | 6.7404 |  | 4.7464 | 4.1676 | 2.7804 | 6.4538 | 5.3044
Difference, % | -1.341% |  | -4.383% | -1.195% | -1.823% | -2.096% | -3.24%
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 3.437 |  | 3.437 | 3.591 | 3.592 | 5.232 | 0
BESTEST Maximum | 4.354 |  | 4.354 | 4.379 | 4.28 | 6.954 | 0
BESTEST Mean | 4 |  | 3.998 | 4.062 | 4.006 | 6.031 | 0
E-Plus | 3.7501 |  | 3.7396 | 3.7409 | 3.7206 | 6.2768 | 0
Difference, % | -6.248% |  | -6.463% | -7.904% | -7.124% | 4.076% | #DIV/0!
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 5.965 |  | 5.669 | 3.634 | 3.072 | 5.892 | 5.831
BESTEST Maximum | 6.827 |  | 6.371 | 5.096 | 4.116 | 6.776 | 6.679
BESTEST Mean | 6.461 |  | 5.988 | 4.343 | 3.626 | 6.41 | 6.321
E-Plus | 6.5655 |  | 6.1645 | 3.9206 | 3.3761 | 6.5012 | 6.3727
Difference, % | 1.617% |  | 2.947% | -9.725% | -6.892% | 1.422% | 0.8184%
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES

## Cases 900
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
High Mass Building |  | Numbers in red are changes made to conform with ASHRAE Standard 140P
BESTEST Case | 900 |  | 910 | 920 | 930 | 940 | 960 | 950
Description | Basic Heat Transfer Problem |  | South Shade Problem | East/West Incid./Trans. Problem | East/West Shade Problem | Setback Problem | Passive Solar Problem | Night Ventilation Problem
| Windows on South wall |  | Same as 900 with | Windows on East & West wall | Same as 920 with | Same as 900 | Same as 900 but with | Same as 900
| 200 w internal load |  | 1.0M overhang on South Wall | 200 w internal load | 1.0M overhang & fins on | Setback Thermostat | sunspace and interior wall | Vent air 1800-700 hrs
| 0.5 ACH infiltration |  |  | 0.5 ACH infiltration | windows from roof to | Cooling 27C, all hours | Sunspace is uncontrolled | Cooling 27C, 700-1800 hrs
| H/C Setpoint 20C/27C |  |  | H/C Setpoint 20C/27C | ground | Heating 10C, 2300 to 0700 | and has two windows | Heating, always off
Heating 20C, 0700 to 2300
Annual Heating (MWh)
BESTEST Minimum | 1.17 |  | 1.575 | 3.313 | 4.143 | 0.793 | 2.311 | 0
BESTEST Maximum | 2.041 |  | 2.282 | 4.3 | 5.335 | 1.411 | 3.373 | 0
BESTEST Mean | 1.745 |  | 2.066 | 3.973 | 4.745 | 1.16 | 2.846 | 0
E-Plus | 1.2237 |  | 1.5058 | 3.1931 | 3.9062 | 0.7681 | 2.4083 | 0
Difference, % | -29.87% |  | -27.11% | -19.63% | -17.68% | -33.78% | -15.38% | #DIV/0!
EnergyPlus Within Range | YES |  | NO | NO | NO | NO | YES | YES
Annual Cooling (MWh)
BESTEST Minimum | 2.132 |  | 0.821 | 1.84 | 1.039 | 2.079 | 0.411 | 0.387
BESTEST Maximum | 3.415 |  | 1.872 | 3.092 | 2.238 | 3.241 | 0.803 | 0.921
BESTEST Mean | 2.678 |  | 1.447 | 2.552 | 1.644 | 2.578 | 0.618 | 0.605
E-Plus | 2.5077 |  | 1.2348 | 2.5485 | 1.6378 | 2.4333 | 0.63954 | 0.5298
Difference, % | -6.361% |  | -14.67% | -0.1388% | -0.3768% | -5.612% | 3.485% | -12.43%
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 2.85 |  | 2.858 | 3.308 | 3.355 | 3.98 | 2.41 | 0
BESTEST Maximum | 3.797 |  | 3.801 | 4.061 | 4.064 | 6.428 | 2.863 | 0
BESTEST Mean | 3.506 |  | 3.514 | 3.804 | 3.795 | 5.494 | 2.701 | 0
E-Plus | 3.1722 |  | 3.1718 | 3.483 | 3.5065 | 4.8155 | 2.6926 | 0
Difference, % | -9.521% |  | -9.738% | -8.438% | -7.603% | -12.35% | -0.3118% | #DIV/0!
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 2.888 |  | 1.896 | 2.385 | 1.873 | 2.888 | 0.953 | 2.033
BESTEST Maximum | 3.871 |  | 3.277 | 3.505 | 3.08 | 3.871 | 1.403 | 3.17
BESTEST Mean | 3.39 |  | 2.676 | 3.077 | 2.479 | 3.39 | 1.212 | 2.674
E-Plus | 3.2497 |  | 2.5734 | 2.7772 | 2.2746 | 3.2497 | 1.1435 | 2.3878
Difference, % | -4.137% |  | -3.835% | -9.745% | -8.246% | -4.137% | -5.656% | -10.7%
EnergyPlus Within Range | YES |  | YES | YES | YES | YES | YES | YES

## Free Float Cases
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
Free Floating Zone Temperature |  | Numbers in red are changes made to conform with ASHRAE Standard 140P
BESTEST Case | 600FF |  | 900FF | 650FF | 950FF | 960
Description | Basic Heat Transfer Problem |  | Basic Heat Transfer Problem | Basic Heat Transfer Problem | Basic Heat Transfer Problem | Passive Solar Problem
| Low Mass Building |  | High Mass Building | High Mass Building | High Mass Building | Same as 900 but with
| Windows on South wall |  | Windows on South wall | Windows on South wall | Windows on South wall | sunspace and interior wall
| 200 w internal load |  | 200 w internal load | 200 w internal load | 200 w internal load | Sunspace is uncontrolled
| 0.5 ACH infiltration |  | 0.5 ACH infiltration | 0.5 ACH infiltration | 0.5 ACH infiltration | and has two windows
| Free Float Temperature |  | Free Float Temperature | Vent Air 1703.16 m3/h 1800-700 | Vent Air 1703.16 m3/h 1800-700 | Temperatures below are
|  |  |  | Free Float Temperature | Free Float Temperature | for Sunspace
Maximum Annual Hourly Zone Temperature (C)
BESTEST Minimum | 64.9 |  | 41.8 | 63.2 | 35.5 | 48.9
BESTEST Maximum | 69.5 |  | 44.8 | 68.2 | 38.5 | 55.3
BESTEST Mean | 66.2 |  | 43.1 | 64.7 | 36.5 | 50.3
E-Plus | 65.2873 |  | 43.1596 | 63.5022 | 36.6437 | 52.3815
Difference, % | -1.379% |  | 0.1384% | -1.851% | 0.3937% | 4.138%
EnergyPlus Within Range | YES |  | YES | YES | YES | YES
Minimum Annual Hourly Zone Temperature (C)
BESTEST Minimum | -18.8 |  | -6.4 | -23 | -20.2 | -2.8
BESTEST Maximum | -15.6 |  | -1.6 | -21.6 | -18.6 | 3.9
BESTEST Mean | -17.6 |  | -4.2 | -22.7 | -19.6 | 1.4
E-Plus | -17.418 |  | -2.603 | -23.0438 | -20.3396 | 2.2205
Difference, % | -1.034% |  | -38.02% | 1.515% | 3.774% | 58.61%
EnergyPlus Within Range | YES |  | YES | NO | NO | YES
Average Annual Hourly Zone Temperature (C)
BESTEST Minimum | 24.2 |  | 24.5 | 18 | 14 | 26.4
BESTEST Maximum | 25.9 |  | 25.9 | 19.6 | 15 | 29
BESTEST Mean | 25.1 |  | 25.2 | 18.7 | 14.4 | 28
E-Plus | 25.8 |  | 25.9988 | 18.6399 | 14.4962 | 29.1286
Difference, % | 2.789% |  | 3.17% | -0.3213% | 0.668% | 4.031%
EnergyPlus Within Range | YES |  | NO | YES | YES | NO

## Compare Eplus Versions
Comparison of Results as EnergyPlus Versions are Updated
New Version
EnergyPlus Version --->
Run --->
Comments --->
Case 195 | Annual Heating (MWH) | 4.3574
| Annual Cooling (MWH) | 0.41216
| Peak Heating (kW) | 2.0902
| Peak Heating Time | 01/04 06:00:00
| Peak Cooling (kW) | 0.72935
| Peak Cooling Time | 07/26 16:00:00
Case 600 | Annual Heating (MWH) | 4.3784
| Annual Cooling (MWH) | 6.7404
| Peak Heating (kW) | 3.7501
| Peak Heating Time | 01/04 05:00:00
| Peak Cooling (kW) | 6.5655
| Peak Cooling Time | 10/17 13:00:00
Case 610 | Annual Heating (MWH) | 4.4215
| Annual Cooling (MWH) | 4.7464
| Peak Heating (kW) | 3.7396
| Peak Heating Time | 01/04 05:00:00
| Peak Cooling (kW) | 6.1645
| Peak Cooling Time | 12/23 13:00:00
Case 620 | Annual Heating (MWH) | 4.5502
| Annual Cooling (MWH) | 4.1676
| Peak Heating (kW) | 3.7409
| Peak Heating Time | 01/04 05:00:00
| Peak Cooling (kW) | 3.9206
| Peak Cooling Time | 07/26 10:00:00
Case 630 | Annual Heating (MWH) | 4.8814
| Annual Cooling (MWH) | 2.7804
| Peak Heating (kW) | 3.7206
| Peak Heating Time | 01/04 05:00:00
| Peak Cooling (kW) | 3.3761
| Peak Cooling Time | 07/26 17:00:00
Case 640 | Annual Heating (MWH) | 2.6843
| Annual Cooling (MWH) | 6.4538
| Peak Heating (kW) | 6.2768
| Peak Heating Time | 01/04 08:00:00
| Peak Cooling (kW) | 6.5012
| Peak Cooling Time | 10/17 13:00:00
Case 900 | Annual Heating (MWH) | 1.2237
| Annual Cooling (MWH) | 2.5077
| Peak Heating (kW) | 3.1722
| Peak Heating Time | 01/04 07:00:00
| Peak Cooling (kW) | 3.2497
| Peak Cooling Time | 10/17 15:00:00
Case 910 | Annual Heating (MWH) | 1.5058
| Annual Cooling (MWH) | 1.2348
| Peak Heating (kW) | 3.1718
| Peak Heating Time | 01/04 07:00:00
| Peak Cooling (kW) | 2.5734
| Peak Cooling Time | 10/17 15:00:00
Case 920 | Annual Heating (MWH) | 3.1931
| Annual Cooling (MWH) | 2.5485
| Peak Heating (kW) | 3.483
| Peak Heating Time | 01/04 07:00:00
| Peak Cooling (kW) | 2.7772
| Peak Cooling Time | 07/26 17:00:00
Case 930 | Annual Heating (MWH) | 3.9062
| Annual Cooling (MWH) | 1.6378
| Peak Heating (kW) | 3.5065
| Peak Heating Time | 01/04 07:00:00
| Peak Cooling (kW) | 2.2746
| Peak Cooling Time | 07/26 17:00:00
Case 940 | Annual Heating (MWH) | 0.7681
| Annual Cooling (MWH) | 2.4333
| Peak Heating (kW) | 4.8155
| Peak Heating Time | 01/04 08:00:00
| Peak Cooling (kW) | 3.2497
| Peak Cooling Time | 10/17 15:00:00
Case 960 | Annual Heating (MWH) | 2.4083
| Annual Cooling (MWH) | 0.63954
| Peak Heating (kW) | 2.6926
| Peak Heating Time | 01/04 08:00:00
| Peak Cooling (kW) | 1.1435
| Peak Cooling Time | 08/16 15:00:00
Case 600FF | Maximum Temp (C) | 65.2873
| Max Temp Time | 10/17 16:00:00
| Minimum Temp (C) | -17.418
| Min Temp Time | 01/04 08:00:00
Case 900FF | Maximum Temp (C) | 43.1596
| Max Temp Time | 09/02 15:00:00
| Minimum Temp (C) | -2.603
| Min Temp Time | 01/04 08:00:00
Case 650FF | Maximum Temp (C) | 63.5022
| Max Temp Time | 10/17 16:00:00
| Minimum Temp (C) | -23.0438
| Min Temp Time | 01/04 07:00:00
Case 950FF | Maximum Temp (C) | 36.6437
| Max Temp Time | 09/02 16:00:00
| Minimum Temp (C) | -20.3396
| Min Temp Time | 01/04 07:00:00
Case 650 | Annual Heating (MWH) | 0
| Annual Cooling (MWH) | 5.3044
| Peak Heating (kW) | 0
| Peak Heating Time | 01/01 01:00:00
| Peak Cooling (kW) | 6.3727
| Peak Cooling Time | 10/17 14:00:00
Case 950 | Annual Heating (MWH) | 0
| Annual Cooling (MWH) | 0.5298
| Peak Heating (kW) | 0
| Peak Heating Time | 01/01 01:00:00
| Peak Cooling (kW) | 2.3878
| Peak Cooling Time | 09/02 15:00:00