## Cases 195
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Low Mass Building
BESTEST Case | 195
Description | Solid Conduction Problem
Rectangular box of low mass construction
No windows, internal load or infiltration
Constant 20C setpoint
Annual Heating (MWh)
BESTEST Minimum | 4.167
BESTEST Maximum | 4.167
BESTEST Average | 4.167
E-Plus | 4.3574
Difference, % | 4.569%
EnergyPlus Within Range | NO
Annual Cooling (MWh)
BESTEST Minimum | 0.414
BESTEST Maximum | 0.414
BESTEST Average | 0.414
E-Plus | 0.41216
Difference, % | -0.4452%
EnergyPlus Within Range | NO
Peak Heating (KW)
BESTEST Minimum | 2.004
BESTEST Maximum | 2.004
BESTEST Average | 2.004
E-Plus | 2.0902
Difference, % | 4.302%
EnergyPlus Within Range | NO
Peak Cooling (KW)
BESTEST Minimum | 0.651
BESTEST Maximum | 0.651
BESTEST Average | 0.651
E-Plus | 0.72935
Difference, % | 12.04%
EnergyPlus Within Range | NO
Checks using peak heating day (internal load = 0.2 kW with 60% radiant, infiltration = 0.5 ACH)
Internal load
Infiltration
Total
Internal + Infiltration
Checks using peak cooling day (internal load = 0.2 kW with 60% radiant, infiltration = 0.5 ACH)
Internal load
Infiltration
Total
Internal + Infiltration
Checks using annual heating load
Internal load
Infiltration
Total
Internal + Infiltration
Checks using annual cooling load
Internal load
Infiltration
Total
Internal + Infiltration

## Cases 600
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Low Mass Building
BESTEST Case | 600 | 610 | 620 | 630 | 640 | 650
Description | Basic Heat Transfer Problem | South Shade Problem | East/West Incid./Trans. Problem | East/West Shade Problem | Setback Problem | Night Ventilation Problem
| Windows on South wall | Same as 600 with | Windows on East & West wall | Same as 620 with | Same as 600 | Same as 600
| 200 w internal load | 1.0M overhang on South Wall | 200 w internal load | 1.0M overhang & fins on | Setback Thermostat | Vent air 1800-700 hrs
| 0.5 ACH infiltration |  | 0.5 ACH infiltration | windows from roof to | Cooling 27C, all hours | Cooling 27C, 700-1800 hrs
| H/C Setpoint 20C/27C |  | H/C Setpoint 20C/27C | ground | Heating 10C, 2300 to 0700 | Heating, always off
Heating 20C, 0700 to 2300
Annual Heating (MWh)
BESTEST Minimum | 4.296 | 4.355 | 4.613 | 5.05 | 2.751 | 0
BESTEST Maximum | 5.709 | 5.786 | 5.944 | 6.469 | 3.803 | 4.171e-06
BESTEST Average | 5.0457 | 5.0984 | 5.3284 | 5.6861 | 3.1355 | 3.7918e-07
E-Plus | 4.3784 | 4.4215 | 4.5502 | 4.8814 | 2.6843 | 0
Difference, % | -13.23% | -13.28% | -14.6% | -14.15% | -14.39% | -100%
EnergyPlus Within Range | YES | YES | NO | NO | NO | YES
Annual Cooling (MWh)
BESTEST Minimum | 6.137 | 3.915 | 3.417 | 2.129 | 5.952 | 4.816
BESTEST Maximum | 8.448 | 6.139 | 5.482 | 3.701 | 8.097 | 7.064
BESTEST Average | 7.0535 | 5.1436 | 4.4157 | 2.9513 | 6.7902 | 5.7076
E-Plus | 6.7404 | 4.7464 | 4.1676 | 2.7804 | 6.4538 | 5.3044
Difference, % | -4.438% | -7.722% | -5.619% | -5.792% | -4.954% | -7.065%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 3.437 | 3.437 | 3.591 | 3.592 | 5.232 | 0
BESTEST Maximum | 4.354 | 4.354 | 4.379 | 4.28 | 6.954 | 0
BESTEST Average | 3.9518 | 3.9474 | 3.9981 | 3.9486 | 5.9027 | 0
E-Plus | 3.7501 | 3.7396 | 3.7409 | 3.7206 | 6.2768 | 0
Difference, % | -5.103% | -5.265% | -6.432% | -5.774% | 6.337% | #DIV/0!
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 5.965 | 5.669 | 3.634 | 3.072 | 5.884 | 5.831
BESTEST Maximum | 7.188 | 6.673 | 5.096 | 4.116 | 7.126 | 7.068
BESTEST Average | 6.5346 | 6.0901 | 4.3934 | 3.6881 | 6.4781 | 6.4042
E-Plus | 6.5655 | 6.1645 | 3.9206 | 3.3761 | 6.5012 | 6.3727
Difference, % | 0.4721% | 1.221% | -10.76% | -8.461% | 0.3563% | -0.491%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES

## Cases 900
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
High Mass Building
BESTEST Case | 900 | 910 | 920 | 930 | 940 | 960 | 950
Description | Basic Heat Transfer Problem | South Shade Problem | East/West Incid./Trans. Problem | East/West Shade Problem | Setback Problem | Passive Solar Problem | Night Ventilation Problem
| Windows on South wall | Same as 900 with | Windows on East & West wall | Same as 920 with | Same as 900 | Same as 900 but with | Same as 900
| 200 w internal load | 1.0M overhang on South Wall | 200 w internal load | 1.0M overhang & fins on | Setback Thermostat | sunspace and interior wall | Vent air 1800-700 hrs
| 0.5 ACH infiltration |  | 0.5 ACH infiltration | windows from roof to | Cooling 27C, all hours | Sunspace is uncontrolled | Cooling 27C, 700-1800 hrs
| H/C Setpoint 20C/27C |  | H/C Setpoint 20C/27C | ground | Heating 10C, 2300 to 0700 | and has two windows | Heating, always off
Heating 20C, 0700 to 2300
Annual Heating (MWh)
BESTEST Minimum | 1.17 | 1.512 | 3.261 | 4.143 | 0.793 | 2.144 | 0
BESTEST Maximum | 2.041 | 2.282 | 4.3 | 5.335 | 1.411 | 3.373 | 7.801e-06
BESTEST Average | 1.6489 | 1.9511 | 3.828 | 4.6032 | 1.0857 | 2.7086 | 7.0918e-07
E-Plus | 1.2237 | 1.5058 | 3.1931 | 3.9062 | 0.7681 | 2.4083 | 0
Difference, % | -25.79% | -22.82% | -16.59% | -15.14% | -29.25% | -11.09% | -100%
EnergyPlus Within Range | YES | NO | NO | NO | NO | YES | YES
Annual Cooling (MWh)
BESTEST Minimum | 2.132 | 0.821 | 1.84 | 1.039 | 2.079 | 0.4113 | 0.387
BESTEST Maximum | 3.669 | 1.883 | 3.313 | 2.238 | 3.546 | 0.895 | 0.921
BESTEST Average | 2.8257 | 1.5212 | 2.6836 | 1.7153 | 2.7249 | 0.66903 | 0.63476
E-Plus | 2.5077 | 1.2348 | 2.5485 | 1.6378 | 2.4333 | 0.63954 | 0.5298
Difference, % | -11.26% | -18.83% | -5.037% | -4.518% | -10.7% | -4.407% | -16.54%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 2.85 | 2.858 | 3.308 | 3.355 | 3.98 | 2.41 | 0
BESTEST Maximum | 3.797 | 3.801 | 4.061 | 4.064 | 6.428 | 2.863 | 0
BESTEST Average | 3.4519 | 3.4592 | 3.7375 | 3.7334 | 5.4144 | 2.686 | 0
E-Plus | 3.1722 | 3.1718 | 3.483 | 3.5065 | 4.8155 | 2.6926 | 0
Difference, % | -8.103% | -8.309% | -6.809% | -6.078% | -11.06% | 0.2449% | #DIV/0!
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 2.888 | 1.896 | 2.385 | 1.873 | 2.888 | 0.953 | 2.033
BESTEST Maximum | 3.932 | 3.277 | 3.505 | 3.08 | 3.932 | 1.422 | 3.17
BESTEST Average | 3.4596 | 2.6764 | 3.1234 | 2.5263 | 3.4596 | 1.2098 | 2.724
E-Plus | 3.2497 | 2.5734 | 2.7772 | 2.2746 | 3.2497 | 1.1435 | 2.3878
Difference, % | -6.065% | -3.848% | -11.09% | -9.963% | -6.065% | -5.484% | -12.34%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES

## Free Float Cases
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Free Floating Zone Temperature
BESTEST Case | 600FF | 900FF | 650FF | 950FF | 960
Description | Basic Heat Transfer Problem | Basic Heat Transfer Problem | Basic Heat Transfer Problem | Basic Heat Transfer Problem | Passive Solar Problem
| Low Mass Building | High Mass Building | Low Mass Building | High Mass Building | Same as 900 but with
| Windows on South wall | Windows on South wall | Windows on South wall | Windows on South wall | sunspace and interior wall
| 200 w internal load | 200 w internal load | 200 w internal load | 200 w internal load | Sunspace is uncontrolled
| 0.5 ACH infiltration | 0.5 ACH infiltration | 0.5 ACH infiltration | 0.5 ACH infiltration | and has two windows
| Free Float Temperature | Free Float Temperature | Vent Air 1703.16 m3/h 1800-700 hrs | Vent Air 1703.16 m3/h 1800-700 hrs
|  |  | Free Float Temperature | Free Float Temperature
Maximum Annual Hourly Zone Temperature (C)
BESTEST Minimum | 64.9 | 41.812 | 63.236 | 35.54 | 48.88
BESTEST Maximum | 75.1 | 46.4 | 73.5 | 38.5 | 55.34
BESTEST Average | 67.7159 | 43.6732 | 66.1236 | 36.629 | 50.5363
E-Plus | 65.2873 | 43.1596 | 63.5022 | 36.6437 | 52.3815
Difference, % | -3.586% | -1.176% | -3.964% | 0.04015% | 3.651%
EnergyPlus Within Range | YES | YES | YES | YES | YES
Minimum Annual Hourly Zone Temperature (C)
BESTEST Minimum | -18.8 | -6.38 | -23 | -20.2 | -2.82
BESTEST Maximum | -15.565 | -1.647 | -21 | -17.8 | 6
BESTEST Average | -17.6045 | -3.6767 | -22.3824 | -19.2964 | 2.2979
E-Plus | -17.418 | -2.603 | -23.0438 | -20.3396 | 2.2205
Difference, % | -1.059% | -29.2% | 2.955% | 5.406% | -3.369%
EnergyPlus Within Range | YES | YES | NO | NO | YES
Average Annual Hourly Zone Temperature (C)
BESTEST Minimum | 24.22 | 24.45 | 17.99 | 14 | 26.43
BESTEST Maximum | 27.4 | 27.5 | 20.8 | 15.3 | 30.5
BESTEST Average | 25.3306 | 25.4843 | 18.9104 | 14.469 | 28.205
E-Plus | 25.8 | 25.9988 | 18.6399 | 14.4962 | 29.1286
Difference, % | 1.853% | 2.019% | -1.43% | 0.1879% | 3.274%
EnergyPlus Within Range | YES | YES | YES | YES | YES

## Cases 200
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Low Mass Building
BESTEST Case | 200 | 210 | 215 | 220 | 230 | 240 | 250 | 270 | 280 | 290
Description | Infrared Radiation Problem | Int. Infrared Radiation Problem | Ext. Infrared Radiation | In-depth Base Case | Infiltration | Internal Gains | Ext. Shortwave Absorp | South Solar Gains | Cavity Albedo | South Shading
| Same as Case 210 with | Same as Case 220 with | Same as Case 220 with | Same as Case 600 with | Same as Case 220 with | Same as Case 220 with | Same as Case 220 with | Same as Case 220 with | Same as Case 270 with | Same as Case 270 with
| Ext. Infrared emittance = 0.1 | Int. Infrared emittance = 0.1 | Ext. Infrared emittance = 0.1 | No infiltration | 1.0 ACH Infiltration | 200 W Internal Load | Ext. shortwave abs = 0.9 | Windows | Int. shortwave abs = 0.1 | Overhang
|  |  |  | No internal load |  |  |  | Int. shortwave abs = 0.9
Int. solar absorp = 0.1
Thermal absorp = 0.9
Heat <20C, Cool > 20C
Annual Heating (MWh)
BESTEST Minimum | 5.252 | 6.456 | 5.547 | 6.944 | 10.376 | 5.649 | 4.751 | 4.51 | 4.675 | 4.577
BESTEST Maximum | 5.252 | 6.967 | 5.547 | 8.787 | 12.243 | 7.448 | 7.024 | 5.92 | 6.148 | 5.942
BESTEST Average | 5.252 | 6.634 | 5.547 | 7.6263 | 11.135 | 6.361 | 5.9807 | 5.1667 | 5.5008 | 5.2542
E-Plus | 5.5781 | 6.5979 | 5.9525 | 7.1101 | 10.8983 | 5.8679 | 5.1891 | 4.4525 | 4.6506 | 4.4878
Difference, % | 6.208% | -0.5442% | 7.311% | -6.769% | -2.126% | -7.752% | -13.24% | -13.82% | -15.46% | -14.59%
EnergyPlus Within Range | NO | YES | NO | YES | YES | YES | YES | NO | NO | NO
Annual Cooling (MWh)
BESTEST Minimum | 0.57 | 0.162 | 0.639 | 0.186 | 0.454 | 0.415 | 2.177 | 7.528 | 4.873 | 5.204
BESTEST Maximum | 0.57 | 0.6679 | 0.639 | 0.835 | 1.139 | 1.246 | 4.284 | 10.35 | 7.114 | 8.089
BESTEST Average | 0.57 | 0.52097 | 0.639 | 0.63608 | 0.92745 | 0.9849 | 2.917 | 8.932 | 6.0437 | 7.0451
E-Plus | 0.58684 | 0.36522 | 0.64348 | 0.40663 | 0.69576 | 0.70436 | 3.1632 | 8.4894 | 5.4978 | 6.3928
Difference, % | 2.955% | -29.9% | 0.701% | -36.07% | -24.98% | -28.48% | 8.441% | -4.955% | -9.032% | -9.26%
EnergyPlus Within Range | NO | YES | NO | YES | YES | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 2.651 | 2.701 | 2.787 | 2.867 | 4.386 | 2.685 | 2.866 | 2.863 | 2.864 | 2.863
BESTEST Maximum | 2.651 | 3.325 | 2.787 | 3.695 | 5.279 | 3.495 | 3.695 | 3.738 | 3.759 | 3.738
BESTEST Average | 2.651 | 2.9949 | 2.787 | 3.3373 | 4.9475 | 3.1521 | 3.344 | 3.375 | 3.3844 | 3.3734
E-Plus | 2.852 | 3.0403 | 3.031 | 3.2431 | 5.0636 | 3.0595 | 3.243 | 3.0235 | 3.0238 | 3.013
Difference, % | 7.58% | 1.516% | 8.756% | -2.825% | 2.345% | -2.938% | -3.021% | -10.41% | -10.66% | -10.68%
EnergyPlus Within Range | NO | YES | NO | YES | YES | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 0.863 | 0.476 | 1.007 | 0.56 | 1.059 | 0.739 | 2.258 | 6.356 | 4.444 | 6.2028
BESTEST Maximum | 0.863 | 1.142 | 1.007 | 1.34 | 1.875 | 1.54 | 4.912 | 7.234 | 5.236 | 6.976
BESTEST Average | 0.863 | 0.92569 | 1.007 | 1.0898 | 1.5981 | 1.2736 | 3.1332 | 6.7604 | 4.797 | 6.5301
E-Plus | 0.97395 | 0.81136 | 1.0732 | 0.90992 | 1.4066 | 1.0926 | 3.0465 | 6.8353 | 4.7126 | 6.7084
Difference, % | 12.86% | -12.35% | 6.577% | -16.5% | -11.98% | -14.21% | -2.766% | 1.108% | -1.76% | 2.729%
EnergyPlus Within Range | NO | YES | NO | YES | YES | YES | YES | YES | YES | YES

## Cases 300
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Low Mass Building
BESTEST Case | 300 | 310 | 320
Description | East/West Incid./Trans. Problem | East/West Shade Problem | Thermostat Problem
| Windows on East & West wall | Same as 300 with | Same as 270 with
| No internal load | 1.0M overhang & fins on | 20C Heating
| No infiltration | windows from roof to | 27C Cooling
| H/C Setpoint 20C/20C | ground
Annual Heating (MWh)
BESTEST Minimum | 4.761 | 5.221 | 3.859
BESTEST Maximum | 5.964 | 6.165 | 5.141
BESTEST Average | 5.3394 | 5.5833 | 4.4619
E-Plus | 4.4977 | 4.7764 | 3.7598
Difference, % | -15.76% | -14.45% | -15.73%
EnergyPlus Within Range | NO | NO | NO
Annual Cooling (MWh)
BESTEST Minimum | 4.302 | 2.732 | 5.061
BESTEST Maximum | 7.1 | 5.471 | 7.304
BESTEST Average | 5.8916 | 4.3678 | 6.0744
E-Plus | 5.4661 | 3.7381 | 5.8058
Difference, % | -7.222% | -14.42% | -4.422%
EnergyPlus Within Range | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 3.014 | 3.015 | 2.861
BESTEST Maximum | 3.77 | 2.9934 | 3.0227
BESTEST Average | 3.4138 | 2.9934 | 2.861
E-Plus | 3.0137 | 2.9934 | 3.0227
Difference, % | -11.72% | 0% | 5.651%
EnergyPlus Within Range | NO | NO | YES
Peak Cooling (KW)
BESTEST Minimum | 3.404 | 2.848 | 5.701
BESTEST Maximum | 4.929 | 4.164 | 6.553
BESTEST Average | 4.2423 | 3.6198 | 6.0775
E-Plus | 3.8985 | 3.263 | 6.1572
Difference, % | -8.105% | -9.856% | 1.312%
EnergyPlus Within Range | YES | YES | YES

## Cases 400 & 800
Comparison Of EnergyPlus Results with Standard 140-2011
Using EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }} with Standard 140-2011 weather file
BESTEST Min, Max, Average values conform with ASHRAE Standard 140
and also include results for DOE-2.1E and BLAST 3.0-334
Low Mass Building
BESTEST Case | 395 | 400 | 410 | 420 | 430 | 440 | 800 | 810
Description | Solid Conduction Test | Opaque Windows | Infiltration | Internal Gains | Exterior Shortwave Absorptance | Cavity Albedo | High Mass Without Solar Gains | High Mass Cavity Albedo
| Same as 400 except | 0 w internal load | Same as 400 except | Same as 410 except | Same as 420 except | Same as 600 except | Same as 430 except | Same as 900 except
| Replace opaque windows | 0 ACH infiltration | 0.5 ACH infiltration | 200 w internal load | Shortwave Abs.=0.6 | Int. Shortwave Abs.=0.1 | High mass walls | Int. Shortwave Abs.=0.1
| with Lt. Wt. Wall | Opaque Windows
Ext. Solar Abs.=0.1
Annual Heating (MWh)
BESTEST Minimum | 4.799 | 6.9 | 8.596 | 7.298 | 5.429 | 4.449 | 4.868 | 1.839
BESTEST Maximum | 5.835 | 8.77 | 10.506 | 9.151 | 7.827 | 5.811 | 7.228 | 3.004
BESTEST Average | 5.1293 | 7.5324 | 9.2793 | 7.9899 | 6.626 | 5.231 | 5.9893 | 2.6077
E-Plus | 4.9804 | 7.0226 | 8.9092 | 7.6519 | 6.0287 | 4.5686 | 5.3705 | 1.9716
Difference, % | -2.903% | -6.767% | -3.988% | -4.23% | -9.015% | -12.66% | -10.33% | -24.39%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES | YES
Annual Cooling (MWh)
BESTEST Minimum | 0 | 0 | 0 | 0.011 | 0.422 | 3.967 | 0.055 | 1.052
BESTEST Maximum | 0.016 | 0.061 | 0.084 | 0.189 | 1.106 | 5.204 | 0.325 | 1.711
BESTEST Average | 0.0077782 | 0.033054 | 0.051019 | 0.12708 | 0.71399 | 4.4841 | 0.22585 | 1.4485
E-Plus | 0.0004051 | 0.0058483 | 0.016246 | 0.067711 | 0.64648 | 4.2466 | 0.20334 | 1.2051
Difference, % | -94.79% | -82.31% | -68.16% | -46.72% | -9.455% | -5.298% | -9.965% | -16.8%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES | YES
Peak Heating (KW)
BESTEST Minimum | 2.062 | 2.867 | 3.625 | 3.443 | 3.442 | 3.439 | 3.227 | 2.979
BESTEST Maximum | 2.385 | 3.695 | 4.487 | 4.287 | 4.287 | 4.376 | 4.138 | 3.963
BESTEST Average | 2.2549 | 3.3306 | 4.1252 | 3.9407 | 3.9417 | 3.9929 | 3.7755 | 3.6057
E-Plus | 2.2319 | 3.2431 | 4.1533 | 3.9697 | 3.9697 | 3.751 | 3.7864 | 3.3211
Difference, % | -1.02% | -2.628% | 0.6818% | 0.7377% | 0.7108% | -6.059% | 0.2889% | -7.893%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES | YES
Peak Cooling (KW)
BESTEST Minimum | 0 | 0 | 0.035 | 0.258 | 1.427 | 4.424 | 0.685 | 1.852
BESTEST Maximum | 0.394 | 0.666 | 0.814 | 1.047 | 2.578 | 5.278 | 1.358 | 2.991
BESTEST Average | 0.25317 | 0.47045 | 0.59547 | 0.81631 | 1.8403 | 4.7354 | 1.0617 | 2.4811
E-Plus | 0.072268 | 0.25542 | 0.39737 | 0.63265 | 1.7294 | 4.7185 | 0.84606 | 2.1114
Difference, % | -71.45% | -45.71% | -33.27% | -22.5% | -6.027% | -0.3559% | -20.31% | -14.9%
EnergyPlus Within Range | YES | YES | YES | YES | YES | YES | YES | YES

## YD
[5 empty] | Program Name and Version (with full build detail): |  | Paste new data in row 61 and below.
[5 empty] | EnergyPlus {{ engine.config["EnergyPlusVersion"] }} |  | Cells in blue are used in titles and labels
STANDARD 140 OUTPUT FORM - RESULTS |  |  |  | Sec5-2out.XLS | Program Version Release Date: | {{ engine.day_month_year() }} | Editing them here flows thru to other tabs
[5 empty] | Program Name for Tables and Charts: | E+{{ engine.config["EnergyPlusVersion"] }} | To print pdf file, see instructions on "Title Page" tab.
Results Submission Date:
INSTRUCTIONS: |  |  |  |  | Modeler Organization for Titles (long):
GARD Analytics, Inc.
1) Use specified units. |  |  |  |  | Modeler Organization for Tables and Charts (short): | GARD
2) All radiation data is for sum of direct and diffuse solar radiation.
3) Format dates using the appropriate two-digit date followed by a three-digit
month code and two-digit hour code (24 hour clock), as shown below.
MONTH |  | CODE
January |  | Jan
February |  | Feb
March |  | Mar
April |  | Apr
May |  | May
June |  | Jun
July |  | Jul
August |  | Aug
September |  | Sep
October |  | Oct
November |  | Nov
December |  | Dec
For example, a peak occuring on Jan 4 during the 15th hour interval (2-3 PM),
should be input as:
DATE HOUR
04-Jan 15
4) Data entry is restricted to Column B or Columns B,C,D. Enter appropriate
output in the proper column(s) for the case or hour listed in column A. This
worksheet extends down to Row 901. Note that the protection option has been
used in this worksheet to help assure that data is input to the correct cells.
GARD
E+{{ engine.config["EnergyPlusVersion"] }}-GARD
ANNUAL HEATING LOADS (COLUMN B)
PROGRAM:
VERSION:
CASE# | MWh
600 | 4.3784
610 | 4.4215
620 | 4.5502
630 | 4.8814
640 | 2.6843
650 | 0
900 | 1.2237
910 | 1.5058
920 | 3.1931
930 | 3.9062
940 | 0.7681
950 | 0
960 | 2.4083
195 | 4.3574
200 | 5.5781
210 | 6.5979
215 | 5.9525
220 | 7.1101
230 | 10.8983
240 | 5.8679
250 | 5.1891
270 | 4.4525
280 | 4.6506
290 | 4.4878
300 | 4.4977
310 | 4.7764
320 | 3.7598
395 | 4.9804
400 | 7.0226
410 | 8.9092
420 | 7.6519
430 | 6.0287
440 | 4.5686
800 | 5.3705
810 | 1.9716
ANNUAL COOLING LOADS (COLUMN B)
PROGRAM:
VERSION:
CASE# | MWh
600 | 6.7404
610 | 4.7464
620 | 4.1676
630 | 2.7804
640 | 6.4538
650 | 5.3044
900 | 2.5077
910 | 1.2348
920 | 2.5485
930 | 1.6378
940 | 2.4333
950 | 0.5298
960 | 0.63954
195 | 0.41216
200 | 0.58684
210 | 0.36522
215 | 0.64348
220 | 0.40663
230 | 0.69576
240 | 0.70436
250 | 3.1632
270 | 8.4894
280 | 5.4978
290 | 6.3928
300 | 5.4661
310 | 3.7381
320 | 5.8058
395 | 0.0004051
400 | 0.0058483
410 | 0.016246
420 | 0.067711
430 | 0.64648
440 | 4.2466
800 | 0.20334
810 | 1.2051
ANNUAL HOURLY INTEGRATED PEAK HEATING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | 3.7501
610 | 3.7396
620 | 3.7409
630 | 3.7206
640 | 6.2768
650 | 0
900 | 3.1722
910 | 3.1718
920 | 3.483
930 | 3.5065
940 | 4.8155
950 | 0
960 | 2.6926
195 | 2.0902
200 | 2.852
210 | 3.0403
215 | 3.031
220 | 3.2431
230 | 5.0636
240 | 3.0595
250 | 3.243
270 | 3.0235
280 | 3.0238
290 | 3.013
300 | 3.0137
310 | 2.9934
320 | 3.0227
395 | 2.2319
400 | 3.2431
410 | 4.1533
420 | 3.9697
430 | 3.9697
440 | 3.751
800 | 3.7864
810 | 3.3211
ANNUAL HOURLY INTEGRATED PEAK COOLING LOADS (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | kW | DATE | TIME
600 | 6.5655
610 | 6.1645
620 | 3.9206
630 | 3.3761
640 | 6.5012
650 | 6.3727
900 | 3.2497
910 | 2.5734
920 | 2.7772
930 | 2.2746
940 | 3.2497
950 | 2.3878
960 | 1.1435
195 | 0.72935
200 | 0.97395
210 | 0.81136
215 | 1.0732
220 | 0.90992
230 | 1.4066
240 | 1.0926
250 | 3.0465
270 | 6.8353
280 | 4.7126
290 | 6.7084
300 | 3.8985
310 | 3.263
320 | 6.1572
395 | 0.072268
400 | 0.25542
410 | 0.39737
420 | 0.63265
430 | 1.7294
440 | 4.7185
800 | 0.84606
810 | 2.1114
FREE-FLOAT CASE TEMPERATURE OUTPUT
MAX ANNUAL HOURLY ZONE TEMP (COLUMNS B,C,D)
PROGRAM:
VERSION:
CASE# | TEMP (C) | DATE | TIME
600FF | 65.2873
900FF | 43.1596
650FF | 63.5022
950FF | 36.6437
960 | 52.3815
MIN ANNUAL HOURLY ZONE TEMP
PROGRAM:
VERSION:
CASE# | TEMP (C) | DATE | TIME
600FF | -17.418
900FF | -2.603
650FF | -23.0438
950FF | -20.3396
960 | 2.2205
AVG ANNUAL HOURLY ZONE TEMP (COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | TEMP (C)
600FF | 25.8
900FF | 25.9988
650FF | 18.6399
950FF | 14.4962
960 | 29.1286
SOLAR RADIATION
ANNUAL INCIDENT TOTAL
CASE 600
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
SURFACE | kWh/m2
= | = | = | =
600NORTH | 432.5714
600EAST | 1185.8901
600WEST | 1040.7444
600SOUTH | 1547.5075
600HORZ. | 1840.9315
= | = | = | =
SOLAR RADIATION
UNSHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | kWh/m2
= | = | = | =
920WEST | 674.4647
900SOUTH | 981.7119
= | = | = | =
SOLAR RADIATION
SHADED ANNUAL TRANSMITTED
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
CASE# | kWh/m2
= | = | = | =
930WEST | 487.6021
910SOUTH | 788.0422
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 4.1392
8 | 19.9066
9 | 35.4789
10 | 48.9837
11 | 58.4496
12 | 63.7276
13 | 63.4692
14 | 57.1639
15 | 46.1404
16 | 31.7261
17 | 15.6423
18 | 2.6702
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION CLOUDY DAY, MARCH 5
CASE 600 OR 900
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 0
6 | 0
7 | 4.1007
8 | 19.5371
9 | 34.5799
10 | 47.8212
11 | 56.9729
12 | 61.3277
13 | 61.4275
14 | 56.2762
15 | 46.1267
16 | 32.2501
17 | 16.1236
18 | 2.7155
19 | 0
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
SOUTH SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 2.8637
6 | 35.6572
7 | 90.2926
8 | 136.1384
9 | 256.058
10 | 377.0924
11 | 449.9555
12 | 468.97
13 | 458.4652
14 | 395.7752
15 | 298.2775
16 | 170.2592
17 | 80.3704
18 | 52.387
19 | 15.1854
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY INCIDENT SOLAR RADIATION, CLEAR DAY, JULY 27
CASE 600
WEST SURFACE
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | Wh/m2
= | = | = | =
1 | 0
2 | 0
3 | 0
4 | 0
5 | 2.8637
6 | 35.6572
7 | 90.2926
8 | 128.8229
9 | 146.3844
10 | 152.7179
11 | 149.8255
12 | 142.658
13 | 257.4
14 | 457.0081
15 | 616.3625
16 | 668.525
17 | 511.0446
18 | 163.2193
19 | 26.8902
20 | 0
21 | 0
22 | 0
23 | 0
24 | 0
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 600FF JAN 4
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | -10.4846
2 | -12.1343
3 | -13.5528
4 | -14.6804
5 | -15.6453
6 | -16.4595
7 | -17.1686
8 | -17.418
9 | -14.4597
10 | -8.0321
11 | 1.5574
12 | 12.3277
13 | 21.2967
14 | 28.2262
15 | 32.2221
16 | 32.627
17 | 28.1819
18 | 21.6323
19 | 15.857
20 | 11.3137
21 | 7.0109
22 | 3.5465
23 | 0.59123
24 | -1.7283
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 900FF JAN 4
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | 0.71166
2 | 0.052724
3 | -0.4729
4 | -0.94975
5 | -1.4586
6 | -1.929
7 | -2.389
8 | -2.603
9 | -1.5848
10 | 0.15759
11 | 3.0251
12 | 5.528
13 | 7.5726
14 | 9.2421
15 | 10.095
16 | 9.8725
17 | 8.3859
18 | 6.8869
19 | 5.897
20 | 5.1978
21 | 4.5145
22 | 3.8903
23 | 3.3942
24 | 2.9061
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 650FF JULY 27
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | 22.8183
2 | 21.3169
3 | 20.3571
4 | 19.5387
5 | 19.0153
6 | 19.3354
7 | 21.4065
8 | 23.8144
9 | 26.7272
10 | 31.0818
11 | 35.198
12 | 39.8578
13 | 43.9276
14 | 46.959
15 | 48.5261
16 | 48.6524
17 | 47.9397
18 | 46.5413
19 | 35.2276
20 | 31.7347
21 | 29.3177
22 | 27.1863
23 | 25.7811
24 | 24.4755
= | = | = | =
HOURLY FREE FLOAT TEMPERATURE DATA
CASE 950FF JULY 27
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
HOUR | TEMP (C)
= | = | = | =
1 | 24.5692
2 | 23.6558
3 | 23.0439
4 | 22.4318
5 | 22.0046
6 | 22.1663
7 | 23.565
8 | 26.7606
9 | 28.5627
10 | 30.0278
11 | 31.2248
12 | 32.3518
13 | 33.3647
14 | 34.0217
15 | 34.3607
16 | 34.4016
17 | 34.3683
18 | 34.0851
19 | 30.5314
20 | 29.4024
21 | 28.5659
22 | 27.5241
23 | 26.8808
24 | 26.0838
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 600 JAN 4
[USE (-) FOR COOLING]
PROGRAM:
VERSION:
HOUR | kWh
= | = | = | =
1 | 3.5719
2 | 3.6913
3 | 3.7294
4 | 3.7384
5 | 3.7501
6 | 3.7462
7 | 3.746
8 | 3.4484
9 | 2.0653
10 | 0.58527
11 | -0.074905
12 | -1.9603
13 | -3.3406
14 | -3.6097
15 | -2.9619
16 | -1.461
17 | -0.013571
18 | 0.43971
19 | 1.8393
20 | 2.5741
21 | 2.9775
22 | 3.1878
23 | 3.2456
24 | 3.2633
= | = | = | =
HOURLY HEATING & COOLING LOAD DATA (COLUMN B ONLY)
CASE 900 JAN 4
[USE (-) FOR COOLING]
PROGRAM:
VERSION:
HOUR | kWh
= | = | = | =
1 | -2.6843
2 | -2.828
3 | -2.9028
4 | -2.9806
5 | -3.0585
6 | -3.1147
7 | -3.1722
8 | -3.0553
9 | -2.4398
10 | -1.7752
11 | -0.99332
12 | -0.27794
13 | 0
14 | 0
15 | 0
16 | 0
17 | -0.1303
18 | -0.63116
19 | -0.98785
20 | -1.231
21 | -1.4595
22 | -1.643
23 | -1.7552
24 | -1.8497
= | = | = | =
FREE-FLOAT CASES
HOURLY ANNUAL ZONE TEMPERATURE BIN DATA
CASE 900FF
(USE COLUMN B ONLY)
PROGRAM:
VERSION:
TEMP (C) | # HOURS
= | = | = | =
-50 | 0
-49 | 0
-48 | 0
-47 | 0
-46 | 0
-45 | 0
-44 | 0
-43 | 0
-42 | 0
-41 | 0
-40 | 0
-39 | 0
-38 | 0
-37 | 0
-36 | 0
-35 | 0
-34 | 0
-33 | 0
-32 | 0
-31 | 0
-30 | 0
-29 | 0
-28 | 0
-27 | 0
-26 | 0
-25 | 0
-24 | 0
-23 | 0
-22 | 0
-21 | 0
-20 | 0
-19 | 0
-18 | 0
-17 | 0
-16 | 0
-15 | 0
-14 | 0
-13 | 0
-12 | 0
-11 | 0
-10 | 0
-9 | 0
-8 | 0
-7 | 0
-6 | 0
-5 | 0
-4 | 0
-3 | 2
-2 | 5
-1 | 5
0 | 8
1 | 15
2 | 14
3 | 18
4 | 16
5 | 20
6 | 24
7 | 30
8 | 30
9 | 46
10 | 53
11 | 61
12 | 99
13 | 119
14 | 142
15 | 162
16 | 185
17 | 232
18 | 269
19 | 320
20 | 333
21 | 370
22 | 383
23 | 396
24 | 368
25 | 417
26 | 402
27 | 472
28 | 436
29 | 438
30 | 451
31 | 403
32 | 358
33 | 337
34 | 320
35 | 246
36 | 198
37 | 189
38 | 132
39 | 107
40 | 71
41 | 40
42 | 15
43 | 3
44 | 0
45 | 0
46 | 0
47 | 0
48 | 0
49 | 0
50 | 0
51 | 0
52 | 0
53 | 0
54 | 0
55 | 0
56 | 0
57 | 0
58 | 0
59 | 0
60 | 0
61 | 0
62 | 0
63 | 0
64 | 0
65 | 0
66 | 0
67 | 0
68 | 0
69 | 0
70 | 0
71 | 0
72 | 0
73 | 0
74 | 0
75 | 0
76 | 0
77 | 0
78 | 0
79 | 0
80 | 0
81 | 0
82 | 0
83 | 0
84 | 0
85 | 0
86 | 0
87 | 0
88 | 0
89 | 0
90 | 0
91 | 0
92 | 0
93 | 0
94 | 0
95 | 0
96 | 0
97 | 0
98 | 0
= | = | = | =
= | = | = | =
= | = | = | =
= | = | = | =