## MaxDiffSummary
EnergyPlus vs Average of Analytical Results
Max. Absolute % Difference
Space Cooling Electricity Consumption | 1.585%
Indoor Fan Electricity Consumption | 1.204%
DX Coil Electricity Consumption | 1.591%
Coefficient of Performance | 0.6777%
Total Cooling Coil Load | 1.516%
Sensible Cooling Coil Load | 1.982%
Latent Cooling Coil Load | 0.0274%
Zone Total Cooling Load | 1.547%
Zone Sensible Cooling Load | 1.547%
Zone Latent Cooling Load | 0.0021%
Mean Indoor Dry-bulb Temperature | 0.2013%
Mean Indoor Humidity Ratio | 2.9%

## Electricity Data
IEA HVAC BESTEST
Results taken from File i221000a.WK3, Sheet Q, Cells A6:Q75
EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 1531 | 1432 | 1520.817 | 1519 | 1583.7 | 1522.2661 | 1511.9369 | 1432 | 1583.7 | 1517.2457 | 9.998% | 1530.548 | 1530.8 | 1530.6 | 1520.1842 | 1530.6493 | 0.6837%
CE110 | 1077 | 1182 | 1061.196 | 1065 | 1129.5 | 1066.9607 | 1061.9658 | 1061.196 | 1182 | 1091.9461 | 11.06% | 1076.2349 | 1077.2 | 1077.4 | 1069.3313 | 1076.945 | 0.707%
CE120 | 1012 | 1021 | 1011.104 | 1003 | 988.2 | 1007.3023 | 1001.6637 | 988.2 | 1021 | 1006.3243 | 3.259% | 1012.6774 | 1011 | 1011 | 1006.6379 | 1011.5591 | 0.4865%
CE130 | 110 | 101 | 105.419 | 106 | 113.7 | 108.7246 | 110.1161 | 101 | 113.7 | 107.8514 | 11.78% | 110.5818 | 109.5 | 109.5 | 108.1197 | 109.8606 | 1.585%
CE140 | 68 | 70 | 65.008 | 66 | 71.7 | 67.7641 | 68.6428 | 65.008 | 71.7 | 68.1593 | 9.818% | 68.9953 | 68.5 | 68.3 | 67.7696 | 68.5984 | 1.208%
CE150 | 1208 | 1220 | 1202.424 | 1183 | 1215.4 | 1199.055 | 1191.613 | 1183 | 1220 | 1202.7846 | 3.076% | 1206.49 | 1206.5 | 1206.5 | 1197.6199 | 1206.4967 | 0.7357%
CE160 | 1140 | 1151 | 1137.63 | 1107 | 1157.9 | 1136.7334 | 1132.8835 | 1107 | 1157.9 | 1137.5924 | 4.474% | 1140.44 | 1139.3 | 1138.9 | 1132.2318 | 1139.5467 | 0.6419%
CE165 | 1502 | 1519 | 1499.447 | 1470 | 1493.1 | 1499.7105 | 1489.9268 | 1470 | 1519 | 1496.1692 | 3.275% | 1497.8302 | 1499.7 | 1499.6 | 1491.5878 | 1499.0434 | 0.4974%
CE170 | 638 | 646 | 629.076 | 620 | 616.4 | 635.909 | 635.8287 | 616.4 | 646 | 631.602 | 4.686% | 641.1173 | 637.7 | 637.8 | 635.4994 | 638.8724 | 0.528%
CE180 | 1083 | 1093 | 1077.109 | 1080 | 1030.6 | 1081.2706 | 1080.0377 | 1030.6 | 1093 | 1075.0025 | 5.805% | 1082.666 | 1082.3 | 1081.9 | 1082.3259 | 1082.2887 | 0.003438%
CE185 | 1544 | 1563 | 1541.155 | 1547 | 1532.9 | 1541.5256 | 1538.3972 | 1532.9 | 1563 | 1543.9968 | 1.949% | 1544.6397 | 1543.4 | 1542.9 | 1540.5373 | 1543.6466 | 0.2014%
CE190 | 164 | 166 | 160.219 | 160 | 155.1 | 163.9975 | 165.1202 | 155.1 | 166 | 162.0624 | 6.726% | 165.173 | 164.1 | 164.2 | 164.1636 | 164.491 | 0.199%
CE195 | 250 | 254 | 244.919 | 246 | 244.5 | 249.7321 | 251.5799 | 244.5 | 254 | 248.6759 | 3.82% | 252.1605 | 250 | 250 | 249.7096 | 250.7202 | 0.4031%
CE200 | 1477 | 1478 | 1468.214 | 1440 | 1487.4 | 1479.9926 | 1479.9926 | 1440 | 1487.4 | 1472.9428 | 3.218% | 1475.8104 | 1477.4 | 1477.1 | 1465.3737 | 1476.7701 | 0.7717%
Energy Consumption, Compressor (kWh,e) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.585%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
CE100 | 1319 | 1233 | 1307.458 | 1311 | 1363 | 1311.1661 | 1302.7258 | 1233 | 1363 | 1306.7643 | 9.948% | 1318.8515 | 1319 | 1318.9
CE110 | 889 | 978 | 865.866 | 883 | 932.3 | 879.3187 | 875.8322 | 865.866 | 978 | 900.4738 | 12.45% | 887.9378 | 889.2 | 889.4
CE120 | 840 | 846 | 850.068 | 838 | 819.4 | 835.847 | 831.9292 | 819.4 | 850.068 | 837.3206 | 3.663% | 840.8662 | 839.1 | 839.2
CE130 | 95 | 87 | 93.198 | 93 | 97.9 | 93.6472 | 94.8489 | 87 | 97.9 | 93.5134 | 11.66% | 95.2867 | 94.4 | 94.3
CE140 | 57 | 58 | 54.799 | 56 | 59.2 | 55.8468 | 56.5735 | 54.799 | 59.2 | 56.7742 | 7.752% | 56.924 | 56.5 | 56.4
CE150 | 1000 | 1010 | 1007.094 | 982 | 1006.8 | 992.0333 | 986.7503 | 982 | 1010 | 997.8111 | 2.806% | 998.9576 | 999.2 | 999.2
CE160 | 950 | 959 | 962.675 | 926 | 965.2 | 946.9958 | 944.3585 | 926 | 965.2 | 950.6042 | 4.124% | 950.4111 | 949.4 | 949.1
CE165 | 1283 | 1297 | 1291.242 | 1256 | 1274.7 | 1280.2205 | 1272.4664 | 1256 | 1297 | 1279.2327 | 3.205% | 1278.7205 | 1280.2 | 1280.2
CE170 | 531 | 537 | 538.959 | 523 | 512.6 | 528.3976 | 528.5837 | 512.6 | 538.959 | 528.5058 | 4.987% | 532.9693 | 530 | 530.1
CE180 | 909 | 917 | 914.262 | 912 | 864.1 | 907.1462 | 906.4398 | 864.1 | 917 | 904.2783 | 5.85% | 908.1216 | 908 | 907.7
CE185 | 1340 | 1356 | 1342.681 | 1344 | 1330.5 | 1336.897 | 1334.3908 | 1330.5 | 1356 | 1340.6384 | 1.902% | 1339.7996 | 1338.6 | 1338.2
CE190 | 138 | 139 | 139.423 | 138 | 130 | 137.5107 | 138.4572 | 130 | 139.423 | 137.1987 | 6.868% | 138.4708 | 137.6 | 137.7
CE195 | 217 | 220 | 218.867 | 217 | 212.1 | 216.4828 | 218.0909 | 212.1 | 220 | 217.0772 | 3.639% | 218.6235 | 216.8 | 216.8
CE200 | 1250 | 1250 | 1249.027 | 1218 | 1259.7 | 1252.8566 | 1252.8566 | 1218 | 1259.7 | 1247.4915 | 3.343% | 1248.8198 | 1250.2 | 1250
Energy Consumption, Supply Fan (kWh,e) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 144 | 136 | 145.185 | 141 | 150.2 | 143.6481 | 142.3625 | 136 | 150.2 | 143.1994 | 9.916% | 144.0538 | 144.1 | 144 | 143.5848 | 144.0513 | 0.3239%
CE110 | 128 | 139 | 132.917 | 122 | 134.3 | 127.6854 | 126.659 | 122 | 139 | 130.0802 | 13.07% | 128.1312 | 127.9 | 127.9 | 127.5927 | 127.9771 | 0.3003%
CE120 | 117 | 119 | 109.581 | 110 | 114.9 | 116.6706 | 115.4998 | 109.581 | 119 | 114.6645 | 8.214% | 116.9129 | 116.9 | 116.9 | 116.438 | 116.9043 | 0.3989%
CE130 | 10 | 10 | 8.316 | 8 | 10.8 | 10.2598 | 10.3889 | 8 | 10.8 | 9.6807 | 28.92% | 10.4079 | 10.3 | 10.3 | 10.2115 | 10.336 | 1.204%
CE140 | 8 | 8 | 6.947 | 6 | 8.5 | 8.1094 | 8.2128 | 6 | 8.5 | 7.6813 | 32.55% | 8.2142 | 8.1 | 8.1 | 8.0856 | 8.1381 | 0.6452%
CE150 | 141 | 143 | 132.917 | 136 | 142 | 140.8727 | 139.4036 | 132.917 | 143 | 139.3133 | 7.238% | 141.2203 | 141.1 | 141.1 | 140.3497 | 141.1401 | 0.56%
CE160 | 129 | 131 | 119.052 | 121 | 131.2 | 129.1114 | 128.2863 | 119.052 | 131.2 | 126.9499 | 9.569% | 129.3096 | 129.2 | 129.2 | 128.3806 | 129.2365 | 0.6623%
CE165 | 149 | 151 | 141.678 | 145 | 148.6 | 149.3574 | 147.976 | 141.678 | 151 | 147.5159 | 6.319% | 149.0983 | 149.3 | 149.3 | 148.616 | 149.2328 | 0.4133%
CE170 | 73 | 74 | 61.322 | 63 | 70.7 | 73.1586 | 72.9774 | 61.322 | 74 | 69.7369 | 18.18% | 73.5918 | 73.2 | 73.2 | 73.0391 | 73.3306 | 0.3975%
CE180 | 118 | 120 | 110.813 | 112 | 113.4 | 118.487 | 118.1287 | 110.813 | 120 | 115.8327 | 7.931% | 118.7728 | 118.6 | 118.5 | 118.4636 | 118.6243 | 0.1354%
CE185 | 139 | 141 | 135.056 | 137 | 137.8 | 139.2444 | 138.821 | 135.056 | 141 | 138.2745 | 4.299% | 139.3882 | 139.4 | 139.3 | 139.139 | 139.3627 | 0.1605%
CE190 | 18 | 18 | 14.151 | 14 | 17.1 | 18.0236 | 18.1435 | 14 | 18.1435 | 16.774 | 24.7% | 18.1701 | 18 | 18 | 18.0123 | 18.0567 | 0.2458%
CE195 | 23 | 23 | 17.728 | 18 | 22 | 22.6253 | 22.7884 | 17.728 | 23 | 21.306 | 24.74% | 22.821 | 22.6 | 22.6 | 22.6112 | 22.6737 | 0.2755%
CE200 | 154 | 155 | 149.151 | 151 | 155.1 | 154.56 | 154.56 | 149.151 | 155.1 | 153.3387 | 3.88% | 154.4611 | 154.6 | 154.6 | 153.4905 | 154.5537 | 0.6879%
Energy Consumption, Condenser Fan (kWh,e) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.204%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
CE100 | 68 | 64 | 68.174 | 67 | 70.4 | 67.452 | 66.8486 | 64 | 70.4 | 67.4107 | 9.494% | 67.6427 | 67.6 | 67.6
CE110 | 60 | 65 | 62.413 | 60 | 63 | 59.9566 | 59.4747 | 59.4747 | 65 | 61.4063 | 8.998% | 60.166 | 60.1 | 60.1
CE120 | 55 | 56 | 51.455 | 55 | 53.9 | 54.7846 | 54.2347 | 51.455 | 56 | 54.3392 | 8.364% | 54.8982 | 54.9 | 54.9
CE130 | 5 | 5 | 3.905 | 5 | 5.1 | 4.8176 | 4.8783 | 3.905 | 5.1 | 4.8144 | 24.82% | 4.8872 | 4.8 | 4.8
CE140 | 4 | 4 | 3.262 | 4 | 4 | 3.8079 | 3.8565 | 3.262 | 4 | 3.8466 | 19.19% | 3.8571 | 3.8 | 3.8
CE150 | 66 | 67 | 62.413 | 65 | 66.6 | 66.1491 | 65.4591 | 62.413 | 67 | 65.5173 | 7.001% | 66.3121 | 66.3 | 66.2
CE160 | 61 | 61 | 55.903 | 60 | 61.5 | 60.6262 | 60.2388 | 55.903 | 61.5 | 60.0383 | 9.322% | 60.7193 | 60.7 | 60.7
CE165 | 70 | 71 | 66.527 | 69 | 69.7 | 70.1326 | 69.4843 | 66.527 | 71 | 69.4063 | 6.445% | 70.0114 | 70.1 | 70.1
CE170 | 34 | 35 | 28.795 | 34 | 33.1 | 34.3527 | 34.2676 | 28.795 | 35 | 33.3593 | 18.6% | 34.5562 | 34.4 | 34.4
CE180 | 56 | 56 | 52.034 | 56 | 53.2 | 55.6374 | 55.4691 | 52.034 | 56 | 54.9058 | 7.223% | 55.7716 | 55.7 | 55.7
CE185 | 65 | 66 | 63.418 | 66 | 64.6 | 65.3842 | 65.1855 | 63.418 | 66 | 65.084 | 3.967% | 65.4519 | 65.4 | 65.4
CE190 | 8 | 8 | 6.645 | 8 | 8 | 8.4632 | 8.5195 | 6.645 | 8.5195 | 7.9468 | 23.59% | 8.5321 | 8.5 | 8.5
CE195 | 11 | 11 | 8.324 | 11 | 10.3 | 10.6241 | 10.7006 | 8.324 | 11 | 10.4212 | 25.68% | 10.716 | 10.6 | 10.6
CE200 | 73 | 73 | 70.036 | 71 | 72.7 | 72.576 | 72.576 | 70.036 | 73 | 72.1269 | 4.109% | 72.5296 | 72.6 | 72.6
i221000a.wk3 q:a06..o75; 10/25/00
Data below added by RHH to allow comparison with E-Plus results which do not allow breakout of compressor and OD fan electricity consumption
Energy Consumption, Compressor + Condenser Fan (kWh,e) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 1387 | 1297 | 1375.632 | 1378 | 1433.4 | 1378.6181 | 1369.5744 | 1297 | 1433.4 | 1374.1749 | 9.926% | 1386.4942 | 1386.6 | 1386.5 | 1376.5994 | 1386.5314 | 0.7163%
CE110 | 949 | 1043 | 928.279 | 943 | 995.3 | 939.2753 | 935.3068 | 928.279 | 1043 | 961.8802 | 11.93% | 948.1037 | 949.3 | 949.5 | 941.7386 | 948.9679 | 0.7618%
CE120 | 895 | 902 | 901.523 | 893 | 873.3 | 890.6316 | 886.1639 | 873.3 | 902 | 891.6598 | 3.219% | 895.7645 | 894 | 894.1 | 890.2 | 894.6215 | 0.4942%
CE130 | 100 | 92 | 97.103 | 98 | 103 | 98.4649 | 99.7272 | 92 | 103 | 98.3279 | 11.19% | 100.1739 | 99.2 | 99.1 | 97.9082 | 99.4913 | 1.591%
CE140 | 61 | 62 | 58.061 | 60 | 63.2 | 59.6547 | 60.43 | 58.061 | 63.2 | 60.6208 | 8.477% | 60.7811 | 60.3 | 60.2 | 59.684 | 60.427 | 1.23%
CE150 | 1066 | 1077 | 1069.507 | 1047 | 1073.4 | 1058.1823 | 1052.2094 | 1047 | 1077 | 1063.3284 | 2.821% | 1065.2697 | 1065.5 | 1065.4 | 1057.2702 | 1065.3899 | 0.7621%
CE160 | 1011 | 1020 | 1018.578 | 986 | 1026.7 | 1007.6221 | 1004.5972 | 986 | 1026.7 | 1010.6425 | 4.027% | 1011.1304 | 1010.1 | 1009.8 | 1003.8512 | 1010.3435 | 0.6426%
CE165 | 1353 | 1368 | 1357.769 | 1325 | 1344.4 | 1350.3531 | 1341.9508 | 1325 | 1368 | 1348.639 | 3.188% | 1348.7318 | 1350.3 | 1350.3 | 1342.9718 | 1349.7773 | 0.5042%
CE170 | 565 | 572 | 567.754 | 557 | 545.7 | 562.7503 | 562.8513 | 545.7 | 572 | 561.8651 | 4.681% | 567.5255 | 564.4 | 564.5 | 562.4603 | 565.4752 | 0.5332%
CE180 | 965 | 973 | 966.296 | 968 | 917.3 | 962.7836 | 961.909 | 917.3 | 973 | 959.1841 | 5.807% | 963.8932 | 963.7 | 963.4 | 963.8623 | 963.6644 | 0.02053%
CE185 | 1405 | 1422 | 1406.099 | 1410 | 1395.1 | 1402.2811 | 1399.5763 | 1395.1 | 1422 | 1405.7223 | 1.914% | 1405.2514 | 1404 | 1403.6 | 1401.3983 | 1404.2838 | 0.2055%
CE190 | 146 | 147 | 146.068 | 146 | 138 | 145.9739 | 146.9768 | 138 | 147 | 145.1455 | 6.201% | 147.0029 | 146.1 | 146.2 | 146.1513 | 146.4343 | 0.1933%
CE195 | 228 | 231 | 227.191 | 228 | 222.4 | 227.1068 | 228.7915 | 222.4 | 231 | 227.4985 | 3.78% | 229.3395 | 227.4 | 227.4 | 227.0984 | 228.0465 | 0.4157%
CE200 | 1323 | 1323 | 1319.063 | 1289 | 1332.4 | 1325.4326 | 1325.4326 | 1289 | 1332.4 | 1319.6183 | 3.289% | 1321.3493 | 1322.8 | 1322.6 | 1311.8832 | 1322.2498 | 0.784%
[16 empty] | Max | 1.591%

## COP Data
IEA HVAC BESTEST
Results taken from File i221000a.WK3, Sheet Q, Cells A185:Q220
From CSV Files
COP: Mean, and (Max-Mean)/Mean
Mean COP | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [10 empty] | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total |  | Total | Total
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  | COP Mean | COP Min | COP Max |  | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP | Load | Power | COP
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Date/Time | E100 | E100 | E100 | E110 | E110 | E110 | E120 | E120 | E120 | E130 | E130 | E130 | E140 | E140 | E140 | E150 | E150 | E150 | E160 | E160 | E160 | E165 | E165 | E165 | E170 | E170 | E170 | E180 | E180 | E180 | E185 | E185 | E185 | E190 | E190 | E190 | E195 | E195 | E195 | E200 | E200 | E200
CE100 | 2.39 | 2.55 | 2.4304 | 2.4064 | 2.31 | 2.4017 | 2.4184 | 2.31 | 2.55 | 2.4153 | 9.937% | 2.3889 | 2.39 | 2.39 | 2.4031 | 2.3974 | 2.4051 | 02/01 01:00:00 | 5.4347 | 2.2609 | 2.4038 | 5.4071 | 1.5901 | 3.4004 | 5.3998 | 1.497 | 3.6071 | 0.30467 | 0.16004 | 1.9038 | 0.27706 | 0.099979 | 2.7712 | 6.5071 | 1.781 | 3.6535 | 6.4999 | 1.684 | 3.8598 | 6.5237 | 2.2183 | 2.9409 | 3.2071 | 0.94462 | 3.3951 | 6.5071 | 1.6094 | 4.0431 | 6.5347 | 2.2908 | 2.8526 | 0.82707 | 0.24335 | 3.3987 | 0.85468 | 0.3706 | 2.3062 | 7.9458 | 2.1795 | 3.6457
CE110 | 3.38 | 3.08 | 3.4589 | 3.4146 | 3.22 | 3.4087 | 3.4271 | 3.08 | 3.4589 | 3.3413 | 11.34% | 3.3795 | 3.38 | 3.38 | 3.3994 | 3.3935 | 3.4022 | 02/01 02:00:00 | 5.4349 | 2.2608 | 2.404 | 5.4072 | 1.5901 | 3.4006 | 5.3998 | 1.4969 | 3.6073 | 0.30489 | 0.16014 | 1.904 | 0.2772 | 0.10002 | 2.7715 | 6.5072 | 1.7809 | 3.6539 | 6.4999 | 1.6838 | 3.8602 | 6.5239 | 2.2181 | 2.9412 | 3.2072 | 0.94457 | 3.3955 | 6.5073 | 1.6094 | 4.0433 | 6.5349 | 2.2907 | 2.8528 | 0.82721 | 0.24345 | 3.3979 | 0.8549 | 0.37078 | 2.3057 | 7.9459 | 2.1793 | 3.6461
CE120 | 3.59 | 3.56 | 3.6139 | 3.623 | 3.68 | 3.6054 | 3.6313 | 3.56 | 3.68 | 3.6148 | 3.32% | 3.5865 | 3.59 | 3.59 | 3.606 | 3.5998 | 3.609 | 02/01 03:00:00 | 5.4349 | 2.261 | 2.4037 | 5.4072 | 1.5902 | 3.4002 | 5.3998 | 1.4971 | 3.6069 | 0.30491 | 0.16017 | 1.9037 | 0.27722 | 0.10004 | 2.7711 | 6.5073 | 1.781 | 3.6537 | 6.4999 | 1.6839 | 3.8601 | 6.5239 | 2.2182 | 2.941 | 3.2073 | 0.94462 | 3.3953 | 6.5073 | 1.6096 | 4.0429 | 6.535 | 2.291 | 2.8524 | 0.82723 | 0.24347 | 3.3977 | 0.85491 | 0.37076 | 2.3058 | 7.9459 | 2.1794 | 3.646
CE130 | 1.91 | 2.07 | 1.9752 | 1.953 | 1.84 | 1.9198 | 1.9163 | 1.84 | 2.07 | 1.9406 | 11.85% | 1.8895 | 1.91 | 1.91 | 1.903 | 1.897 | 1.9053 | 02/01 04:00:00 | 5.4351 | 2.2613 | 2.4036 | 5.4073 | 1.5904 | 3.4 | 5.3998 | 1.4972 | 3.6067 | 0.30511 | 0.16029 | 1.9035 | 0.27734 | 0.10009 | 2.7708 | 6.5074 | 1.7812 | 3.6534 | 6.4999 | 1.684 | 3.8598 | 6.5241 | 2.2185 | 2.9408 | 3.2074 | 0.94476 | 3.3949 | 6.5074 | 1.6097 | 4.0426 | 6.5352 | 2.2913 | 2.8522 | 0.82735 | 0.24357 | 3.3967 | 0.85511 | 0.37099 | 2.3049 | 7.9461 | 2.1796 | 3.6457
CE140 | 2.77 | 2.71 | 2.9151 | 2.854 | 2.65 | 2.7974 | 2.7996 | 2.65 | 2.9151 | 2.7852 | 9.518% | 2.7502 | 2.77 | 2.77 | 2.7701 | 2.7637 | 2.7735 | 02/01 05:00:00 | 5.4356 | 2.2617 | 2.4033 | 5.4077 | 1.5907 | 3.3997 | 5.4 | 1.4974 | 3.6063 | 0.30557 | 0.16055 | 1.9032 | 0.27767 | 0.10023 | 2.7704 | 6.5077 | 1.7814 | 3.6532 | 6.5 | 1.6841 | 3.8595 | 6.5245 | 2.2188 | 2.9406 | 3.2077 | 0.94495 | 3.3946 | 6.5077 | 1.6099 | 4.0422 | 6.5356 | 2.2917 | 2.8518 | 0.82768 | 0.2438 | 3.3949 | 0.85558 | 0.37142 | 2.3035 | 7.9464 | 2.1798 | 3.6455
CE150 | 3.62 | 3.59 | 3.6675 | 3.7 | 3.61 | 3.6496 | 3.6734 | 3.59 | 3.7 | 3.6444 | 3.018% | 3.6273 | 3.63 | 3.63 | 3.6525 | 3.6428 | 3.6619 | 02/01 06:00:00 | 5.4359 | 2.2619 | 2.4032 | 5.408 | 1.5908 | 3.3995 | 5.4001 | 1.4975 | 3.606 | 0.30591 | 0.16074 | 1.9031 | 0.27795 | 0.10034 | 2.7702 | 6.508 | 1.7816 | 3.6529 | 6.5002 | 1.6843 | 3.8592 | 6.5249 | 2.2191 | 2.9404 | 3.208 | 0.94512 | 3.3942 | 6.508 | 1.6101 | 4.042 | 6.536 | 2.292 | 2.8516 | 0.82796 | 0.24393 | 3.3943 | 0.85592 | 0.3716 | 2.3033 | 7.9467 | 2.1801 | 3.6452
CE160 | 3.84 | 3.8 | 3.8658 | 3.95 | 3.78 | 3.8452 | 3.8599 | 3.78 | 3.95 | 3.8487 | 4.417% | 3.8329 | 3.84 | 3.84 | 3.8589 | 3.8476 | 3.8696 | 02/01 07:00:00 | 5.436 | 2.2617 | 2.4035 | 5.4081 | 1.5907 | 3.3999 | 5.4002 | 1.4974 | 3.6065 | 0.30605 | 0.16079 | 1.9034 | 0.2781 | 0.10038 | 2.7706 | 6.5081 | 1.7816 | 3.6531 | 6.5003 | 1.6843 | 3.8593 | 6.525 | 2.219 | 2.9405 | 3.2081 | 0.9451 | 3.3945 | 6.5082 | 1.6099 | 4.0425 | 6.5361 | 2.2917 | 2.8521 | 0.82811 | 0.24388 | 3.3955 | 0.85605 | 0.37148 | 2.3044 | 7.9469 | 2.18 | 3.6453
CE165 | 2.92 | 2.89 | 2.9514 | 2.9853 | 2.95 | 2.9257 | 2.9449 | 2.89 | 2.9853 | 2.9382 | 3.242% | 2.9295 | 2.93 | 2.93 | 2.9399 | 2.9309 | 2.9486 | 02/01 08:00:00 | 5.436 | 2.2616 | 2.4037 | 5.4082 | 1.5906 | 3.4001 | 5.4004 | 1.4973 | 3.6067 | 0.306 | 0.16075 | 1.9036 | 0.27818 | 0.10039 | 2.7709 | 6.5082 | 1.7814 | 3.6534 | 6.5004 | 1.6842 | 3.8597 | 6.525 | 2.2188 | 2.9408 | 3.2082 | 0.94503 | 3.3948 | 6.5083 | 1.6099 | 4.0427 | 6.5361 | 2.2915 | 2.8523 | 0.82819 | 0.24386 | 3.3962 | 0.85601 | 0.37133 | 2.3052 | 7.9469 | 2.1799 | 3.6456
CE170 | 3.38 | 3.34 | 3.4423 | 3.477 | 3.52 | 3.3944 | 3.4033 | 3.34 | 3.52 | 3.4224 | 5.259% | 3.3672 | 3.39 | 3.39 | 3.3937 | 3.3792 | 3.4067 | 02/01 09:00:00 | 5.4365 | 2.2617 | 2.4037 | 5.4088 | 1.5907 | 3.4002 | 5.401 | 1.4974 | 3.6068 | 0.30646 | 0.16099 | 1.9036 | 0.27882 | 0.10062 | 2.771 | 6.5088 | 1.7815 | 3.6535 | 6.501 | 1.6843 | 3.8599 | 6.5255 | 2.2189 | 2.9408 | 3.2088 | 0.94523 | 3.3948 | 6.5089 | 1.6101 | 4.0425 | 6.5365 | 2.2918 | 2.8522 | 0.82883 | 0.2443 | 3.3927 | 0.85647 | 0.37179 | 2.3036 | 7.9474 | 2.1799 | 3.6457
CE180 | 4.04 | 4 | 4.0842 | 4.026 | 4.27 | 4.0472 | 4.055 | 4 | 4.27 | 4.0746 | 6.626% | 4.0423 | 4.04 | 4.04 | 4.0416 | 4.0206 | 4.062 | 02/01 10:00:00 | 5.4379 | 2.2619 | 2.4041 | 5.4103 | 1.5909 | 3.4008 | 5.4026 | 1.4976 | 3.6074 | 0.30786 | 0.16169 | 1.9041 | 0.28031 | 0.10114 | 2.7716 | 6.5103 | 1.7818 | 3.6538 | 6.5026 | 1.6845 | 3.8602 | 6.5269 | 2.2192 | 2.9411 | 3.2103 | 0.94564 | 3.3949 | 6.5104 | 1.6104 | 4.0428 | 6.5379 | 2.2921 | 2.8523 | 0.83032 | 0.24517 | 3.3867 | 0.85787 | 0.37298 | 2.3 | 7.9489 | 2.1802 | 3.646
CE185 | 2.85 | 2.81 | 2.8744 | 2.823 | 2.92 | 2.8512 | 2.8574 | 2.81 | 2.92 | 2.8552 | 3.853% | 2.8458 | 2.85 | 2.85 | 2.8512 | 2.8341 | 2.8674 | 02/01 11:00:00 | 5.4396 | 2.2626 | 2.4042 | 5.412 | 1.5914 | 3.4008 | 5.4043 | 1.4981 | 3.6075 | 0.30963 | 0.16261 | 1.9041 | 0.28203 | 0.10176 | 2.7717 | 6.512 | 1.7821 | 3.6541 | 6.5043 | 1.6848 | 3.8606 | 6.5287 | 2.2196 | 2.9414 | 3.212 | 0.94612 | 3.395 | 6.5121 | 1.6109 | 4.0426 | 6.5397 | 2.2928 | 2.8522 | 0.83204 | 0.24596 | 3.3827 | 0.85964 | 0.37417 | 2.2975 | 7.9506 | 2.1805 | 3.6463
CE190 | 3.41 | 3.37 | 3.4865 | 3.457 | 3.63 | 3.4096 | 3.4048 | 3.37 | 3.63 | 3.4525 | 7.531% | 3.3865 | 3.41 | 3.41 | 3.395 | 3.3365 | 3.4737 | 02/01 12:00:00 | 5.4407 | 2.2631 | 2.4041 | 5.4132 | 1.5918 | 3.4007 | 5.4054 | 1.4984 | 3.6073 | 0.3107 | 0.16318 | 1.904 | 0.28316 | 0.10217 | 2.7715 | 6.5132 | 1.7825 | 3.654 | 6.5055 | 1.6852 | 3.8604 | 6.5298 | 2.2201 | 2.9413 | 3.2132 | 0.94648 | 3.3949 | 6.5132 | 1.6111 | 4.0427 | 6.5407 | 2.2932 | 2.8523 | 0.83317 | 0.24618 | 3.3844 | 0.86071 | 0.37442 | 2.2988 | 7.9517 | 2.1808 | 3.6462
CE195 | 2.31 | 2.28 | 2.3598 | 2.337 | 2.41 | 2.3158 | 2.3054 | 2.28 | 2.41 | 2.3311 | 5.577% | 2.2944 | 2.31 | 2.31 | 2.3041 | 2.2341 | 2.4165 | 02/01 13:00:00 | 5.4411 | 2.2635 | 2.4039 | 5.4136 | 1.5921 | 3.4004 | 5.4058 | 1.4987 | 3.607 | 0.31105 | 0.16339 | 1.9038 | 0.28357 | 0.10233 | 2.7711 | 6.5136 | 1.7827 | 3.6538 | 6.5059 | 1.6853 | 3.8603 | 6.5301 | 2.2203 | 2.9411 | 3.2136 | 0.94663 | 3.3948 | 6.5136 | 1.6113 | 4.0425 | 6.5411 | 2.2935 | 2.852 | 0.83358 | 0.24601 | 3.3883 | 0.86106 | 0.37424 | 2.3008 | 7.9522 | 2.1811 | 3.646
CE200 | 3.62 | 3.57 | 3.6677 | 3.708 | 3.61 | 3.6102 | 3.6102 | 3.57 | 3.708 | 3.628 | 3.804% | 3.6206 | 3.62 | 3.62 | 3.6447 | 3.6334 | 3.6553 | 02/01 14:00:00 | 5.4412 | 2.2639 | 2.4034 | 5.4137 | 1.5924 | 3.3998 | 5.406 | 1.499 | 3.6063 | 0.31123 | 0.16352 | 1.9033 | 0.2837 | 0.1024 | 2.7705 | 6.5137 | 1.783 | 3.6533 | 6.506 | 1.6856 | 3.8598 | 6.5303 | 2.2207 | 2.9407 | 3.2137 | 0.94682 | 3.3942 | 6.5137 | 1.6116 | 4.0419 | 6.5413 | 2.294 | 2.8515 | 0.8337 | 0.24591 | 3.3903 | 0.86124 | 0.37424 | 2.3013 | 7.9523 | 2.1814 | 3.6456
(Max - Min)/Mean COP | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [9 empty] | 02/01 15:00:00 | 5.4411 | 2.2643 | 2.403 | 5.4136 | 1.5927 | 3.3991 | 5.406 | 1.4993 | 3.6056 | 0.31114 | 0.16352 | 1.9028 | 0.28364 | 0.10241 | 2.7697 | 6.5137 | 1.7832 | 3.6528 | 6.506 | 1.6858 | 3.8593 | 6.5302 | 2.221 | 2.9402 | 3.2137 | 0.94697 | 3.3936 | 6.5137 | 1.6118 | 4.0413 | 6.5412 | 2.2944 | 2.851 | 0.83365 | 0.2458 | 3.3916 | 0.86115 | 0.3741 | 2.3019 | 7.9523 | 2.1817 | 3.645
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  |  |  | 02/01 16:00:00 | 5.4407 | 2.2643 | 2.4028 | 5.4133 | 1.5927 | 3.3988 | 5.4057 | 1.4994 | 3.6054 | 0.31072 | 0.16332 | 1.9026 | 0.2833 | 0.1023 | 2.7694 | 6.5133 | 1.7833 | 3.6523 | 6.5058 | 1.6859 | 3.8588 | 6.5299 | 2.2212 | 2.9398 | 3.2133 | 0.94697 | 3.3933 | 6.5134 | 1.6117 | 4.0412 | 6.5408 | 2.2943 | 2.8508 | 0.83331 | 0.24555 | 3.3937 | 0.86073 | 0.37372 | 2.3032 | 7.9519 | 2.1818 | 3.6446
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver 1-09 |  |  | 02/01 17:00:00 | 5.4397 | 2.264 | 2.4027 | 5.4123 | 1.5924 | 3.3987 | 5.4046 | 1.4991 | 3.6052 | 0.3097 | 0.16279 | 1.9025 | 0.28226 | 0.10192 | 2.7693 | 6.5123 | 1.7831 | 3.6522 | 6.5047 | 1.6857 | 3.8586 | 6.5289 | 2.2209 | 2.9397 | 3.2123 | 0.94664 | 3.3934 | 6.5124 | 1.6114 | 4.0415 | 6.5398 | 2.2939 | 2.851 | 0.83227 | 0.24485 | 3.3991 | 0.8597 | 0.37282 | 2.3059 | 7.9509 | 2.1816 | 3.6445
E100 | 0 | 0 | 0.0015062 | 0.0012467 | 0.008658 | 0 | 0 | 0 | 0.008658 | 0.0016301 |  | 0 | 0 | 0.00012552 |  |  |  | 02/01 18:00:00 | 5.4377 | 2.2634 | 2.4025 | 5.4104 | 1.592 | 3.3985 | 5.4028 | 1.4987 | 3.605 | 0.30774 | 0.16178 | 1.9023 | 0.28037 | 0.10125 | 2.7691 | 6.5104 | 1.7827 | 3.652 | 6.5029 | 1.6854 | 3.8584 | 6.5269 | 2.2204 | 2.9396 | 3.2104 | 0.94605 | 3.3935 | 6.5105 | 1.6109 | 4.0416 | 6.5378 | 2.2931 | 2.8511 | 0.83039 | 0.2438 | 3.4061 | 0.85775 | 0.37132 | 2.31 | 7.9491 | 2.1812 | 3.6443
E110 | 0 | 0 | 0.0017378 | 0.0011714 | 0.0062112 | 0 | 0.010592 | 0 | 0.010592 | 0.0028161 |  | 0 | 0 | 0.00038462 |  |  |  | 02/01 19:00:00 | 5.4363 | 2.2629 | 2.4024 | 5.4089 | 1.5916 | 3.3983 | 5.4013 | 1.4983 | 3.6048 | 0.30634 | 0.16105 | 1.9022 | 0.27889 | 0.10072 | 2.7689 | 6.509 | 1.7824 | 3.6518 | 6.5014 | 1.6851 | 3.8582 | 6.5255 | 2.22 | 2.9394 | 3.209 | 0.94567 | 3.3933 | 6.509 | 1.6107 | 4.0412 | 6.5364 | 2.2928 | 2.8508 | 0.82891 | 0.24336 | 3.4061 | 0.85635 | 0.3708 | 2.3095 | 7.9476 | 2.1809 | 3.6441
E120 | 0 | 0 | 0.00079758 | 0.0011041 | 0.0081522 | 0 | 0.012271 | 0 | 0.012271 | 0.0031893 |  | 0 | 0 | 0.00030641 |  |  |  | 02/01 20:00:00 | 5.4355 | 2.2624 | 2.4026 | 5.4081 | 1.5913 | 3.3986 | 5.4007 | 1.498 | 3.6052 | 0.30549 | 0.16058 | 1.9024 | 0.27814 | 0.10044 | 2.7692 | 6.5082 | 1.7821 | 3.6519 | 6.5008 | 1.6849 | 3.8582 | 6.5246 | 2.2196 | 2.9395 | 3.2082 | 0.94542 | 3.3934 | 6.5081 | 1.6103 | 4.0415 | 6.5356 | 2.2923 | 2.8511 | 0.82816 | 0.24334 | 3.4033 | 0.85549 | 0.3706 | 2.3084 | 7.9468 | 2.1807 | 3.6442
E130 | 0 | 0 | 0.012602 | 0.0087046 | 0.01087 | 0 | 0.17198 | 0 | 0.17198 | 0.029165 |  | 0 | 0 | -5.2356e-05 |  |  |  | 02/01 21:00:00 | 5.4349 | 2.262 | 2.4027 | 5.4075 | 1.591 | 3.3988 | 5.4003 | 1.4978 | 3.6054 | 0.30486 | 0.16024 | 1.9025 | 0.27754 | 0.10021 | 2.7694 | 6.5076 | 1.7818 | 3.6522 | 6.5004 | 1.6847 | 3.8585 | 6.524 | 2.2193 | 2.9397 | 3.2076 | 0.94517 | 3.3937 | 6.5076 | 1.6101 | 4.0416 | 6.5349 | 2.292 | 2.8512 | 0.82755 | 0.24326 | 3.4019 | 0.85486 | 0.37044 | 2.3077 | 7.9462 | 2.1804 | 3.6445
E140 | 0 | 0 | 0.010989 | 0.018921 | 0.0075472 | 0 | 0.20433 | 0 | 0.20433 | 0.034541 |  | 0 | 0 | 3.6101e-05 |  |  |  | 02/01 22:00:00 | 5.4345 | 2.2622 | 2.4023 | 5.4072 | 1.5911 | 3.3983 | 5.4001 | 1.498 | 3.605 | 0.30455 | 0.16011 | 1.9022 | 0.27717 | 0.1001 | 2.7689 | 6.5072 | 1.7818 | 3.652 | 6.5002 | 1.6847 | 3.8584 | 6.5237 | 2.2193 | 2.9395 | 3.2072 | 0.94514 | 3.3934 | 6.5072 | 1.6103 | 4.0411 | 6.5346 | 2.2922 | 2.8508 | 0.82718 | 0.24332 | 3.3995 | 0.85455 | 0.37057 | 2.3061 | 7.9459 | 2.1803 | 3.6443
E150 | 0.0027624 | 0 | 0.0014674 | 0.0048649 | 0.0055402 | 0 | 0.0092759 | 0 | 0.0092759 | 0.0034158 |  | 0 | 0 | 0.00096419 |  |  |  | 02/01 23:00:00 | 5.4345 | 2.2623 | 2.4022 | 5.407 | 1.5912 | 3.3981 | 5.3999 | 1.498 | 3.6047 | 0.30451 | 0.1601 | 1.902 | 0.27704 | 0.10006 | 2.7687 | 6.5071 | 1.782 | 3.6517 | 6.5 | 1.6848 | 3.858 | 6.5236 | 2.2195 | 2.9393 | 3.2071 | 0.94521 | 3.393 | 6.5071 | 1.6103 | 4.0408 | 6.5346 | 2.2924 | 2.8505 | 0.82705 | 0.24343 | 3.3975 | 0.85452 | 0.37077 | 2.3047 | 7.9457 | 2.1805 | 3.644
E160 | 0.0026042 | 0 | 0.0010614 | 0.0032911 | 0.0079365 | 0 | 0.010193 | 0 | 0.010193 | 0.0035837 |  | 0 | 0 | 0.00026042 |  |  |  | 02/01 24:00:00 | 5.4341 | 2.2622 | 2.4021 | 5.4066 | 1.5911 | 3.398 | 5.3994 | 1.4979 | 3.6046 | 0.30411 | 0.15989 | 1.9019 | 0.27663 | 0.099918 | 2.7686 | 6.5067 | 1.7819 | 3.6516 | 6.4995 | 1.6847 | 3.858 | 6.5232 | 2.2194 | 2.9392 | 3.2067 | 0.94508 | 3.393 | 6.5067 | 1.6101 | 4.0411 | 6.5342 | 2.2921 | 2.8507 | 0.82664 | 0.24319 | 3.3992 | 0.85412 | 0.37038 | 2.3061 | 7.9453 | 2.1804 | 3.6439
E165 | 0.010274 | 0 | 0.0012002 | 0.0026798 | 0.0067797 | 0 | 0.0084429 | 0 | 0.010274 | 0.0041967 |  | 0 | 0 | 0.00030717 |  |  |  | 02/02 01:00:00 | 5.4335 | 2.262 | 2.4021 | 5.4058 | 1.5909 | 3.3979 | 5.398 | 1.4976 | 3.6045 | 0.30354 | 0.1596 | 1.9019 | 0.27579 | 0.099616 | 2.7685 | 6.5059 | 1.7817 | 3.6515 | 6.4978 | 1.6842 | 3.8581 | 6.5226 | 2.2192 | 2.9391 | 3.2058 | 0.94485 | 3.393 | 6.5059 | 1.6101 | 4.0407 | 6.5336 | 2.2922 | 2.8504 | 0.82581 | 0.24278 | 3.4014 | 0.85355 | 0.37012 | 2.3061 | 7.9446 | 2.1803 | 3.6438
E170 | 0 | 0 | 0.0021466 | 0.0040265 | 0.0056818 | 0 | 0.043444 | 0 | 0.043444 | 0.0078998 |  | 0 | 0 | 0.00026549 |  |  |  | 02/02 02:00:00 | 5.4343 | 2.2622 | 2.4022 | 5.4063 | 1.591 | 3.398 | 5.3986 | 1.4977 | 3.6045 | 0.30425 | 0.15997 | 1.902 | 0.27631 | 0.099801 | 2.7686 | 6.5064 | 1.7818 | 3.6515 | 6.4986 | 1.6845 | 3.8579 | 6.5232 | 2.2194 | 2.9392 | 3.2063 | 0.94505 | 3.3928 | 6.5064 | 1.6102 | 4.0407 | 6.5343 | 2.2924 | 2.8505 | 0.82632 | 0.2434 | 3.3949 | 0.85426 | 0.37098 | 2.3027 | 7.9452 | 2.1804 | 3.6439
E180 | 0.0049505 | 0 | 0.0023307 | 0.009687 | 0.014052 | 0 | 0.011687 | 0 | 0.014052 | 0.0061009 |  | 0 | 0 | 4.9505e-05 |  |  |  | 02/02 03:00:00 | 5.4344 | 2.2625 | 2.4019 | 5.4065 | 1.5913 | 3.3976 | 5.3988 | 1.4979 | 3.6041 | 0.30437 | 0.16005 | 1.9017 | 0.27651 | 0.099889 | 2.7682 | 6.5065 | 1.782 | 3.6513 | 6.4988 | 1.6846 | 3.8578 | 6.5234 | 2.2196 | 2.939 | 3.2065 | 0.94517 | 3.3926 | 6.5066 | 1.6104 | 4.0403 | 6.5344 | 2.2927 | 2.8501 | 0.82652 | 0.24353 | 3.3939 | 0.85437 | 0.37099 | 2.303 | 7.9453 | 2.1806 | 3.6437
E185 | 0.0070175 | 0 | 0.0023597 | 0.010273 | 0.013699 | 0 | 0.0091078 | 0 | 0.013699 | 0.0060652 |  | 0 | 0 | 0.00017544 |  |  |  | 02/02 04:00:00 | 5.435 | 2.2629 | 2.4018 | 5.407 | 1.5915 | 3.3974 | 5.3992 | 1.4982 | 3.6039 | 0.305 | 0.1604 | 1.9015 | 0.27703 | 0.10008 | 2.7679 | 6.5071 | 1.7822 | 3.6511 | 6.4993 | 1.6849 | 3.8574 | 6.524 | 2.22 | 2.9388 | 3.2071 | 0.94543 | 3.3922 | 6.5071 | 1.6107 | 4.04 | 6.5351 | 2.2932 | 2.8498 | 0.82704 | 0.24386 | 3.3914 | 0.85501 | 0.37157 | 2.3011 | 7.9458 | 2.1809 | 3.6434
E190 | 0 | 0 | 0.0071705 | 0.018802 | 0.024793 | 0 | 0.10066 | 0 | 0.10066 | 0.021633 |  | 0 | 0 | -8.7977e-05 |  |  |  | 02/02 05:00:00 | 5.4355 | 2.2631 | 2.4018 | 5.4075 | 1.5916 | 3.3975 | 5.3997 | 1.4982 | 3.604 | 0.30548 | 0.16065 | 1.9016 | 0.27748 | 0.10024 | 2.768 | 6.5075 | 1.7824 | 3.6511 | 6.4998 | 1.685 | 3.8573 | 6.5244 | 2.2201 | 2.9388 | 3.2075 | 0.94556 | 3.3922 | 6.5075 | 1.6107 | 4.0401 | 6.5355 | 2.2932 | 2.8499 | 0.82748 | 0.24401 | 3.3912 | 0.85549 | 0.37176 | 2.3012 | 7.9463 | 2.181 | 3.6434
E195 | 0 | 0 | 0.0078108 | 0.016688 | 0.020747 | 0 | 0.08606 | 0 | 0.08606 | 0.018758 |  | 0 | 0 | 0.00012987 |  |  |  | 02/02 06:00:00 | 5.4354 | 2.263 | 2.4018 | 5.4075 | 1.5916 | 3.3975 | 5.3997 | 1.4983 | 3.604 | 0.30535 | 0.16058 | 1.9016 | 0.27751 | 0.10026 | 2.768 | 6.5075 | 1.7824 | 3.6511 | 6.4998 | 1.6851 | 3.8573 | 6.5244 | 2.2201 | 2.9388 | 3.2075 | 0.94555 | 3.3922 | 6.5076 | 1.6107 | 4.0402 | 6.5354 | 2.2931 | 2.85 | 0.82752 | 0.24386 | 3.3935 | 0.85536 | 0.37138 | 2.3032 | 7.9463 | 2.181 | 3.6434
E200 | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.0055402 | 0 | 0 | -1.2839e-05 | 0.0055402 | 0.0023109 |  | 0 | 0 | 8.2873e-05 |  |  |  | 02/02 07:00:00 | 5.4351 | 2.2627 | 2.4021 | 5.4074 | 1.5914 | 3.3979 | 5.3997 | 1.4981 | 3.6044 | 0.30515 | 0.16045 | 1.9019 | 0.27742 | 0.10021 | 2.7684 | 6.5075 | 1.7822 | 3.6513 | 6.4998 | 1.685 | 3.8575 | 6.5242 | 2.2199 | 2.939 | 3.2075 | 0.94545 | 3.3925 | 6.5075 | 1.6105 | 4.0406 | 6.5352 | 2.2928 | 2.8503 | 0.82743 | 0.24371 | 3.3952 | 0.85516 | 0.37113 | 2.3042 | 7.9462 | 2.1809 | 3.6436
|  | i221000a.wk3 q:a185..o220; 10/23/00 | [15 empty] | 02/02 08:00:00 | 5.4358 | 2.2627 | 2.4023 | 5.4079 | 1.5914 | 3.3982 | 5.4001 | 1.4981 | 3.6047 | 0.30577 | 0.16075 | 1.9021 | 0.27792 | 0.10038 | 2.7688 | 6.508 | 1.7822 | 3.6516 | 6.5002 | 1.6849 | 3.8579 | 6.5247 | 2.2199 | 2.9392 | 3.2079 | 0.94554 | 3.3927 | 6.508 | 1.6107 | 4.0405 | 6.5358 | 2.293 | 2.8503 | 0.82793 | 0.24409 | 3.3919 | 0.85578 | 0.37183 | 2.3015 | 7.9467 | 2.1808 | 3.6439
[18 empty] | 02/02 09:00:00 | 5.4376 | 2.2631 | 2.4028 | 5.4097 | 1.5916 | 3.3988 | 5.4019 | 1.4983 | 3.6053 | 0.30758 | 0.16166 | 1.9026 | 0.27966 | 0.10098 | 2.7694 | 6.5097 | 1.7825 | 3.652 | 6.5019 | 1.6851 | 3.8585 | 6.5265 | 2.2202 | 2.9396 | 3.2097 | 0.94601 | 3.3928 | 6.5097 | 1.611 | 4.0409 | 6.5376 | 2.2934 | 2.8506 | 0.82967 | 0.24517 | 3.384 | 0.85759 | 0.37332 | 2.2972 | 7.9483 | 2.181 | 3.6443
[18 empty] | 02/02 10:00:00 | 5.4388 | 2.2633 | 2.403 | 5.4111 | 1.5919 | 3.3992 | 5.4034 | 1.4985 | 3.6058 | 0.3088 | 0.16228 | 1.9029 | 0.28112 | 0.10149 | 2.7699 | 6.5111 | 1.7826 | 3.6525 | 6.5034 | 1.6853 | 3.8589 | 6.5278 | 2.2204 | 2.94 | 3.2111 | 0.94633 | 3.3933 | 6.5111 | 1.6112 | 4.0412 | 6.5388 | 2.2936 | 2.8509 | 0.83113 | 0.2457 | 3.3826 | 0.8588 | 0.37377 | 2.2977 | 7.9497 | 2.1811 | 3.6447
[18 empty] | 02/02 11:00:00 | 5.44 | 2.2637 | 2.4032 | 5.4124 | 1.5922 | 3.3994 | 5.4047 | 1.4988 | 3.6059 | 0.31004 | 0.16292 | 1.903 | 0.28239 | 0.10194 | 2.77 | 6.5124 | 1.7829 | 3.6527 | 6.5047 | 1.6855 | 3.8591 | 6.5292 | 2.2207 | 2.9402 | 3.2124 | 0.94665 | 3.3934 | 6.5124 | 1.6114 | 4.0414 | 6.5401 | 2.2939 | 2.8511 | 0.83239 | 0.24604 | 3.3831 | 0.86004 | 0.37432 | 2.2976 | 7.951 | 2.1814 | 3.6449
[18 empty] | 02/02 12:00:00 | 5.4404 | 2.2641 | 2.4029 | 5.4127 | 1.5924 | 3.399 | 5.405 | 1.4991 | 3.6055 | 0.31041 | 0.16314 | 1.9027 | 0.28272 | 0.10208 | 2.7696 | 6.5127 | 1.783 | 3.6526 | 6.505 | 1.6857 | 3.8591 | 6.5295 | 2.2209 | 2.9401 | 3.2127 | 0.94676 | 3.3934 | 6.5128 | 1.6116 | 4.0412 | 6.5405 | 2.2942 | 2.8509 | 0.83273 | 0.24581 | 3.3876 | 0.86042 | 0.37414 | 2.2997 | 7.9513 | 2.1815 | 3.6448
[18 empty] | 02/02 13:00:00 | 5.4405 | 2.2645 | 2.4025 | 5.4128 | 1.5928 | 3.3984 | 5.4051 | 1.4994 | 3.6049 | 0.31049 | 0.16322 | 1.9023 | 0.28281 | 0.10214 | 2.7689 | 6.5128 | 1.7833 | 3.6521 | 6.5051 | 1.6859 | 3.8586 | 6.5295 | 2.2212 | 2.9396 | 3.2128 | 0.94693 | 3.3929 | 6.5129 | 1.6118 | 4.0406 | 6.5405 | 2.2946 | 2.8503 | 0.83281 | 0.24569 | 3.3897 | 0.8605 | 0.37402 | 2.3007 | 7.9514 | 2.1818 | 3.6444
[18 empty] | 02/02 14:00:00 | 5.4406 | 2.2647 | 2.4023 | 5.4129 | 1.5929 | 3.3982 | 5.4052 | 1.4995 | 3.6046 | 0.31055 | 0.16327 | 1.9021 | 0.28287 | 0.10217 | 2.7687 | 6.5129 | 1.7835 | 3.6517 | 6.5052 | 1.6861 | 3.8582 | 6.5296 | 2.2215 | 2.9393 | 3.2129 | 0.94706 | 3.3925 | 6.5129 | 1.612 | 4.0404 | 6.5406 | 2.2949 | 2.8501 | 0.83288 | 0.24566 | 3.3903 | 0.86056 | 0.37403 | 2.3008 | 7.9515 | 2.1821 | 3.644
[18 empty] | 02/02 15:00:00 | 5.4406 | 2.2647 | 2.4023 | 5.4129 | 1.5929 | 3.3982 | 5.4052 | 1.4995 | 3.6046 | 0.31061 | 0.1633 | 1.9021 | 0.28286 | 0.10216 | 2.7687 | 6.5129 | 1.7835 | 3.6517 | 6.5053 | 1.6861 | 3.8581 | 6.5296 | 2.2215 | 2.9393 | 3.2129 | 0.94707 | 3.3925 | 6.5129 | 1.6119 | 4.0405 | 6.5407 | 2.2948 | 2.8502 | 0.83287 | 0.24559 | 3.3912 | 0.86062 | 0.37402 | 2.301 | 7.9516 | 2.1821 | 3.6439
[18 empty] | 02/02 16:00:00 | 5.4406 | 2.2647 | 2.4023 | 5.4127 | 1.5928 | 3.3981 | 5.4051 | 1.4995 | 3.6046 | 0.31057 | 0.16328 | 1.9021 | 0.28272 | 0.10211 | 2.7687 | 6.5128 | 1.7835 | 3.6516 | 6.5052 | 1.6861 | 3.8581 | 6.5296 | 2.2215 | 2.9393 | 3.2128 | 0.94702 | 3.3925 | 6.5128 | 1.6119 | 4.0405 | 6.5406 | 2.2948 | 2.8502 | 0.83273 | 0.24548 | 3.3922 | 0.86058 | 0.37395 | 2.3013 | 7.9515 | 2.1821 | 3.6439
[18 empty] | 02/02 17:00:00 | 5.4402 | 2.2646 | 2.4023 | 5.4123 | 1.5928 | 3.3981 | 5.4048 | 1.4994 | 3.6046 | 0.31022 | 0.1631 | 1.9021 | 0.28234 | 0.10198 | 2.7686 | 6.5124 | 1.7834 | 3.6516 | 6.5048 | 1.686 | 3.858 | 6.5292 | 2.2214 | 2.9392 | 3.2124 | 0.9469 | 3.3925 | 6.5124 | 1.6118 | 4.0405 | 6.5403 | 2.2946 | 2.8502 | 0.83235 | 0.24523 | 3.3941 | 0.86023 | 0.3736 | 2.3025 | 7.9511 | 2.182 | 3.6439
[18 empty] | 02/02 18:00:00 | 5.4397 | 2.2644 | 2.4022 | 5.4118 | 1.5926 | 3.398 | 5.4043 | 1.4993 | 3.6045 | 0.30974 | 0.16285 | 1.902 | 0.28181 | 0.10179 | 2.7685 | 6.5119 | 1.7833 | 3.6516 | 6.5044 | 1.6859 | 3.858 | 6.5287 | 2.2213 | 2.9392 | 3.2118 | 0.94674 | 3.3925 | 6.5119 | 1.6116 | 4.0406 | 6.5398 | 2.2945 | 2.8502 | 0.83182 | 0.24496 | 3.3957 | 0.85975 | 0.37326 | 2.3033 | 7.9507 | 2.1819 | 3.6439
[18 empty] | 02/02 19:00:00 | 5.4391 | 2.264 | 2.4025 | 5.4111 | 1.5923 | 3.3983 | 5.4037 | 1.499 | 3.6049 | 0.30908 | 0.16248 | 1.9022 | 0.28111 | 0.10153 | 2.7689 | 6.5112 | 1.7831 | 3.6517 | 6.5038 | 1.6858 | 3.8581 | 6.528 | 2.2209 | 2.9393 | 3.2112 | 0.94646 | 3.3928 | 6.5112 | 1.6113 | 4.041 | 6.5391 | 2.2939 | 2.8506 | 0.83112 | 0.2446 | 3.3979 | 0.85909 | 0.37275 | 2.3047 | 7.9501 | 2.1817 | 3.644
[18 empty] | 02/02 20:00:00 | 5.4386 | 2.2636 | 2.4026 | 5.4106 | 1.5921 | 3.3985 | 5.4032 | 1.4988 | 3.6051 | 0.30856 | 0.1622 | 1.9024 | 0.28065 | 0.10135 | 2.7691 | 6.5107 | 1.7828 | 3.652 | 6.5033 | 1.6855 | 3.8584 | 6.5275 | 2.2206 | 2.9395 | 3.2107 | 0.94625 | 3.3931 | 6.5107 | 1.6111 | 4.0411 | 6.5386 | 2.2937 | 2.8507 | 0.83066 | 0.2445 | 3.3974 | 0.85857 | 0.37253 | 2.3047 | 7.9495 | 2.1814 | 3.6442
[18 empty] | 02/02 21:00:00 | 5.4124 | 2.2549 | 2.4003 | 5.4002 | 1.5894 | 3.3976 | 5.3915 | 1.4959 | 3.6041 | 0.28242 | 0.14863 | 1.9002 | 0.27023 | 0.097617 | 2.7683 | 6.5004 | 1.7802 | 3.6515 | 6.4914 | 1.6825 | 3.8582 | 6.5074 | 2.2145 | 2.9385 | 3.2003 | 0.94242 | 3.3959 | 6.5005 | 1.6069 | 4.0455 | 6.5127 | 2.2789 | 2.8578 | 0.82024 | 0.23661 | 3.4666 | 0.83243 | 0.34489 | 2.4136 | 7.9341 | 2.1774 | 3.6439
[18 empty] | 02/02 22:00:00 | 5.4031 | 2.252 | 2.3993 | 5.3962 | 1.5885 | 3.397 | 5.3872 | 1.495 | 3.6034 | 0.27313 | 0.14382 | 1.8991 | 0.26622 | 0.096194 | 2.7676 | 6.4964 | 1.7794 | 3.6509 | 6.4871 | 1.6817 | 3.8575 | 6.5003 | 2.2131 | 2.9372 | 3.1963 | 0.94187 | 3.3936 | 6.4965 | 1.6078 | 4.0405 | 6.5035 | 2.2826 | 2.8491 | 0.81626 | 0.23726 | 3.4404 | 0.82317 | 0.34777 | 2.367 | 7.9283 | 2.1764 | 3.6429
[18 empty] | 02/02 23:00:00 | 5.4211 | 2.258 | 2.4009 | 5.4031 | 1.5903 | 3.3976 | 5.3945 | 1.4968 | 3.604 | 0.29112 | 0.15316 | 1.9008 | 0.27314 | 0.098671 | 2.7682 | 6.5032 | 1.7813 | 3.6509 | 6.4946 | 1.6838 | 3.8572 | 6.5137 | 2.2172 | 2.9378 | 3.2032 | 0.94476 | 3.3905 | 6.5032 | 1.6114 | 4.0358 | 6.521 | 2.294 | 2.8427 | 0.82315 | 0.24493 | 3.3608 | 0.84113 | 0.37443 | 2.2465 | 7.9384 | 2.1793 | 3.6427
[18 empty] | 02/02 24:00:00 | 5.4381 | 2.2638 | 2.4023 | 5.4103 | 1.5922 | 3.3981 | 5.4017 | 1.4986 | 3.6045 | 0.30811 | 0.16199 | 1.902 | 0.2803 | 0.10124 | 2.7686 | 6.5104 | 1.7828 | 3.6517 | 6.5019 | 1.6854 | 3.8578 | 6.5271 | 2.2207 | 2.9393 | 3.2104 | 0.94653 | 3.3917 | 6.5104 | 1.611 | 4.0413 | 6.538 | 2.2935 | 2.8507 | 0.83031 | 0.24767 | 3.3525 | 0.8581 | 0.38184 | 2.2473 | 7.9488 | 2.1814 | 3.6438
[18 empty] | 02/03 01:00:00 | 5.4364 | 2.2633 | 2.4019 | 5.4088 | 1.5919 | 3.3977 | 5.4013 | 1.4986 | 3.6042 | 0.30636 | 0.1611 | 1.9017 | 0.2788 | 0.10072 | 2.7682 | 6.5089 | 1.7826 | 3.6513 | 6.5014 | 1.6853 | 3.8577 | 6.5255 | 2.2203 | 2.939 | 3.2089 | 0.94585 | 3.3925 | 6.5089 | 1.6109 | 4.0405 | 6.5364 | 2.2933 | 2.8503 | 0.82881 | 0.24453 | 3.3894 | 0.85636 | 0.37334 | 2.2938 | 7.9476 | 2.1812 | 3.6436
[18 empty] | 02/03 02:00:00 | 5.4357 | 2.2631 | 2.4018 | 5.4082 | 1.5918 | 3.3976 | 5.4008 | 1.4985 | 3.6041 | 0.3057 | 0.16076 | 1.9016 | 0.27823 | 0.10051 | 2.7681 | 6.5083 | 1.7825 | 3.6512 | 6.5008 | 1.6852 | 3.8575 | 6.5248 | 2.2202 | 2.9389 | 3.2083 | 0.94572 | 3.3924 | 6.5083 | 1.6108 | 4.0403 | 6.5357 | 2.2932 | 2.8501 | 0.82824 | 0.24391 | 3.3956 | 0.8557 | 0.37167 | 2.3023 | 7.947 | 2.1811 | 3.6435
[18 empty] | 02/03 03:00:00 | 5.4359 | 2.2632 | 2.4019 | 5.4082 | 1.5918 | 3.3976 | 5.4008 | 1.4985 | 3.6041 | 0.30589 | 0.16086 | 1.9016 | 0.27823 | 0.10051 | 2.7681 | 6.5083 | 1.7825 | 3.6512 | 6.5008 | 1.6852 | 3.8575 | 6.5249 | 2.2202 | 2.9388 | 3.2083 | 0.94576 | 3.3923 | 6.5083 | 1.6109 | 4.0402 | 6.5359 | 2.2934 | 2.8499 | 0.82824 | 0.244 | 3.3944 | 0.8559 | 0.37181 | 2.302 | 7.947 | 2.1812 | 3.6435
[18 empty] | 02/03 04:00:00 | 5.4367 | 2.2637 | 2.4017 | 5.4087 | 1.5921 | 3.3973 | 5.401 | 1.4987 | 3.6037 | 0.3067 | 0.1613 | 1.9014 | 0.27874 | 0.10071 | 2.7677 | 6.5088 | 1.7827 | 3.651 | 6.5011 | 1.6853 | 3.8574 | 6.5257 | 2.2206 | 2.9387 | 3.2088 | 0.94601 | 3.3919 | 6.5088 | 1.6112 | 4.0397 | 6.5368 | 2.294 | 2.8495 | 0.82875 | 0.24443 | 3.3906 | 0.85671 | 0.37256 | 2.2995 | 7.9475 | 2.1814 | 3.6434
[18 empty] | 02/03 05:00:00 | 5.4375 | 2.2641 | 2.4016 | 5.4094 | 1.5923 | 3.3971 | 5.4015 | 1.4989 | 3.6035 | 0.30754 | 0.16175 | 1.9013 | 0.27935 | 0.10094 | 2.7675 | 6.5094 | 1.783 | 3.6507 | 6.5015 | 1.6856 | 3.8572 | 6.5264 | 2.221 | 2.9385 | 3.2094 | 0.94628 | 3.3916 | 6.5094 | 1.6115 | 4.0395 | 6.5376 | 2.2945 | 2.8493 | 0.82936 | 0.24476 | 3.3885 | 0.85754 | 0.3731 | 2.2984 | 7.9482 | 2.1817 | 3.6431
[18 empty] | 02/03 06:00:00 | 5.4123 | 2.2559 | 2.3991 | 5.4 | 1.5901 | 3.396 | 5.3912 | 1.4966 | 3.6023 | 0.28228 | 0.14866 | 1.8989 | 0.26999 | 0.097596 | 2.7664 | 6.5001 | 1.7808 | 3.6501 | 6.4911 | 1.683 | 3.8569 | 6.5072 | 2.2153 | 2.9373 | 3.2001 | 0.94286 | 3.394 | 6.5002 | 1.6076 | 4.0435 | 6.5126 | 2.2802 | 2.8561 | 0.81999 | 0.23726 | 3.4562 | 0.83228 | 0.34569 | 2.4076 | 7.9338 | 2.1781 | 3.6426
[18 empty] | 02/03 07:00:00 | 5.421 | 2.2585 | 2.4003 | 5.4034 | 1.5908 | 3.3968 | 5.3945 | 1.4972 | 3.6031 | 0.29099 | 0.15315 | 1.9001 | 0.2734 | 0.0988 | 2.7673 | 6.5034 | 1.7818 | 3.6499 | 6.4946 | 1.6841 | 3.8563 | 6.5138 | 2.2178 | 2.937 | 3.2034 | 0.94497 | 3.3899 | 6.5034 | 1.6118 | 4.035 | 6.521 | 2.2949 | 2.8415 | 0.82339 | 0.24357 | 3.3805 | 0.84102 | 0.36906 | 2.2788 | 7.9385 | 2.1798 | 3.6418
[18 empty] | 02/03 08:00:00 | 5.4125 | 2.2556 | 2.3996 | 5.4005 | 1.5899 | 3.3966 | 5.3913 | 1.4963 | 3.603 | 0.28253 | 0.14875 | 1.8994 | 0.27048 | 0.097748 | 2.7672 | 6.5005 | 1.7807 | 3.6506 | 6.4911 | 1.6829 | 3.857 | 6.5075 | 2.2152 | 2.9377 | 3.2005 | 0.94307 | 3.3938 | 6.5006 | 1.6072 | 4.0448 | 6.5127 | 2.2795 | 2.857 | 0.82046 | 0.23951 | 3.4256 | 0.83252 | 0.35293 | 2.3589 | 7.9341 | 2.178 | 3.6429
[18 empty] | 02/03 09:00:00 | 5.4213 | 2.2584 | 2.4005 | 5.4038 | 1.5907 | 3.3971 | 5.395 | 1.4972 | 3.6034 | 0.29127 | 0.15328 | 1.9003 | 0.27382 | 0.09894 | 2.7676 | 6.5038 | 1.7817 | 3.6503 | 6.4949 | 1.6841 | 3.8567 | 6.5141 | 2.2177 | 2.9373 | 3.2038 | 0.94504 | 3.3902 | 6.5039 | 1.6119 | 4.0349 | 6.5213 | 2.295 | 2.8415 | 0.82383 | 0.24444 | 3.3703 | 0.84129 | 0.37129 | 2.2658 | 7.9389 | 2.1797 | 3.6422
[18 empty] | 02/03 10:00:00 | 5.4395 | 2.2641 | 2.4025 | 5.4121 | 1.5925 | 3.3985 | 5.4029 | 1.4988 | 3.6048 | 0.3095 | 0.1627 | 1.9023 | 0.28212 | 0.10189 | 2.769 | 6.5121 | 1.7833 | 3.6517 | 6.503 | 1.6858 | 3.8576 | 6.5289 | 2.2213 | 2.9392 | 3.2121 | 0.94713 | 3.3914 | 6.512 | 1.6114 | 4.0412 | 6.5395 | 2.2941 | 2.8506 | 0.83213 | 0.24851 | 3.3484 | 0.8595 | 0.38235 | 2.2479 | 7.9501 | 2.1819 | 3.6437
[18 empty] | 02/03 11:00:00 | 5.4396 | 2.264 | 2.4027 | 5.412 | 1.5924 | 3.3987 | 5.4035 | 1.4989 | 3.6051 | 0.30962 | 0.16274 | 1.9025 | 0.28204 | 0.10185 | 2.7693 | 6.512 | 1.7831 | 3.6521 | 6.5036 | 1.6856 | 3.8583 | 6.5288 | 2.221 | 2.9396 | 3.212 | 0.9467 | 3.3929 | 6.5119 | 1.6115 | 4.0409 | 6.5397 | 2.2941 | 2.8506 | 0.83203 | 0.24618 | 3.3797 | 0.85962 | 0.37573 | 2.2878 | 7.9503 | 2.1816 | 3.6443
[18 empty] | 02/03 12:00:00 | 5.4402 | 2.2644 | 2.4024 | 5.4125 | 1.5927 | 3.3983 | 5.4046 | 1.4993 | 3.6048 | 0.31017 | 0.16306 | 1.9022 | 0.28246 | 0.10201 | 2.7689 | 6.5125 | 1.7833 | 3.652 | 6.5046 | 1.6858 | 3.8584 | 6.5292 | 2.2212 | 2.9395 | 3.2125 | 0.94687 | 3.3927 | 6.5124 | 1.6118 | 4.0405 | 6.5402 | 2.2946 | 2.8502 | 0.83246 | 0.2459 | 3.3854 | 0.86017 | 0.37465 | 2.296 | 7.9509 | 2.1818 | 3.6442
[18 empty] | 02/03 13:00:00 | 5.4404 | 2.2649 | 2.402 | 5.4127 | 1.593 | 3.3977 | 5.4049 | 1.4996 | 3.6042 | 0.3104 | 0.16321 | 1.9018 | 0.28273 | 0.10214 | 2.7682 | 6.5127 | 1.7836 | 3.6515 | 6.5049 | 1.6861 | 3.858 | 6.5295 | 2.2216 | 2.9391 | 3.2127 | 0.94711 | 3.3922 | 6.5127 | 1.6121 | 4.0399 | 6.5404 | 2.2951 | 2.8497 | 0.83274 | 0.24583 | 3.3875 | 0.8604 | 0.37429 | 2.2987 | 7.9513 | 2.1822 | 3.6438
[18 empty] | 02/03 14:00:00 | 5.4406 | 2.2654 | 2.4016 | 5.413 | 1.5934 | 3.3971 | 5.4052 | 1.5 | 3.6036 | 0.31064 | 0.16338 | 1.9013 | 0.28298 | 0.10225 | 2.7675 | 6.513 | 1.7839 | 3.6509 | 6.5052 | 1.6864 | 3.8574 | 6.5297 | 2.222 | 2.9387 | 3.213 | 0.94736 | 3.3915 | 6.513 | 1.6124 | 4.0393 | 6.5407 | 2.2957 | 2.8491 | 0.83299 | 0.24589 | 3.3876 | 0.86065 | 0.37438 | 2.2989 | 7.9516 | 2.1825 | 3.6433
[18 empty] | 02/03 15:00:00 | 5.4408 | 2.2659 | 2.4012 | 5.4131 | 1.5937 | 3.3965 | 5.4054 | 1.5003 | 3.6029 | 0.31081 | 0.16351 | 1.9008 | 0.28314 | 0.10233 | 2.7668 | 6.5132 | 1.7842 | 3.6504 | 6.5054 | 1.6867 | 3.8569 | 6.5299 | 2.2224 | 2.9382 | 3.2132 | 0.94758 | 3.3909 | 6.5132 | 1.6127 | 4.0387 | 6.5409 | 2.2961 | 2.8486 | 0.83315 | 0.24593 | 3.3877 | 0.86081 | 0.37446 | 2.2988 | 7.9518 | 2.1829 | 3.6427
[18 empty] | 02/03 16:00:00 | 5.4403 | 2.2659 | 2.401 | 5.4127 | 1.5937 | 3.3962 | 5.4051 | 1.5003 | 3.6026 | 0.3103 | 0.16326 | 1.9006 | 0.28271 | 0.10219 | 2.7665 | 6.5127 | 1.7843 | 3.65 | 6.5051 | 1.6868 | 3.8565 | 6.5294 | 2.2225 | 2.9378 | 3.2127 | 0.94753 | 3.3906 | 6.5128 | 1.6126 | 4.0387 | 6.5404 | 2.296 | 2.8486 | 0.83272 | 0.24555 | 3.3913 | 0.8603 | 0.37388 | 2.301 | 7.9514 | 2.183 | 3.6423
[18 empty] | 02/03 17:00:00 | 5.4395 | 2.2656 | 2.4009 | 5.4119 | 1.5936 | 3.3961 | 5.4044 | 1.5002 | 3.6025 | 0.30947 | 0.16283 | 1.9005 | 0.28193 | 0.10191 | 2.7664 | 6.512 | 1.7842 | 3.6498 | 6.5045 | 1.6867 | 3.8563 | 6.5285 | 2.2223 | 2.9377 | 3.212 | 0.94731 | 3.3906 | 6.512 | 1.6124 | 4.0387 | 6.5395 | 2.2957 | 2.8486 | 0.83194 | 0.24508 | 3.3946 | 0.85947 | 0.37324 | 2.3028 | 7.9506 | 2.1829 | 3.6422
[18 empty] | 02/03 18:00:00 | 5.4386 | 2.2651 | 2.4011 | 5.411 | 1.5931 | 3.3964 | 5.4034 | 1.4998 | 3.6028 | 0.30863 | 0.16237 | 1.9007 | 0.28097 | 0.10155 | 2.7668 | 6.511 | 1.7839 | 3.6499 | 6.5035 | 1.6864 | 3.8563 | 6.5276 | 2.2219 | 2.9378 | 3.211 | 0.94695 | 3.3909 | 6.5111 | 1.6119 | 4.0393 | 6.5387 | 2.2951 | 2.849 | 0.83098 | 0.24456 | 3.3978 | 0.85864 | 0.37267 | 2.304 | 7.9497 | 2.1826 | 3.6423
[18 empty] | 02/03 19:00:00 | 5.4375 | 2.2645 | 2.4011 | 5.4097 | 1.5927 | 3.3965 | 5.4023 | 1.4994 | 3.603 | 0.30746 | 0.16175 | 1.9008 | 0.27969 | 0.10108 | 2.7669 | 6.5097 | 1.7834 | 3.6501 | 6.5024 | 1.6861 | 3.8565 | 6.5264 | 2.2214 | 2.938 | 3.2097 | 0.94648 | 3.3912 | 6.5098 | 1.6116 | 4.0393 | 6.5375 | 2.2946 | 2.8491 | 0.8297 | 0.24398 | 3.4007 | 0.85746 | 0.3719 | 2.3056 | 7.9484 | 2.1821 | 3.6425
[18 empty] | 02/03 20:00:00 | 5.4372 | 2.2642 | 2.4014 | 5.4094 | 1.5925 | 3.3969 | 5.4019 | 1.4991 | 3.6033 | 0.30718 | 0.16158 | 1.9011 | 0.27936 | 0.10095 | 2.7673 | 6.5094 | 1.7832 | 3.6503 | 6.502 | 1.6859 | 3.8567 | 6.5261 | 2.2212 | 2.9381 | 3.2094 | 0.94636 | 3.3913 | 6.5095 | 1.6115 | 4.0395 | 6.5372 | 2.2944 | 2.8492 | 0.82937 | 0.24416 | 3.3969 | 0.85718 | 0.37212 | 2.3035 | 7.9481 | 2.182 | 3.6427
[18 empty] | 02/03 21:00:00 | 5.4121 | 2.2559 | 2.3991 | 5.3999 | 1.5901 | 3.3959 | 5.3913 | 1.4966 | 3.6023 | 0.28214 | 0.14858 | 1.8989 | 0.26991 | 0.09757 | 2.7664 | 6.5001 | 1.7808 | 3.6501 | 6.4912 | 1.6831 | 3.8568 | 6.5071 | 2.2154 | 2.9373 | 3.2 | 0.94286 | 3.394 | 6.5002 | 1.6076 | 4.0434 | 6.5124 | 2.2803 | 2.856 | 0.81992 | 0.23702 | 3.4593 | 0.83214 | 0.34555 | 2.4082 | 7.9337 | 2.1781 | 3.6425
[18 empty] | 02/03 22:00:00 | 5.4031 | 2.2527 | 2.3985 | 5.3962 | 1.589 | 3.3959 | 5.3876 | 1.4956 | 3.6023 | 0.27312 | 0.14388 | 1.8982 | 0.26617 | 0.096219 | 2.7663 | 6.4964 | 1.78 | 3.6496 | 6.4874 | 1.6823 | 3.8562 | 6.5003 | 2.2139 | 2.9361 | 3.1963 | 0.94226 | 3.3922 | 6.4965 | 1.6082 | 4.0395 | 6.5035 | 2.2834 | 2.8482 | 0.8162 | 0.23754 | 3.4361 | 0.82315 | 0.34821 | 2.364 | 7.9282 | 2.1771 | 3.6416
[18 empty] | 02/03 23:00:00 | 5.4033 | 2.2526 | 2.3987 | 5.3959 | 1.5889 | 3.3961 | 5.3876 | 1.4955 | 3.6026 | 0.27334 | 0.14398 | 1.8984 | 0.26587 | 0.0961 | 2.7666 | 6.496 | 1.7798 | 3.6498 | 6.4876 | 1.6823 | 3.8564 | 6.5001 | 2.2137 | 2.9364 | 3.1959 | 0.94221 | 3.392 | 6.4961 | 1.608 | 4.0399 | 6.5036 | 2.2829 | 2.8488 | 0.81588 | 0.23899 | 3.4139 | 0.82336 | 0.35367 | 2.328 | 7.9279 | 2.1769 | 3.6418
[18 empty] | 02/03 24:00:00 | 5.4035 | 2.2526 | 2.3987 | 5.3957 | 1.5888 | 3.3961 | 5.3877 | 1.4955 | 3.6026 | 0.27348 | 0.14406 | 1.8984 | 0.26567 | 0.096031 | 2.7665 | 6.4958 | 1.7797 | 3.6499 | 6.4877 | 1.6823 | 3.8564 | 6.5 | 2.2136 | 2.9364 | 3.1957 | 0.94216 | 3.3919 | 6.4958 | 1.6079 | 4.0398 | 6.5037 | 2.2829 | 2.8488 | 0.81569 | 0.23944 | 3.4066 | 0.8235 | 0.35515 | 2.3188 | 7.9278 | 2.1769 | 3.6418
[18 empty] | 02/04 01:00:00 | 5.4036 | 2.2527 | 2.3987 | 5.3956 | 1.5888 | 3.396 | 5.3877 | 1.4955 | 3.6026 | 0.27357 | 0.1441 | 1.8984 | 0.26555 | 0.095988 | 2.7665 | 6.4956 | 1.7797 | 3.6498 | 6.4877 | 1.6823 | 3.8564 | 6.4998 | 2.2135 | 2.9365 | 3.1956 | 0.94213 | 3.3919 | 6.4957 | 1.6079 | 4.0398 | 6.5037 | 2.283 | 2.8488 | 0.81556 | 0.23959 | 3.4039 | 0.82359 | 0.35555 | 2.3164 | 7.9277 | 2.1769 | 3.6418
[18 empty] | 02/04 02:00:00 | 5.4036 | 2.253 | 2.3985 | 5.3955 | 1.5889 | 3.3956 | 5.3877 | 1.4957 | 3.6022 | 0.27363 | 0.14416 | 1.8981 | 0.26548 | 0.095976 | 2.7661 | 6.4955 | 1.7798 | 3.6496 | 6.4878 | 1.6824 | 3.8563 | 6.4997 | 2.2135 | 2.9363 | 3.1955 | 0.94218 | 3.3916 | 6.4956 | 1.6081 | 4.0393 | 6.5037 | 2.2833 | 2.8485 | 0.81549 | 0.23968 | 3.4024 | 0.82364 | 0.35571 | 2.3155 | 7.9276 | 2.1769 | 3.6416
[18 empty] | 02/04 03:00:00 | 5.4037 | 2.2531 | 2.3983 | 5.3954 | 1.589 | 3.3954 | 5.3877 | 1.4958 | 3.6019 | 0.27366 | 0.14419 | 1.898 | 0.26543 | 0.095968 | 2.7658 | 6.4955 | 1.7799 | 3.6493 | 6.4878 | 1.6825 | 3.856 | 6.4996 | 2.2137 | 2.936 | 3.1955 | 0.94226 | 3.3913 | 6.4955 | 1.6081 | 4.0391 | 6.5038 | 2.2834 | 2.8483 | 0.81544 | 0.23972 | 3.4016 | 0.82367 | 0.35577 | 2.3152 | 7.9276 | 2.1771 | 3.6413
[18 empty] | 02/04 04:00:00 | 5.4037 | 2.2531 | 2.3983 | 5.3954 | 1.589 | 3.3954 | 5.3877 | 1.4958 | 3.6019 | 0.27368 | 0.1442 | 1.898 | 0.2654 | 0.095957 | 2.7658 | 6.4954 | 1.7799 | 3.6493 | 6.4878 | 1.6826 | 3.8559 | 6.4995 | 2.2137 | 2.936 | 3.1954 | 0.94227 | 3.3912 | 6.4955 | 1.6081 | 4.0391 | 6.5038 | 2.2834 | 2.8483 | 0.81541 | 0.23973 | 3.4014 | 0.82369 | 0.35578 | 2.3152 | 7.9276 | 2.1772 | 3.6412
[18 empty] | 02/04 05:00:00 | 5.4037 | 2.2529 | 2.3986 | 5.3954 | 1.5888 | 3.3958 | 5.3877 | 1.4956 | 3.6023 | 0.2737 | 0.14418 | 1.8983 | 0.26538 | 0.095936 | 2.7662 | 6.4954 | 1.7798 | 3.6494 | 6.4878 | 1.6825 | 3.856 | 6.4994 | 2.2136 | 2.9361 | 3.1954 | 0.9422 | 3.3915 | 6.4955 | 1.608 | 4.0395 | 6.5038 | 2.2831 | 2.8486 | 0.81539 | 0.23969 | 3.4018 | 0.82371 | 0.35572 | 2.3156 | 7.9276 | 2.1771 | 3.6414
[18 empty] | 02/04 06:00:00 | 5.4037 | 2.2527 | 2.3988 | 5.3954 | 1.5887 | 3.396 | 5.3877 | 1.4955 | 3.6026 | 0.27371 | 0.14417 | 1.8985 | 0.26537 | 0.095923 | 2.7665 | 6.4954 | 1.7797 | 3.6498 | 6.4878 | 1.6824 | 3.8564 | 6.4993 | 2.2134 | 2.9364 | 3.1954 | 0.9421 | 3.3918 | 6.4954 | 1.6079 | 4.0397 | 6.5038 | 2.283 | 2.8488 | 0.81538 | 0.23968 | 3.402 | 0.82372 | 0.35569 | 2.3158 | 7.9276 | 2.1769 | 3.6417
[18 empty] | 02/04 07:00:00 | 5.4037 | 2.2525 | 2.399 | 5.3954 | 1.5885 | 3.3964 | 5.3877 | 1.4954 | 3.603 | 0.27372 | 0.14416 | 1.8988 | 0.26537 | 0.095906 | 2.7669 | 6.4954 | 1.7796 | 3.65 | 6.4878 | 1.6823 | 3.8566 | 6.4993 | 2.2132 | 2.9366 | 3.1954 | 0.94201 | 3.3921 | 6.4954 | 1.6077 | 4.0402 | 6.5038 | 2.2827 | 2.8492 | 0.81538 | 0.23965 | 3.4024 | 0.82372 | 0.35563 | 2.3162 | 7.9276 | 2.1767 | 3.642
[18 empty] | 02/04 08:00:00 | 5.4037 | 2.2523 | 2.3992 | 5.3954 | 1.5884 | 3.3967 | 5.3877 | 1.4952 | 3.6032 | 0.27372 | 0.14415 | 1.8989 | 0.26537 | 0.095896 | 2.7672 | 6.4954 | 1.7794 | 3.6503 | 6.4878 | 1.6821 | 3.8569 | 6.4993 | 2.213 | 2.9369 | 3.1954 | 0.94191 | 3.3924 | 6.4954 | 1.6076 | 4.0404 | 6.5038 | 2.2825 | 2.8494 | 0.81538 | 0.23963 | 3.4026 | 0.82373 | 0.3556 | 2.3165 | 7.9276 | 2.1765 | 3.6423
[18 empty] | 02/04 09:00:00 | 5.4217 | 2.2579 | 2.4012 | 5.4033 | 1.5901 | 3.398 | 5.395 | 1.4967 | 3.6045 | 0.29169 | 0.15343 | 1.9011 | 0.27329 | 0.098708 | 2.7687 | 6.5033 | 1.7813 | 3.651 | 6.4952 | 1.6839 | 3.8573 | 6.5137 | 2.2171 | 2.9379 | 3.2033 | 0.94483 | 3.3903 | 6.5032 | 1.6114 | 4.0357 | 6.5214 | 2.2939 | 2.8429 | 0.8233 | 0.24624 | 3.3434 | 0.84169 | 0.37674 | 2.2341 | 7.9385 | 2.1793 | 3.6427
[18 empty] | 02/04 10:00:00 | 5.4127 | 2.2545 | 2.4008 | 5.4006 | 1.5892 | 3.3983 | 5.3914 | 1.4956 | 3.6048 | 0.2827 | 0.14874 | 1.9007 | 0.27059 | 0.097719 | 2.769 | 6.5008 | 1.7801 | 3.652 | 6.4912 | 1.6824 | 3.8583 | 6.5076 | 2.2143 | 2.9388 | 3.2008 | 0.94271 | 3.3953 | 6.5009 | 1.6064 | 4.0467 | 6.5129 | 2.2783 | 2.8587 | 0.82067 | 0.24029 | 3.4153 | 0.83269 | 0.35434 | 2.35 | 7.9343 | 2.1773 | 3.6441
[18 empty] | 02/04 11:00:00 | 5.4031 | 2.251 | 2.4003 | 5.3962 | 1.5878 | 3.3984 | 5.3874 | 1.4944 | 3.605 | 0.27313 | 0.14374 | 1.9002 | 0.26615 | 0.096114 | 2.7692 | 6.4964 | 1.779 | 3.6518 | 6.4871 | 1.6813 | 3.8583 | 6.5003 | 2.2124 | 2.9381 | 3.1964 | 0.94159 | 3.3947 | 6.4966 | 1.6073 | 4.042 | 6.5035 | 2.2816 | 2.8504 | 0.81632 | 0.23816 | 3.4276 | 0.82316 | 0.35007 | 2.3514 | 7.9284 | 2.1759 | 3.6437
[18 empty] | 02/04 12:00:00 | 5.4225 | 2.2574 | 2.4021 | 5.4047 | 1.5899 | 3.3993 | 5.396 | 1.4965 | 3.6058 | 0.29248 | 0.15377 | 1.9021 | 0.27469 | 0.099164 | 2.7701 | 6.5048 | 1.781 | 3.6524 | 6.496 | 1.6835 | 3.8587 | 6.515 | 2.2167 | 2.9391 | 3.2047 | 0.94489 | 3.3916 | 6.5048 | 1.6115 | 4.0364 | 6.5223 | 2.2938 | 2.8434 | 0.82474 | 0.24642 | 3.3468 | 0.84249 | 0.37654 | 2.2375 | 7.9399 | 2.1789 | 3.6441
[18 empty] | 02/04 13:00:00 | 5.442 | 2.2642 | 2.4035 | 5.4142 | 1.5925 | 3.3998 | 5.4052 | 1.4989 | 3.6062 | 0.312 | 0.16392 | 1.9034 | 0.2842 | 0.10258 | 2.7705 | 6.5142 | 1.7831 | 3.6533 | 6.5053 | 1.6856 | 3.8594 | 6.5313 | 2.2211 | 2.9406 | 3.2142 | 0.94736 | 3.3927 | 6.5141 | 1.6115 | 4.0424 | 6.5418 | 2.2941 | 2.8516 | 0.83421 | 0.25003 | 3.3365 | 0.862 | 0.38517 | 2.238 | 7.9525 | 2.1816 | 3.6453
[18 empty] | 02/04 14:00:00 | 5.4412 | 2.2643 | 2.403 | 5.4135 | 1.5926 | 3.3991 | 5.4053 | 1.4992 | 3.6056 | 0.31122 | 0.16355 | 1.9028 | 0.28352 | 0.10236 | 2.7697 | 6.5135 | 1.7832 | 3.6528 | 6.5054 | 1.6857 | 3.8592 | 6.5303 | 2.221 | 2.9402 | 3.2135 | 0.94693 | 3.3936 | 6.5135 | 1.6116 | 4.0415 | 6.5412 | 2.2942 | 2.8512 | 0.83352 | 0.24667 | 3.3791 | 0.86121 | 0.37642 | 2.2879 | 7.952 | 2.1816 | 3.645
[18 empty] | 02/04 15:00:00 | 5.4402 | 2.2642 | 2.4027 | 5.4126 | 1.5925 | 3.3988 | 5.4049 | 1.4992 | 3.6053 | 0.31018 | 0.16303 | 1.9025 | 0.28258 | 0.10204 | 2.7693 | 6.5126 | 1.7832 | 3.6523 | 6.505 | 1.6858 | 3.8587 | 6.5293 | 2.221 | 2.9398 | 3.2126 | 0.94674 | 3.3933 | 6.5126 | 1.6116 | 4.0412 | 6.5402 | 2.2942 | 2.8508 | 0.83258 | 0.2454 | 3.3927 | 0.86018 | 0.37386 | 2.3008 | 7.9512 | 2.1817 | 3.6445
[18 empty] | 02/04 16:00:00 | 5.4402 | 2.2642 | 2.4027 | 5.4125 | 1.5925 | 3.3987 | 5.4048 | 1.4992 | 3.6053 | 0.31022 | 0.16306 | 1.9025 | 0.28245 | 0.10199 | 2.7693 | 6.5125 | 1.7832 | 3.6522 | 6.5049 | 1.6858 | 3.8586 | 6.5292 | 2.221 | 2.9397 | 3.2125 | 0.94676 | 3.3931 | 6.5125 | 1.6116 | 4.0411 | 6.5403 | 2.2943 | 2.8507 | 0.83246 | 0.24534 | 3.3931 | 0.86023 | 0.37377 | 2.3015 | 7.9512 | 2.1817 | 3.6445
[18 empty] | 02/04 17:00:00 | 5.4394 | 2.2636 | 2.4029 | 5.4116 | 1.5921 | 3.399 | 5.4041 | 1.4988 | 3.6056 | 0.30939 | 0.1626 | 1.9028 | 0.2816 | 0.10167 | 2.7697 | 6.5117 | 1.7829 | 3.6523 | 6.5042 | 1.6856 | 3.8587 | 6.5284 | 2.2207 | 2.9399 | 3.2116 | 0.94639 | 3.3936 | 6.5117 | 1.6111 | 4.0418 | 6.5394 | 2.2935 | 2.8513 | 0.83161 | 0.24469 | 3.3986 | 0.85939 | 0.37277 | 2.3054 | 7.9503 | 2.1814 | 3.6446
[18 empty] | 02/04 18:00:00 | 5.4385 | 2.2632 | 2.403 | 5.4108 | 1.5918 | 3.3992 | 5.4034 | 1.4985 | 3.6058 | 0.3085 | 0.16213 | 1.9029 | 0.28075 | 0.10136 | 2.7698 | 6.5108 | 1.7825 | 3.6525 | 6.5034 | 1.6853 | 3.8589 | 6.5275 | 2.2202 | 2.94 | 3.2108 | 0.94608 | 3.3938 | 6.5109 | 1.6109 | 4.0417 | 6.5386 | 2.2932 | 2.8513 | 0.83076 | 0.24434 | 3.4 | 0.85851 | 0.37225 | 2.3063 | 7.9495 | 2.1811 | 3.6448
[18 empty] | 02/04 19:00:00 | 5.4384 | 2.2632 | 2.403 | 5.4105 | 1.5917 | 3.3991 | 5.4031 | 1.4985 | 3.6057 | 0.30842 | 0.16209 | 1.9028 | 0.28055 | 0.10129 | 2.7698 | 6.5106 | 1.7825 | 3.6526 | 6.5032 | 1.6852 | 3.859 | 6.5274 | 2.2202 | 2.9401 | 3.2106 | 0.94603 | 3.3938 | 6.5106 | 1.6109 | 4.0417 | 6.5385 | 2.2932 | 2.8513 | 0.83056 | 0.24448 | 3.3973 | 0.85843 | 0.37251 | 2.3044 | 7.9493 | 2.181 | 3.6448
[18 empty] | 02/04 20:00:00 | 5.438 | 2.2628 | 2.4032 | 5.4101 | 1.5915 | 3.3995 | 5.4027 | 1.4982 | 3.6061 | 0.30798 | 0.16183 | 1.9031 | 0.28015 | 0.10113 | 2.7702 | 6.5102 | 1.7823 | 3.6527 | 6.5028 | 1.6851 | 3.8591 | 6.527 | 2.2199 | 2.9402 | 3.2102 | 0.94583 | 3.394 | 6.5102 | 1.6106 | 4.0421 | 6.538 | 2.2927 | 2.8517 | 0.83016 | 0.2443 | 3.3981 | 0.85798 | 0.37215 | 2.3055 | 7.9489 | 2.1808 | 3.645
[18 empty] | 02/04 21:00:00 | 5.4377 | 2.2625 | 2.4034 | 5.4099 | 1.5913 | 3.3997 | 5.4025 | 1.4981 | 3.6063 | 0.30774 | 0.16169 | 1.9033 | 0.2799 | 0.10103 | 2.7704 | 6.51 | 1.7821 | 3.653 | 6.5026 | 1.6849 | 3.8594 | 6.5267 | 2.2196 | 2.9404 | 3.2099 | 0.94568 | 3.3943 | 6.51 | 1.6105 | 4.0423 | 6.5378 | 2.2925 | 2.8518 | 0.82991 | 0.24426 | 3.3977 | 0.85775 | 0.37209 | 2.3052 | 7.9487 | 2.1806 | 3.6453
[18 empty] | 02/04 22:00:00 | 5.4376 | 2.2622 | 2.4036 | 5.4098 | 1.5911 | 3.4001 | 5.4023 | 1.4978 | 3.6067 | 0.30762 | 0.1616 | 1.9036 | 0.27976 | 0.10096 | 2.7709 | 6.5098 | 1.7819 | 3.6532 | 6.5024 | 1.6847 | 3.8596 | 6.5266 | 2.2194 | 2.9406 | 3.2098 | 0.94555 | 3.3946 | 6.5098 | 1.6103 | 4.0427 | 6.5377 | 2.2922 | 2.8522 | 0.82977 | 0.24423 | 3.3975 | 0.85763 | 0.37204 | 2.3052 | 7.9485 | 2.1804 | 3.6455
[18 empty] | 02/04 23:00:00 | 5.4375 | 2.262 | 2.4038 | 5.4096 | 1.5909 | 3.4003 | 5.4022 | 1.4977 | 3.6069 | 0.30749 | 0.16152 | 1.9037 | 0.27961 | 0.1009 | 2.7711 | 6.5097 | 1.7817 | 3.6536 | 6.5022 | 1.6845 | 3.8599 | 6.5264 | 2.2192 | 2.9409 | 3.2097 | 0.94542 | 3.3949 | 6.5097 | 1.6102 | 4.0428 | 6.5375 | 2.292 | 2.8523 | 0.82962 | 0.24418 | 3.3975 | 0.8575 | 0.37196 | 2.3054 | 7.9484 | 2.1802 | 3.6458
[18 empty] | 02/04 24:00:00 | 5.4375 | 2.262 | 2.4038 | 5.4096 | 1.5909 | 3.4003 | 5.4021 | 1.4977 | 3.6069 | 0.30747 | 0.16151 | 1.9037 | 0.27957 | 0.10089 | 2.7711 | 6.5096 | 1.7817 | 3.6536 | 6.5021 | 1.6845 | 3.86 | 6.5264 | 2.2192 | 2.9409 | 3.2096 | 0.9454 | 3.395 | 6.5096 | 1.6102 | 4.0428 | 6.5375 | 2.292 | 2.8523 | 0.82958 | 0.24421 | 3.397 | 0.85748 | 0.372 | 2.305 | 7.9483 | 2.1801 | 3.6458
[18 empty] | 02/05 01:00:00 | 5.4375 | 2.2623 | 2.4035 | 5.4096 | 1.5911 | 3.3999 | 5.402 | 1.4979 | 3.6065 | 0.30752 | 0.16156 | 1.9034 | 0.27957 | 0.10091 | 2.7707 | 6.5096 | 1.7818 | 3.6534 | 6.5021 | 1.6845 | 3.8599 | 6.5265 | 2.2193 | 2.9408 | 3.2096 | 0.94547 | 3.3947 | 6.5097 | 1.6104 | 4.0424 | 6.5376 | 2.2923 | 2.8519 | 0.82958 | 0.24429 | 3.3959 | 0.85752 | 0.37214 | 2.3043 | 7.9483 | 2.1802 | 3.6457
[18 empty] | 02/05 02:00:00 | 5.4378 | 2.2625 | 2.4034 | 5.4097 | 1.5913 | 3.3997 | 5.4021 | 1.498 | 3.6063 | 0.30776 | 0.1617 | 1.9033 | 0.27974 | 0.10097 | 2.7704 | 6.5098 | 1.782 | 3.6531 | 6.5022 | 1.6847 | 3.8595 | 6.5267 | 2.2196 | 2.9405 | 3.2098 | 0.94562 | 3.3943 | 6.5098 | 1.6105 | 4.0421 | 6.5378 | 2.2926 | 2.8517 | 0.82975 | 0.24443 | 3.3946 | 0.85777 | 0.3724 | 2.3033 | 7.9485 | 2.1805 | 3.6454
[18 empty] | 02/05 03:00:00 | 5.438 | 2.2626 | 2.4034 | 5.4099 | 1.5913 | 3.3997 | 5.4023 | 1.498 | 3.6063 | 0.308 | 0.16183 | 1.9033 | 0.27991 | 0.10104 | 2.7704 | 6.51 | 1.7821 | 3.6531 | 6.5023 | 1.6848 | 3.8595 | 6.5269 | 2.2197 | 2.9405 | 3.2099 | 0.94569 | 3.3943 | 6.51 | 1.6105 | 4.0421 | 6.5381 | 2.2927 | 2.8517 | 0.82992 | 0.24452 | 3.3941 | 0.85801 | 0.37256 | 2.303 | 7.9487 | 2.1805 | 3.6453
[18 empty] | 02/05 04:00:00 | 5.4123 | 2.2543 | 2.4009 | 5.4001 | 1.589 | 3.3985 | 5.3913 | 1.4955 | 3.605 | 0.28234 | 0.14853 | 1.9008 | 0.27009 | 0.097531 | 2.7692 | 6.5002 | 1.7797 | 3.6525 | 6.4912 | 1.682 | 3.8592 | 6.5073 | 2.2139 | 2.9393 | 3.2002 | 0.94213 | 3.3968 | 6.5003 | 1.6066 | 4.0461 | 6.5126 | 2.2784 | 2.8585 | 0.82009 | 0.23684 | 3.4627 | 0.83234 | 0.34507 | 2.4121 | 7.9339 | 2.1768 | 3.6448
[18 empty] | 02/05 05:00:00 | 5.4209 | 2.2571 | 2.4018 | 5.4032 | 1.5897 | 3.3989 | 5.3943 | 1.4962 | 3.6054 | 0.29091 | 0.15297 | 1.9017 | 0.27323 | 0.098652 | 2.7696 | 6.5033 | 1.7808 | 3.652 | 6.4944 | 1.6832 | 3.8584 | 6.5137 | 2.2165 | 2.9388 | 3.2033 | 0.94427 | 3.3924 | 6.5033 | 1.6109 | 4.0371 | 6.5209 | 2.2933 | 2.8434 | 0.82332 | 0.24322 | 3.3851 | 0.84093 | 0.36848 | 2.2821 | 7.9384 | 2.1786 | 3.6439
[18 empty] | 02/05 06:00:00 | 5.4388 | 2.2629 | 2.4035 | 5.411 | 1.5916 | 3.3998 | 5.4019 | 1.4979 | 3.6063 | 0.30884 | 0.16226 | 1.9034 | 0.28104 | 0.10144 | 2.7706 | 6.5111 | 1.7823 | 3.6531 | 6.5021 | 1.6849 | 3.8591 | 6.528 | 2.2201 | 2.9404 | 3.2111 | 0.94634 | 3.3932 | 6.511 | 1.6106 | 4.0425 | 6.5387 | 2.2927 | 2.8519 | 0.83114 | 0.24764 | 3.3563 | 0.85884 | 0.38108 | 2.2537 | 7.9492 | 2.1808 | 3.6451
[18 empty] | 02/05 07:00:00 | 5.4388 | 2.2626 | 2.4038 | 5.4108 | 1.5913 | 3.4002 | 5.4023 | 1.4978 | 3.6067 | 0.30875 | 0.16219 | 1.9037 | 0.2808 | 0.10134 | 2.771 | 6.5108 | 1.7821 | 3.6534 | 6.5024 | 1.6847 | 3.8596 | 6.5278 | 2.2198 | 2.9407 | 3.2108 | 0.94588 | 3.3945 | 6.5108 | 1.6105 | 4.0427 | 6.5387 | 2.2926 | 2.8521 | 0.83085 | 0.24543 | 3.3852 | 0.85876 | 0.37475 | 2.2915 | 7.9493 | 2.1806 | 3.6455
[18 empty] | 02/05 08:00:00 | 5.4389 | 2.2625 | 2.4039 | 5.4108 | 1.5912 | 3.4004 | 5.4026 | 1.4978 | 3.607 | 0.30886 | 0.16223 | 1.9039 | 0.28079 | 0.10132 | 2.7712 | 6.5108 | 1.782 | 3.6537 | 6.5027 | 1.6846 | 3.86 | 6.5278 | 2.2196 | 2.941 | 3.2108 | 0.94577 | 3.3949 | 6.5108 | 1.6105 | 4.0428 | 6.5389 | 2.2925 | 2.8523 | 0.83082 | 0.24491 | 3.3923 | 0.85886 | 0.37336 | 2.3004 | 7.9494 | 2.1804 | 3.6459
[18 empty] | 02/05 09:00:00 | 5.4392 | 2.2623 | 2.4042 | 5.4111 | 1.5911 | 3.4009 | 5.403 | 1.4977 | 3.6075 | 0.30918 | 0.16237 | 1.9042 | 0.28106 | 0.1014 | 2.7717 | 6.5111 | 1.7819 | 3.6539 | 6.5031 | 1.6846 | 3.8602 | 6.5281 | 2.2195 | 2.9413 | 3.2111 | 0.94577 | 3.3952 | 6.5111 | 1.6104 | 4.0432 | 6.5392 | 2.2923 | 2.8527 | 0.83108 | 0.24491 | 3.3934 | 0.85919 | 0.37317 | 2.3024 | 7.9498 | 2.1803 | 3.6461
[18 empty] | 02/05 10:00:00 | 5.4396 | 2.2623 | 2.4044 | 5.4115 | 1.5911 | 3.4012 | 5.4037 | 1.4978 | 3.6078 | 0.30963 | 0.16258 | 1.9044 | 0.28154 | 0.10156 | 2.772 | 6.5116 | 1.7819 | 3.6543 | 6.5037 | 1.6846 | 3.8607 | 6.5286 | 2.2194 | 2.9416 | 3.2116 | 0.94583 | 3.3955 | 6.5116 | 1.6104 | 4.0434 | 6.5397 | 2.2923 | 2.8529 | 0.83156 | 0.24512 | 3.3924 | 0.85964 | 0.37333 | 2.3026 | 7.9503 | 2.1803 | 3.6465
[18 empty] | 02/05 11:00:00 | 5.4401 | 2.2625 | 2.4045 | 5.4121 | 1.5912 | 3.4012 | 5.4042 | 1.4979 | 3.6079 | 0.31011 | 0.16283 | 1.9045 | 0.28209 | 0.10176 | 2.7721 | 6.5121 | 1.782 | 3.6544 | 6.5042 | 1.6847 | 3.8608 | 6.5291 | 2.2195 | 2.9416 | 3.2121 | 0.94597 | 3.3956 | 6.5121 | 1.6106 | 4.0434 | 6.5402 | 2.2925 | 2.8529 | 0.83211 | 0.24535 | 3.3915 | 0.86012 | 0.37357 | 2.3024 | 7.9508 | 2.1803 | 3.6466
[18 empty] | 02/05 12:00:00 | 5.4405 | 2.2626 | 2.4045 | 5.4125 | 1.5913 | 3.4013 | 5.4047 | 1.498 | 3.6079 | 0.31048 | 0.16302 | 1.9045 | 0.28254 | 0.10192 | 2.7722 | 6.5126 | 1.7821 | 3.6545 | 6.5047 | 1.6848 | 3.8609 | 6.5294 | 2.2196 | 2.9417 | 3.2126 | 0.94609 | 3.3956 | 6.5126 | 1.6106 | 4.0435 | 6.5405 | 2.2926 | 2.8529 | 0.83255 | 0.24547 | 3.3917 | 0.86049 | 0.37369 | 2.3027 | 7.9512 | 2.1804 | 3.6466
[18 empty] | 02/05 13:00:00 | 5.4408 | 2.263 | 2.4043 | 5.4129 | 1.5916 | 3.4009 | 5.4051 | 1.4983 | 3.6075 | 0.3108 | 0.16321 | 1.9042 | 0.28286 | 0.10205 | 2.7718 | 6.5129 | 1.7822 | 3.6543 | 6.5051 | 1.6849 | 3.8608 | 6.5298 | 2.2198 | 2.9416 | 3.2129 | 0.94625 | 3.3954 | 6.5129 | 1.6109 | 4.0431 | 6.5408 | 2.293 | 2.8526 | 0.83287 | 0.24556 | 3.3917 | 0.86081 | 0.37388 | 2.3023 | 7.9516 | 2.1806 | 3.6465
[18 empty] | 02/05 14:00:00 | 5.4411 | 2.2632 | 2.4041 | 5.4131 | 1.5917 | 3.4007 | 5.4053 | 1.4984 | 3.6073 | 0.31107 | 0.16337 | 1.9041 | 0.28307 | 0.10214 | 2.7715 | 6.5131 | 1.7824 | 3.654 | 6.5053 | 1.6851 | 3.8605 | 6.53 | 2.2201 | 2.9413 | 3.2131 | 0.94639 | 3.3951 | 6.5131 | 1.611 | 4.0429 | 6.5411 | 2.2932 | 2.8524 | 0.83308 | 0.24558 | 3.3923 | 0.86108 | 0.374 | 2.3023 | 7.9518 | 2.1808 | 3.6462
[18 empty] | 02/05 15:00:00 | 5.441 | 2.2632 | 2.4041 | 5.413 | 1.5917 | 3.4007 | 5.4053 | 1.4984 | 3.6073 | 0.31104 | 0.16336 | 1.9041 | 0.28304 | 0.10212 | 2.7715 | 6.5131 | 1.7825 | 3.654 | 6.5054 | 1.6852 | 3.8604 | 6.53 | 2.2201 | 2.9413 | 3.2131 | 0.94638 | 3.3951 | 6.5131 | 1.611 | 4.043 | 6.5411 | 2.2931 | 2.8525 | 0.83305 | 0.24546 | 3.3938 | 0.86105 | 0.37384 | 2.3033 | 7.9518 | 2.1809 | 3.6462
[18 empty] | 02/05 16:00:00 | 5.441 | 2.2632 | 2.4041 | 5.413 | 1.5917 | 3.4007 | 5.4053 | 1.4984 | 3.6073 | 0.311 | 0.16333 | 1.9041 | 0.28299 | 0.10211 | 2.7715 | 6.513 | 1.7824 | 3.654 | 6.5054 | 1.6852 | 3.8604 | 6.5299 | 2.2201 | 2.9413 | 3.213 | 0.94637 | 3.3951 | 6.5131 | 1.611 | 4.043 | 6.541 | 2.2931 | 2.8525 | 0.833 | 0.2454 | 3.3944 | 0.861 | 0.37376 | 2.3036 | 7.9518 | 2.1809 | 3.6462
[18 empty] | 02/05 17:00:00 | 5.4406 | 2.2631 | 2.4041 | 5.4127 | 1.5917 | 3.4007 | 5.4051 | 1.4984 | 3.6073 | 0.31062 | 0.16314 | 1.904 | 0.28268 | 0.102 | 2.7715 | 6.5127 | 1.7824 | 3.654 | 6.5051 | 1.6851 | 3.8604 | 6.5296 | 2.22 | 2.9412 | 3.2127 | 0.94626 | 3.3952 | 6.5128 | 1.6108 | 4.0431 | 6.5407 | 2.2929 | 2.8525 | 0.83269 | 0.24518 | 3.3963 | 0.86063 | 0.37339 | 2.3049 | 7.9515 | 2.1808 | 3.6461
[18 empty] | 02/05 18:00:00 | 5.4394 | 2.2624 | 2.4043 | 5.4116 | 1.5912 | 3.4009 | 5.4041 | 1.498 | 3.6076 | 0.30942 | 0.16249 | 1.9042 | 0.28164 | 0.10161 | 2.7718 | 6.5117 | 1.782 | 3.6541 | 6.5042 | 1.6848 | 3.8604 | 6.5284 | 2.2195 | 2.9413 | 3.2117 | 0.94584 | 3.3956 | 6.5117 | 1.6103 | 4.0438 | 6.5395 | 2.2921 | 2.8531 | 0.83165 | 0.24444 | 3.4022 | 0.85942 | 0.37224 | 2.3088 | 7.9504 | 2.1804 | 3.6463
[18 empty] | 02/05 19:00:00 | 5.4381 | 2.2618 | 2.4043 | 5.4103 | 1.5908 | 3.401 | 5.4029 | 1.4976 | 3.6077 | 0.30809 | 0.16179 | 1.9043 | 0.28031 | 0.10113 | 2.7719 | 6.5104 | 1.7816 | 3.6542 | 6.5029 | 1.6844 | 3.8606 | 6.5271 | 2.219 | 2.9415 | 3.2104 | 0.94537 | 3.3959 | 6.5104 | 1.61 | 4.0437 | 6.5382 | 2.2916 | 2.8531 | 0.83032 | 0.24382 | 3.4055 | 0.8581 | 0.37146 | 2.3101 | 7.9491 | 2.18 | 3.6464
[18 empty] | 02/05 20:00:00 | 5.4376 | 2.2616 | 2.4042 | 5.4098 | 1.5907 | 3.4009 | 5.4024 | 1.4975 | 3.6076 | 0.30756 | 0.16151 | 1.9042 | 0.27983 | 0.10095 | 2.7718 | 6.5099 | 1.7815 | 3.6542 | 6.5025 | 1.6843 | 3.8606 | 6.5266 | 2.2188 | 2.9415 | 3.2099 | 0.94525 | 3.3958 | 6.5099 | 1.6099 | 4.0436 | 6.5376 | 2.2915 | 2.853 | 0.82984 | 0.2439 | 3.4024 | 0.85756 | 0.37149 | 2.3084 | 7.9486 | 2.1798 | 3.6464
[18 empty] | 02/05 21:00:00 | 5.4368 | 2.2614 | 2.4042 | 5.4092 | 1.5905 | 3.4009 | 5.4018 | 1.4974 | 3.6076 | 0.30679 | 0.16111 | 1.9041 | 0.2792 | 0.10073 | 2.7718 | 6.5093 | 1.7813 | 3.6542 | 6.5019 | 1.6842 | 3.8605 | 6.5259 | 2.2186 | 2.9414 | 3.2092 | 0.94507 | 3.3958 | 6.5093 | 1.6098 | 4.0436 | 6.5369 | 2.2912 | 2.853 | 0.82921 | 0.24371 | 3.4025 | 0.85679 | 0.37108 | 2.3089 | 7.9479 | 2.1797 | 3.6464
[18 empty] | 02/05 22:00:00 | 5.4362 | 2.2612 | 2.4041 | 5.4087 | 1.5904 | 3.4008 | 5.4014 | 1.4973 | 3.6075 | 0.30616 | 0.16079 | 1.9041 | 0.27866 | 0.10054 | 2.7717 | 6.5087 | 1.7812 | 3.6541 | 6.5014 | 1.6841 | 3.8605 | 6.5253 | 2.2185 | 2.9413 | 3.2087 | 0.94492 | 3.3957 | 6.5088 | 1.6097 | 4.0436 | 6.5362 | 2.291 | 2.853 | 0.82867 | 0.24357 | 3.4022 | 0.85617 | 0.37084 | 2.3087 | 7.9474 | 2.1796 | 3.6463
[18 empty] | 02/05 23:00:00 | 5.4357 | 2.2611 | 2.4041 | 5.4083 | 1.5903 | 3.4008 | 5.401 | 1.4972 | 3.6075 | 0.30574 | 0.16058 | 1.904 | 0.27826 | 0.10039 | 2.7716 | 6.5083 | 1.7811 | 3.6541 | 6.5011 | 1.684 | 3.8604 | 6.5248 | 2.2183 | 2.9413 | 3.2083 | 0.94482 | 3.3957 | 6.5084 | 1.6096 | 4.0435 | 6.5358 | 2.2909 | 2.8529 | 0.82827 | 0.24351 | 3.4014 | 0.85575 | 0.37076 | 2.3081 | 7.947 | 2.1795 | 3.6463
[18 empty] | 02/05 24:00:00 | 5.4355 | 2.261 | 2.4041 | 5.408 | 1.5903 | 3.4007 | 5.4008 | 1.4971 | 3.6074 | 0.30554 | 0.16047 | 1.904 | 0.27802 | 0.10031 | 2.7716 | 6.5081 | 1.7811 | 3.654 | 6.5009 | 1.684 | 3.8604 | 6.5246 | 2.2183 | 2.9413 | 3.2081 | 0.94476 | 3.3956 | 6.5081 | 1.6095 | 4.0434 | 6.5356 | 2.2909 | 2.8529 | 0.82803 | 0.24351 | 3.4004 | 0.85555 | 0.37079 | 2.3074 | 7.9467 | 2.1794 | 3.6462
[18 empty] | 02/06 01:00:00 | 5.4354 | 2.2612 | 2.4038 | 5.4079 | 1.5904 | 3.4003 | 5.4006 | 1.4972 | 3.607 | 0.30544 | 0.16044 | 1.9037 | 0.27786 | 0.10027 | 2.7711 | 6.5079 | 1.7811 | 3.6538 | 6.5007 | 1.684 | 3.8602 | 6.5245 | 2.2184 | 2.9411 | 3.2079 | 0.9448 | 3.3953 | 6.508 | 1.6097 | 4.0429 | 6.5355 | 2.2912 | 2.8524 | 0.82788 | 0.24356 | 3.3991 | 0.85544 | 0.37091 | 2.3064 | 7.9466 | 2.1795 | 3.6461
[18 empty] | 02/06 02:00:00 | 5.4357 | 2.2615 | 2.4036 | 5.408 | 1.5905 | 3.4001 | 5.4006 | 1.4974 | 3.6068 | 0.30575 | 0.16062 | 1.9036 | 0.27802 | 0.10034 | 2.7709 | 6.5081 | 1.7813 | 3.6535 | 6.5007 | 1.6842 | 3.8599 | 6.5248 | 2.2187 | 2.9408 | 3.2081 | 0.94495 | 3.3949 | 6.5081 | 1.6098 | 4.0427 | 6.5358 | 2.2915 | 2.8522 | 0.82803 | 0.24377 | 3.3968 | 0.85576 | 0.37132 | 2.3047 | 7.9468 | 2.1797 | 3.6457
[18 empty] | 02/06 03:00:00 | 5.4359 | 2.2615 | 2.4036 | 5.4081 | 1.5906 | 3.4001 | 5.4006 | 1.4974 | 3.6068 | 0.30587 | 0.16068 | 1.9036 | 0.27811 | 0.10037 | 2.7709 | 6.5081 | 1.7814 | 3.6535 | 6.5007 | 1.6842 | 3.8598 | 6.5249 | 2.2187 | 2.9408 | 3.2081 | 0.94499 | 3.3949 | 6.5082 | 1.6098 | 4.0427 | 6.5359 | 2.2915 | 2.8523 | 0.82811 | 0.24381 | 3.3966 | 0.85588 | 0.37134 | 2.3049 | 7.9468 | 2.1798 | 3.6457
[18 empty] | 02/06 04:00:00 | 5.4359 | 2.2618 | 2.4034 | 5.4082 | 1.5908 | 3.3997 | 5.4006 | 1.4975 | 3.6063 | 0.30594 | 0.16074 | 1.9033 | 0.27815 | 0.1004 | 2.7705 | 6.5082 | 1.7815 | 3.6533 | 6.5007 | 1.6843 | 3.8597 | 6.5249 | 2.2189 | 2.9406 | 3.2082 | 0.94507 | 3.3946 | 6.5082 | 1.61 | 4.0423 | 6.536 | 2.2918 | 2.8519 | 0.82816 | 0.24385 | 3.3962 | 0.85595 | 0.3714 | 2.3046 | 7.9469 | 2.1799 | 3.6455
[18 empty] | 02/06 05:00:00 | 5.4361 | 2.262 | 2.4032 | 5.4083 | 1.5909 | 3.3995 | 5.4007 | 1.4976 | 3.6061 | 0.30606 | 0.16082 | 1.9031 | 0.27826 | 0.10045 | 2.7702 | 6.5083 | 1.7817 | 3.6529 | 6.5007 | 1.6844 | 3.8593 | 6.5251 | 2.2191 | 2.9404 | 3.2083 | 0.9452 | 3.3943 | 6.5083 | 1.6101 | 4.0421 | 6.5361 | 2.292 | 2.8517 | 0.82827 | 0.24392 | 3.3956 | 0.85607 | 0.3715 | 2.3043 | 7.947 | 2.1801 | 3.6452
[18 empty] | 02/06 06:00:00 | 5.4359 | 2.2619 | 2.4032 | 5.4082 | 1.5909 | 3.3995 | 5.4006 | 1.4976 | 3.6061 | 0.30586 | 0.16072 | 1.9031 | 0.27815 | 0.10041 | 2.7702 | 6.5082 | 1.7817 | 3.6529 | 6.5007 | 1.6844 | 3.8593 | 6.5249 | 2.2191 | 2.9403 | 3.2082 | 0.94517 | 3.3943 | 6.5082 | 1.6101 | 4.0422 | 6.5359 | 2.2919 | 2.8518 | 0.82816 | 0.2438 | 3.3968 | 0.85587 | 0.37124 | 2.3054 | 7.9469 | 2.1801 | 3.6452
[18 empty] | 02/06 07:00:00 | 5.4358 | 2.2616 | 2.4035 | 5.4081 | 1.5907 | 3.3999 | 5.4005 | 1.4974 | 3.6065 | 0.30576 | 0.16064 | 1.9034 | 0.27807 | 0.10036 | 2.7706 | 6.5081 | 1.7815 | 3.6531 | 6.5006 | 1.6844 | 3.8594 | 6.5248 | 2.219 | 2.9405 | 3.2081 | 0.94508 | 3.3945 | 6.5081 | 1.6099 | 4.0425 | 6.5358 | 2.2916 | 2.852 | 0.82807 | 0.24373 | 3.3974 | 0.85577 | 0.37118 | 2.3056 | 7.9468 | 2.18 | 3.6453
[18 empty] | 02/06 08:00:00 | 5.4365 | 2.2617 | 2.4037 | 5.4086 | 1.5907 | 3.4002 | 5.4008 | 1.4974 | 3.6068 | 0.30647 | 0.16099 | 1.9036 | 0.27856 | 0.10053 | 2.771 | 6.5086 | 1.7815 | 3.6534 | 6.5009 | 1.6843 | 3.8598 | 6.5254 | 2.2189 | 2.9408 | 3.2086 | 0.94516 | 3.3947 | 6.5086 | 1.61 | 4.0426 | 6.5365 | 2.2918 | 2.8521 | 0.82857 | 0.24411 | 3.3942 | 0.85648 | 0.3719 | 2.303 | 7.9473 | 2.1799 | 3.6456
[18 empty] | 02/06 09:00:00 | 5.4372 | 2.262 | 2.4038 | 5.4093 | 1.5909 | 3.4003 | 5.4015 | 1.4976 | 3.6069 | 0.30723 | 0.16139 | 1.9037 | 0.27932 | 0.1008 | 2.7711 | 6.5093 | 1.7817 | 3.6535 | 6.5015 | 1.6844 | 3.8599 | 6.5262 | 2.2191 | 2.9409 | 3.2093 | 0.94539 | 3.3947 | 6.5094 | 1.6102 | 4.0425 | 6.5373 | 2.2921 | 2.8521 | 0.82933 | 0.24455 | 3.3912 | 0.85724 | 0.3724 | 2.3019 | 7.9481 | 2.1801 | 3.6458
[18 empty] | 02/06 10:00:00 | 5.4382 | 2.262 | 2.4041 | 5.4106 | 1.591 | 3.4008 | 5.4028 | 1.4977 | 3.6074 | 0.3082 | 0.16186 | 1.9041 | 0.28064 | 0.10125 | 2.7717 | 6.5107 | 1.7818 | 3.6539 | 6.5029 | 1.6846 | 3.8602 | 6.5273 | 2.2193 | 2.9412 | 3.2107 | 0.94571 | 3.395 | 6.5107 | 1.6104 | 4.0429 | 6.5382 | 2.2921 | 2.8525 | 0.83065 | 0.24522 | 3.3874 | 0.85821 | 0.37296 | 2.3011 | 7.9492 | 2.1802 | 3.646
[18 empty] | 02/06 11:00:00 | 5.4392 | 2.2624 | 2.4041 | 5.4118 | 1.5913 | 3.4008 | 5.404 | 1.498 | 3.6074 | 0.30922 | 0.1624 | 1.9041 | 0.28175 | 0.10166 | 2.7716 | 6.5118 | 1.782 | 3.6541 | 6.504 | 1.6847 | 3.8606 | 6.5283 | 2.2195 | 2.9414 | 3.2118 | 0.946 | 3.3951 | 6.5118 | 1.6107 | 4.0428 | 6.5393 | 2.2926 | 2.8524 | 0.83176 | 0.24561 | 3.3865 | 0.85922 | 0.37353 | 2.3003 | 7.9503 | 2.1804 | 3.6463
[18 empty] | 02/06 12:00:00 | 5.4399 | 2.2631 | 2.4038 | 5.4123 | 1.5918 | 3.4002 | 5.4045 | 1.4984 | 3.6068 | 0.30991 | 0.1628 | 1.9037 | 0.28233 | 0.10189 | 2.771 | 6.5123 | 1.7824 | 3.6537 | 6.5046 | 1.685 | 3.8602 | 6.529 | 2.22 | 2.941 | 3.2123 | 0.94628 | 3.3947 | 6.5124 | 1.611 | 4.0424 | 6.54 | 2.2932 | 2.8519 | 0.83234 | 0.24565 | 3.3884 | 0.85992 | 0.37382 | 2.3004 | 7.9509 | 2.1808 | 3.646
[18 empty] | 02/06 13:00:00 | 5.4403 | 2.2636 | 2.4033 | 5.4127 | 1.5921 | 3.3996 | 5.4049 | 1.4988 | 3.6062 | 0.31028 | 0.16303 | 1.9032 | 0.28266 | 0.10203 | 2.7703 | 6.5127 | 1.7827 | 3.6532 | 6.5049 | 1.6853 | 3.8597 | 6.5293 | 2.2204 | 2.9406 | 3.2127 | 0.94654 | 3.3941 | 6.5127 | 1.6113 | 4.0418 | 6.5403 | 2.2937 | 2.8514 | 0.83267 | 0.24565 | 3.3897 | 0.86029 | 0.37389 | 2.3009 | 7.9513 | 2.1811 | 3.6455
[18 empty] | 02/06 14:00:00 | 5.4404 | 2.2641 | 2.4029 | 5.4128 | 1.5925 | 3.399 | 5.4051 | 1.4991 | 3.6055 | 0.31042 | 0.16314 | 1.9027 | 0.28282 | 0.10211 | 2.7696 | 6.5128 | 1.783 | 3.6527 | 6.5051 | 1.6856 | 3.8592 | 6.5295 | 2.2208 | 2.9401 | 3.2128 | 0.94675 | 3.3935 | 6.5129 | 1.6116 | 4.0412 | 6.5405 | 2.2942 | 2.8509 | 0.83282 | 0.24564 | 3.3905 | 0.86042 | 0.37389 | 2.3013 | 7.9515 | 2.1815 | 3.6449
[18 empty] | 02/06 15:00:00 | 5.4404 | 2.2645 | 2.4025 | 5.4128 | 1.5927 | 3.3984 | 5.4051 | 1.4994 | 3.6049 | 0.31035 | 0.16315 | 1.9022 | 0.28277 | 0.10212 | 2.7689 | 6.5128 | 1.7833 | 3.6521 | 6.5051 | 1.6859 | 3.8586 | 6.5294 | 2.2212 | 2.9396 | 3.2128 | 0.94691 | 3.3929 | 6.5128 | 1.6118 | 4.0407 | 6.5404 | 2.2946 | 2.8504 | 0.83277 | 0.24556 | 3.3914 | 0.86036 | 0.37382 | 2.3015 | 7.9514 | 2.1818 | 3.6444
[18 empty] | 02/06 16:00:00 | 5.4401 | 2.2643 | 2.4026 | 5.4125 | 1.5926 | 3.3985 | 5.4049 | 1.4993 | 3.605 | 0.31012 | 0.16302 | 1.9023 | 0.28251 | 0.10202 | 2.7691 | 6.5125 | 1.7833 | 3.6519 | 6.5049 | 1.686 | 3.8583 | 6.5292 | 2.2212 | 2.9395 | 3.2125 | 0.94686 | 3.3928 | 6.5126 | 1.6116 | 4.041 | 6.5402 | 2.2943 | 2.8506 | 0.83252 | 0.24533 | 3.3935 | 0.86013 | 0.37354 | 2.3026 | 7.9512 | 2.1819 | 3.6441
[18 empty] | 02/06 17:00:00 | 5.4395 | 2.2639 | 2.4027 | 5.4119 | 1.5924 | 3.3987 | 5.4044 | 1.499 | 3.6052 | 0.30949 | 0.16268 | 1.9025 | 0.2819 | 0.1018 | 2.7693 | 6.5119 | 1.7831 | 3.6521 | 6.5044 | 1.6857 | 3.8585 | 6.5285 | 2.2209 | 2.9396 | 3.2119 | 0.94659 | 3.3932 | 6.512 | 1.6114 | 4.0412 | 6.5395 | 2.2939 | 2.8508 | 0.83191 | 0.24493 | 3.3965 | 0.85949 | 0.37298 | 2.3044 | 7.9506 | 2.1816 | 3.6444
[18 empty] | 02/06 18:00:00 | 5.439 | 2.2638 | 2.4026 | 5.4113 | 1.5922 | 3.3986 | 5.4039 | 1.4989 | 3.6051 | 0.30895 | 0.1624 | 1.9024 | 0.28131 | 0.10158 | 2.7692 | 6.5114 | 1.7829 | 3.6521 | 6.5039 | 1.6856 | 3.8585 | 6.528 | 2.2207 | 2.9396 | 3.2113 | 0.94641 | 3.3932 | 6.5114 | 1.6113 | 4.0412 | 6.539 | 2.2938 | 2.8508 | 0.83132 | 0.24469 | 3.3975 | 0.85896 | 0.37271 | 2.3047 | 7.95 | 2.1815 | 3.6444
[18 empty] | 02/06 19:00:00 | 5.4386 | 2.2637 | 2.4026 | 5.4108 | 1.5921 | 3.3985 | 5.4034 | 1.4988 | 3.6051 | 0.30863 | 0.16224 | 1.9024 | 0.28083 | 0.10141 | 2.7691 | 6.5109 | 1.7828 | 3.652 | 6.5035 | 1.6855 | 3.8585 | 6.5276 | 2.2206 | 2.9396 | 3.2109 | 0.94628 | 3.3931 | 6.5109 | 1.6112 | 4.0411 | 6.5387 | 2.2937 | 2.8507 | 0.83084 | 0.24457 | 3.3972 | 0.85864 | 0.37267 | 2.304 | 7.9496 | 2.1814 | 3.6443
[18 empty] | 02/06 20:00:00 | 5.4388 | 2.2637 | 2.4026 | 5.4108 | 1.5921 | 3.3985 | 5.4033 | 1.4988 | 3.6051 | 0.30881 | 0.16233 | 1.9024 | 0.28081 | 0.10141 | 2.7691 | 6.5109 | 1.7828 | 3.652 | 6.5034 | 1.6855 | 3.8584 | 6.5277 | 2.2206 | 2.9396 | 3.2108 | 0.9463 | 3.393 | 6.5109 | 1.6112 | 4.041 | 6.5389 | 2.2938 | 2.8506 | 0.83082 | 0.24474 | 3.3946 | 0.85882 | 0.37302 | 2.3023 | 7.9496 | 2.1814 | 3.6443
[18 empty] | 02/06 21:00:00 | 5.4389 | 2.2635 | 2.4029 | 5.4108 | 1.5919 | 3.3989 | 5.4033 | 1.4986 | 3.6055 | 0.30892 | 0.16236 | 1.9027 | 0.28082 | 0.10139 | 2.7696 | 6.5109 | 1.7827 | 3.6522 | 6.5033 | 1.6854 | 3.8586 | 6.5278 | 2.2205 | 2.9398 | 3.2109 | 0.94623 | 3.3933 | 6.5109 | 1.611 | 4.0414 | 6.539 | 2.2936 | 2.851 | 0.83083 | 0.24478 | 3.3942 | 0.85893 | 0.37305 | 2.3025 | 7.9497 | 2.1813 | 3.6445
[18 empty] | 02/06 22:00:00 | 5.439 | 2.2636 | 2.4028 | 5.4108 | 1.592 | 3.3988 | 5.4033 | 1.4987 | 3.6053 | 0.30899 | 0.1624 | 1.9026 | 0.28083 | 0.10141 | 2.7694 | 6.5109 | 1.7827 | 3.6523 | 6.5033 | 1.6853 | 3.8588 | 6.5279 | 2.2205 | 2.9399 | 3.2109 | 0.94622 | 3.3934 | 6.5109 | 1.6111 | 4.0412 | 6.539 | 2.2937 | 2.8509 | 0.83084 | 0.24482 | 3.3936 | 0.85899 | 0.37309 | 2.3024 | 7.9497 | 2.1812 | 3.6446
[18 empty] | 02/06 23:00:00 | 5.439 | 2.2635 | 2.4029 | 5.4108 | 1.5919 | 3.3989 | 5.4033 | 1.4986 | 3.6055 | 0.30902 | 0.16241 | 1.9027 | 0.28085 | 0.1014 | 2.7696 | 6.5109 | 1.7827 | 3.6523 | 6.5033 | 1.6854 | 3.8587 | 6.5279 | 2.2205 | 2.9398 | 3.2109 | 0.94623 | 3.3934 | 6.5109 | 1.6111 | 4.0414 | 6.5391 | 2.2936 | 2.851 | 0.83085 | 0.24482 | 3.3938 | 0.85902 | 0.37306 | 2.3026 | 7.9497 | 2.1813 | 3.6445
[18 empty] | 02/06 24:00:00 | 5.4125 | 2.255 | 2.4002 | 5.4003 | 1.5895 | 3.3975 | 5.3915 | 1.496 | 3.6039 | 0.28253 | 0.14869 | 1.9001 | 0.2703 | 0.097649 | 2.7681 | 6.5004 | 1.7801 | 3.6517 | 6.4914 | 1.6824 | 3.8584 | 6.5075 | 2.2144 | 2.9386 | 3.2004 | 0.94241 | 3.396 | 6.5005 | 1.6069 | 4.0453 | 6.5128 | 2.279 | 2.8577 | 0.82031 | 0.23668 | 3.4659 | 0.83253 | 0.34488 | 2.414 | 7.9342 | 2.1773 | 3.6441
[18 empty] | 02/07 01:00:00 | 5.4199 | 2.2578 | 2.4005 | 5.4024 | 1.5903 | 3.3971 | 5.3936 | 1.4968 | 3.6035 | 0.28994 | 0.15257 | 1.9003 | 0.27244 | 0.098436 | 2.7677 | 6.5026 | 1.7812 | 3.6507 | 6.4938 | 1.6836 | 3.8572 | 6.5128 | 2.217 | 2.9376 | 3.2025 | 0.94438 | 3.3911 | 6.5026 | 1.6112 | 4.0359 | 6.52 | 2.2939 | 2.8423 | 0.82253 | 0.24252 | 3.3915 | 0.84001 | 0.36747 | 2.2859 | 7.9377 | 2.1791 | 3.6426
[18 empty] | 02/07 02:00:00 | 5.4369 | 2.2635 | 2.402 | 5.4094 | 1.5921 | 3.3977 | 5.401 | 1.4985 | 3.6041 | 0.30692 | 0.16139 | 1.9017 | 0.27938 | 0.10092 | 2.7682 | 6.5095 | 1.7828 | 3.6512 | 6.5011 | 1.6854 | 3.8573 | 6.526 | 2.2206 | 2.9388 | 3.2095 | 0.94638 | 3.3913 | 6.5095 | 1.6111 | 4.0404 | 6.5369 | 2.2937 | 2.8499 | 0.82948 | 0.24682 | 3.3606 | 0.85705 | 0.38002 | 2.2553 | 7.9477 | 2.1814 | 3.6434
[18 empty] | 02/07 03:00:00 | 5.4123 | 2.2558 | 2.3993 | 5.4 | 1.59 | 3.3962 | 5.3913 | 1.4965 | 3.6026 | 0.28227 | 0.14864 | 1.8991 | 0.27003 | 0.0976 | 2.7667 | 6.5001 | 1.7806 | 3.6505 | 6.4911 | 1.6828 | 3.8573 | 6.5072 | 2.2151 | 2.9376 | 3.2001 | 0.94279 | 3.3943 | 6.5002 | 1.6075 | 4.0436 | 6.5126 | 2.2801 | 2.8563 | 0.82004 | 0.23782 | 3.4481 | 0.83229 | 0.34759 | 2.3945 | 7.9339 | 2.1779 | 3.643
[18 empty] | 02/07 04:00:00 | 5.4208 | 2.2589 | 2.3997 | 5.4032 | 1.5911 | 3.3959 | 5.3944 | 1.4975 | 3.6023 | 0.29076 | 0.15308 | 1.8994 | 0.27315 | 0.098742 | 2.7663 | 6.5032 | 1.7819 | 3.6496 | 6.4944 | 1.6842 | 3.8561 | 6.5136 | 2.218 | 2.9367 | 3.2032 | 0.94503 | 3.3895 | 6.5032 | 1.612 | 4.0342 | 6.5207 | 2.2954 | 2.8408 | 0.82317 | 0.24365 | 3.3786 | 0.84078 | 0.36951 | 2.2754 | 7.9383 | 2.1799 | 3.6415
[18 empty] | 02/07 05:00:00 | 5.4381 | 2.2647 | 2.4012 | 5.4106 | 1.5929 | 3.3966 | 5.4013 | 1.4992 | 3.6028 | 0.30807 | 0.16207 | 1.9009 | 0.28056 | 0.1014 | 2.767 | 6.5104 | 1.7836 | 3.6502 | 6.5014 | 1.686 | 3.8562 | 6.5272 | 2.2217 | 2.938 | 3.2104 | 0.94703 | 3.39 | 6.5104 | 1.6117 | 4.0395 | 6.5379 | 2.2947 | 2.8492 | 0.83057 | 0.24761 | 3.3543 | 0.85808 | 0.38102 | 2.252 | 7.9486 | 2.1823 | 3.6424
[18 empty] | 02/07 06:00:00 | 5.4375 | 2.2645 | 2.4011 | 5.4098 | 1.5927 | 3.3965 | 5.4013 | 1.4992 | 3.6028 | 0.30747 | 0.16176 | 1.9008 | 0.27978 | 0.10112 | 2.7669 | 6.5098 | 1.7834 | 3.6502 | 6.5015 | 1.6859 | 3.8565 | 6.5265 | 2.2214 | 2.938 | 3.2098 | 0.94657 | 3.391 | 6.5098 | 1.6117 | 4.0391 | 6.5374 | 2.2947 | 2.849 | 0.82978 | 0.24515 | 3.3848 | 0.85748 | 0.37436 | 2.2905 | 7.9483 | 2.1821 | 3.6425
[18 empty] | 02/07 07:00:00 | 5.4371 | 2.2644 | 2.4011 | 5.4094 | 1.5927 | 3.3965 | 5.4013 | 1.4992 | 3.6028 | 0.30711 | 0.16157 | 1.9008 | 0.27941 | 0.10099 | 2.7668 | 6.5095 | 1.7833 | 3.6501 | 6.5015 | 1.6859 | 3.8565 | 6.5261 | 2.2213 | 2.938 | 3.2095 | 0.94644 | 3.3911 | 6.5095 | 1.6116 | 4.0391 | 6.5371 | 2.2946 | 2.849 | 0.82942 | 0.24454 | 3.3917 | 0.85712 | 0.37275 | 2.2995 | 7.948 | 2.182 | 3.6425
[18 empty] | 02/07 08:00:00 | 5.4374 | 2.2643 | 2.4014 | 5.4096 | 1.5925 | 3.3969 | 5.4018 | 1.4991 | 3.6033 | 0.30742 | 0.16171 | 1.9011 | 0.27958 | 0.10103 | 2.7673 | 6.5096 | 1.7833 | 3.6503 | 6.5018 | 1.6859 | 3.8567 | 6.5264 | 2.2213 | 2.9381 | 3.2096 | 0.94647 | 3.3912 | 6.5097 | 1.6116 | 4.0391 | 6.5375 | 2.2947 | 2.849 | 0.82959 | 0.24467 | 3.3907 | 0.85743 | 0.37288 | 2.2995 | 7.9483 | 2.182 | 3.6426
[18 empty] | 02/07 09:00:00 | 5.439 | 2.2646 | 2.4017 | 5.4109 | 1.5927 | 3.3973 | 5.4032 | 1.4993 | 3.6037 | 0.30903 | 0.16252 | 1.9014 | 0.28092 | 0.1015 | 2.7677 | 6.5109 | 1.7834 | 3.6508 | 6.5031 | 1.686 | 3.8572 | 6.528 | 2.2215 | 2.9385 | 3.2109 | 0.9468 | 3.3914 | 6.511 | 1.6118 | 4.0395 | 6.5392 | 2.295 | 2.8493 | 0.83093 | 0.24552 | 3.3844 | 0.85904 | 0.37414 | 2.2961 | 7.9497 | 2.1821 | 3.6431
[18 empty] | 02/07 10:00:00 | 5.4395 | 2.2645 | 2.4021 | 5.4114 | 1.5927 | 3.3977 | 5.4036 | 1.4993 | 3.6042 | 0.30951 | 0.16275 | 1.9018 | 0.28144 | 0.10167 | 2.7682 | 6.5115 | 1.7834 | 3.6511 | 6.5036 | 1.686 | 3.8575 | 6.5285 | 2.2215 | 2.9388 | 3.2115 | 0.94682 | 3.3918 | 6.5115 | 1.6118 | 4.04 | 6.5396 | 2.2948 | 2.8498 | 0.83145 | 0.24549 | 3.3868 | 0.85952 | 0.37394 | 2.2985 | 7.9502 | 2.1821 | 3.6434
[18 empty] | 02/07 11:00:00 | 5.4401 | 2.2646 | 2.4023 | 5.4121 | 1.5927 | 3.3981 | 5.4042 | 1.4993 | 3.6045 | 0.3101 | 0.16304 | 1.902 | 0.28208 | 0.10189 | 2.7686 | 6.5121 | 1.7834 | 3.6515 | 6.5042 | 1.686 | 3.8579 | 6.5291 | 2.2214 | 2.9391 | 3.2121 | 0.94691 | 3.3922 | 6.5121 | 1.6118 | 4.0402 | 6.5402 | 2.2948 | 2.85 | 0.83208 | 0.24568 | 3.3868 | 0.86011 | 0.37415 | 2.2988 | 7.9508 | 2.182 | 3.6438
[18 empty] | 02/07 12:00:00 | 5.4407 | 2.265 | 2.4021 | 5.4127 | 1.593 | 3.3977 | 5.4048 | 1.4996 | 3.6042 | 0.3107 | 0.16337 | 1.9018 | 0.2827 | 0.10212 | 2.7682 | 6.5127 | 1.7836 | 3.6514 | 6.5048 | 1.6861 | 3.8579 | 6.5296 | 2.2217 | 2.9391 | 3.2127 | 0.94714 | 3.392 | 6.5127 | 1.6121 | 4.0398 | 6.5408 | 2.2953 | 2.8497 | 0.83271 | 0.24592 | 3.3861 | 0.8607 | 0.37449 | 2.2983 | 7.9514 | 2.1822 | 3.6437
[18 empty] | 02/07 13:00:00 | 5.4411 | 2.2656 | 2.4017 | 5.4132 | 1.5934 | 3.3972 | 5.4054 | 1.5 | 3.6036 | 0.31115 | 0.16365 | 1.9014 | 0.28319 | 0.10233 | 2.7676 | 6.5132 | 1.784 | 3.6509 | 6.5053 | 1.6864 | 3.8574 | 6.5301 | 2.2221 | 2.9387 | 3.2132 | 0.94744 | 3.3915 | 6.5132 | 1.6125 | 4.0392 | 6.5412 | 2.2958 | 2.8491 | 0.8332 | 0.24609 | 3.3858 | 0.86116 | 0.37473 | 2.2981 | 7.9519 | 2.1826 | 3.6433
[18 empty] | 02/07 14:00:00 | 5.4413 | 2.266 | 2.4012 | 5.4134 | 1.5938 | 3.3966 | 5.4056 | 1.5003 | 3.6029 | 0.31128 | 0.16376 | 1.9009 | 0.28342 | 0.10243 | 2.7669 | 6.5134 | 1.7843 | 3.6504 | 6.5056 | 1.6867 | 3.8569 | 6.5303 | 2.2225 | 2.9382 | 3.2134 | 0.94767 | 3.3909 | 6.5135 | 1.6128 | 4.0387 | 6.5413 | 2.2963 | 2.8487 | 0.83343 | 0.24609 | 3.3867 | 0.86129 | 0.3747 | 2.2986 | 7.9521 | 2.183 | 3.6428
[18 empty] | 02/07 15:00:00 | 5.4407 | 2.266 | 2.401 | 5.4131 | 1.5938 | 3.3963 | 5.4054 | 1.5004 | 3.6027 | 0.3107 | 0.16347 | 1.9006 | 0.28306 | 0.10231 | 2.7666 | 6.5131 | 1.7844 | 3.65 | 6.5054 | 1.6869 | 3.8565 | 6.5298 | 2.2226 | 2.9379 | 3.2131 | 0.94764 | 3.3906 | 6.5131 | 1.6127 | 4.0387 | 6.5408 | 2.2961 | 2.8486 | 0.83307 | 0.24571 | 3.3904 | 0.86071 | 0.37405 | 2.3011 | 7.9518 | 2.1831 | 3.6424
[18 empty] | 02/07 16:00:00 | 5.4399 | 2.2657 | 2.4009 | 5.4123 | 1.5937 | 3.3962 | 5.4048 | 1.5003 | 3.6026 | 0.30985 | 0.16303 | 1.9006 | 0.28235 | 0.10206 | 2.7665 | 6.5124 | 1.7843 | 3.6499 | 6.5049 | 1.6868 | 3.8563 | 6.529 | 2.2224 | 2.9378 | 3.2124 | 0.94743 | 3.3906 | 6.5124 | 1.6125 | 4.0387 | 6.5399 | 2.2958 | 2.8486 | 0.83236 | 0.24526 | 3.3938 | 0.85986 | 0.37341 | 2.3027 | 7.9511 | 2.183 | 3.6422
[18 empty] | 02/07 17:00:00 | 5.4392 | 2.2655 | 2.4008 | 5.4117 | 1.5935 | 3.3961 | 5.4042 | 1.5001 | 3.6025 | 0.30916 | 0.16268 | 1.9005 | 0.28168 | 0.10182 | 2.7664 | 6.5117 | 1.7841 | 3.6498 | 6.5043 | 1.6867 | 3.8563 | 6.5283 | 2.2223 | 2.9377 | 3.2117 | 0.94725 | 3.3906 | 6.5118 | 1.6124 | 4.0387 | 6.5392 | 2.2957 | 2.8485 | 0.83169 | 0.24499 | 3.3948 | 0.85917 | 0.37309 | 2.3029 | 7.9504 | 2.1829 | 3.6422
[18 empty] | 02/07 18:00:00 | 5.4383 | 2.265 | 2.401 | 5.4108 | 1.5931 | 3.3964 | 5.4033 | 1.4997 | 3.6028 | 0.30834 | 0.16223 | 1.9007 | 0.28077 | 0.10148 | 2.7667 | 6.5108 | 1.7838 | 3.6499 | 6.5033 | 1.6864 | 3.8563 | 6.5275 | 2.2219 | 2.9378 | 3.2108 | 0.94689 | 3.3909 | 6.5109 | 1.6119 | 4.0393 | 6.5384 | 2.295 | 2.8489 | 0.83078 | 0.24451 | 3.3978 | 0.85835 | 0.37254 | 2.304 | 7.9495 | 2.1826 | 3.6423
[18 empty] | 02/07 19:00:00 | 5.4375 | 2.2645 | 2.4011 | 5.4097 | 1.5927 | 3.3965 | 5.4022 | 1.4994 | 3.603 | 0.30746 | 0.16175 | 1.9008 | 0.27969 | 0.10109 | 2.7669 | 6.5098 | 1.7834 | 3.6501 | 6.5024 | 1.6861 | 3.8565 | 6.5266 | 2.2215 | 2.938 | 3.2097 | 0.9465 | 3.3912 | 6.5098 | 1.6117 | 4.0392 | 6.5375 | 2.2947 | 2.849 | 0.82971 | 0.24408 | 3.3994 | 0.85747 | 0.37207 | 2.3046 | 7.9485 | 2.1822 | 3.6425
[18 empty] | 02/07 20:00:00 | 5.4378 | 2.2647 | 2.4012 | 5.4098 | 1.5928 | 3.3965 | 5.4023 | 1.4994 | 3.603 | 0.3078 | 0.16193 | 1.9008 | 0.27983 | 0.10114 | 2.7669 | 6.5099 | 1.7835 | 3.6502 | 6.5024 | 1.6861 | 3.8566 | 6.5268 | 2.2215 | 2.938 | 3.2099 | 0.94659 | 3.391 | 6.5099 | 1.6118 | 4.0389 | 6.5379 | 2.2949 | 2.8488 | 0.82984 | 0.24456 | 3.3932 | 0.8578 | 0.37283 | 2.3008 | 7.9486 | 2.1822 | 3.6425
[18 empty] | 02/07 21:00:00 | 5.4383 | 2.2648 | 2.4012 | 5.4102 | 1.5928 | 3.3966 | 5.4025 | 1.4995 | 3.603 | 0.30834 | 0.16221 | 1.9009 | 0.28018 | 0.10126 | 2.7669 | 6.5102 | 1.7835 | 3.6502 | 6.5026 | 1.6861 | 3.8566 | 6.5272 | 2.2216 | 2.9381 | 3.2102 | 0.9467 | 3.3909 | 6.5103 | 1.6119 | 4.039 | 6.5384 | 2.2951 | 2.8488 | 0.83019 | 0.24488 | 3.3901 | 0.85835 | 0.37333 | 2.2992 | 7.949 | 2.1823 | 3.6426
[18 empty] | 02/07 22:00:00 | 5.4124 | 2.2561 | 2.399 | 5.4001 | 1.5903 | 3.3957 | 5.3914 | 1.4967 | 3.6021 | 0.2824 | 0.14873 | 1.8987 | 0.27015 | 0.097663 | 2.7661 | 6.5003 | 1.781 | 3.6498 | 6.4913 | 1.6832 | 3.8565 | 6.5073 | 2.2156 | 2.937 | 3.2003 | 0.94298 | 3.3938 | 6.5004 | 1.6076 | 4.0435 | 6.5127 | 2.2803 | 2.8561 | 0.82016 | 0.237 | 3.4606 | 0.8324 | 0.34539 | 2.41 | 7.934 | 2.1783 | 3.6422
[18 empty] | 02/07 23:00:00 | 5.421 | 2.2588 | 2.4 | 5.4034 | 1.5909 | 3.3964 | 5.3945 | 1.4973 | 3.6027 | 0.29102 | 0.15318 | 1.8998 | 0.27344 | 0.09883 | 2.7668 | 6.5034 | 1.7819 | 3.6497 | 6.4945 | 1.6842 | 3.8561 | 6.5138 | 2.218 | 2.9368 | 3.2034 | 0.94506 | 3.3896 | 6.5035 | 1.612 | 4.0345 | 6.521 | 2.2953 | 2.8411 | 0.82343 | 0.24348 | 3.382 | 0.84104 | 0.36899 | 2.2793 | 7.9386 | 2.18 | 3.6416
[18 empty] | 02/07 24:00:00 | 5.439 | 2.2649 | 2.4014 | 5.4114 | 1.593 | 3.3969 | 5.4021 | 1.4993 | 3.6032 | 0.30901 | 0.16254 | 1.9011 | 0.28138 | 0.10168 | 2.7673 | 6.5112 | 1.7836 | 3.6506 | 6.5023 | 1.686 | 3.8567 | 6.5282 | 2.2218 | 2.9383 | 3.2112 | 0.94719 | 3.3903 | 6.5112 | 1.6118 | 4.0396 | 6.5389 | 2.2949 | 2.8493 | 0.83127 | 0.24793 | 3.3528 | 0.85901 | 0.38162 | 2.251 | 7.9494 | 2.1823 | 3.6427
[18 empty] | 02/08 01:00:00 | 5.4387 | 2.2652 | 2.401 | 5.4109 | 1.5932 | 3.3963 | 5.4023 | 1.4996 | 3.6025 | 0.30872 | 0.16243 | 1.9006 | 0.28092 | 0.10154 | 2.7666 | 6.5108 | 1.7837 | 3.6501 | 6.5025 | 1.6861 | 3.8565 | 6.5278 | 2.2218 | 2.938 | 3.2108 | 0.94693 | 3.3908 | 6.5108 | 1.6121 | 4.0387 | 6.5387 | 2.2954 | 2.8486 | 0.83086 | 0.24571 | 3.3814 | 0.85872 | 0.37521 | 2.2886 | 7.9493 | 2.1824 | 3.6425
[18 empty] | 02/08 02:00:00 | 5.4375 | 2.2647 | 2.401 | 5.4098 | 1.5929 | 3.3963 | 5.4021 | 1.4995 | 3.6027 | 0.30749 | 0.16179 | 1.9006 | 0.27984 | 0.10115 | 2.7666 | 6.5098 | 1.7836 | 3.6499 | 6.5022 | 1.6861 | 3.8563 | 6.5266 | 2.2216 | 2.9378 | 3.2098 | 0.94659 | 3.3909 | 6.5099 | 1.6117 | 4.0392 | 6.5376 | 2.2947 | 2.849 | 0.82982 | 0.24446 | 3.3945 | 0.8575 | 0.37254 | 2.3017 | 7.9486 | 2.1823 | 3.6423
[18 empty] | 02/08 03:00:00 | 5.4364 | 2.2645 | 2.4008 | 5.4089 | 1.5927 | 3.396 | 5.4015 | 1.4994 | 3.6024 | 0.30643 | 0.16125 | 1.9004 | 0.27889 | 0.10082 | 2.7663 | 6.5089 | 1.7833 | 3.6498 | 6.5015 | 1.686 | 3.8563 | 6.5255 | 2.2213 | 2.9377 | 3.2089 | 0.94635 | 3.3909 | 6.509 | 1.6117 | 4.0387 | 6.5365 | 2.2946 | 2.8486 | 0.82889 | 0.24398 | 3.3974 | 0.85644 | 0.37167 | 2.3043 | 7.9477 | 2.1821 | 3.6422
[18 empty] | 02/08 04:00:00 | 5.4369 | 2.2645 | 2.4009 | 5.409 | 1.5927 | 3.3962 | 5.4015 | 1.4993 | 3.6026 | 0.30689 | 0.16148 | 1.9006 | 0.279 | 0.10085 | 2.7665 | 6.509 | 1.7834 | 3.6497 | 6.5015 | 1.686 | 3.8561 | 6.5259 | 2.2215 | 2.9377 | 3.209 | 0.94645 | 3.3906 | 6.5091 | 1.6117 | 4.0386 | 6.537 | 2.2949 | 2.8485 | 0.829 | 0.24434 | 3.3928 | 0.8569 | 0.37254 | 2.3002 | 7.9478 | 2.1822 | 3.6421
[18 empty] | 02/08 05:00:00 | 5.4379 | 2.2647 | 2.4012 | 5.4097 | 1.5927 | 3.3965 | 5.4019 | 1.4993 | 3.6029 | 0.30792 | 0.16199 | 1.9008 | 0.27965 | 0.10107 | 2.7669 | 6.5097 | 1.7834 | 3.6501 | 6.5019 | 1.686 | 3.8565 | 6.5268 | 2.2215 | 2.938 | 3.2097 | 0.94658 | 3.3908 | 6.5097 | 1.6118 | 4.0389 | 6.538 | 2.295 | 2.8488 | 0.82966 | 0.24483 | 3.3887 | 0.85792 | 0.37335 | 2.2979 | 7.9485 | 2.1822 | 3.6424
[18 empty] | 02/08 06:00:00 | 5.438 | 2.2644 | 2.4015 | 5.4098 | 1.5926 | 3.3969 | 5.4021 | 1.4992 | 3.6034 | 0.30796 | 0.16199 | 1.9012 | 0.2798 | 0.10111 | 2.7673 | 6.5098 | 1.7833 | 3.6504 | 6.5021 | 1.6859 | 3.8567 | 6.5269 | 2.2214 | 2.9382 | 3.2098 | 0.94651 | 3.3912 | 6.5099 | 1.6116 | 4.0394 | 6.538 | 2.2946 | 2.8493 | 0.82981 | 0.24474 | 3.3905 | 0.85797 | 0.37296 | 2.3005 | 7.9486 | 2.1821 | 3.6427
[18 empty] | 02/08 07:00:00 | 5.4381 | 2.2643 | 2.4016 | 5.4099 | 1.5925 | 3.3972 | 5.4022 | 1.4991 | 3.6036 | 0.30809 | 0.16204 | 1.9014 | 0.27995 | 0.10115 | 2.7676 | 6.51 | 1.7832 | 3.6507 | 6.5022 | 1.6858 | 3.8571 | 6.527 | 2.2212 | 2.9385 | 3.21 | 0.94646 | 3.3916 | 6.51 | 1.6115 | 4.0396 | 6.5381 | 2.2945 | 2.8494 | 0.82996 | 0.24475 | 3.391 | 0.8581 | 0.37295 | 2.3008 | 7.9488 | 2.1819 | 3.643
[18 empty] | 02/08 08:00:00 | 5.4384 | 2.2642 | 2.4019 | 5.4103 | 1.5924 | 3.3976 | 5.4025 | 1.499 | 3.6041 | 0.30842 | 0.16218 | 1.9017 | 0.28029 | 0.10126 | 2.7681 | 6.5103 | 1.7832 | 3.651 | 6.5026 | 1.6858 | 3.8573 | 6.5273 | 2.2211 | 2.9387 | 3.2103 | 0.94647 | 3.3919 | 6.5103 | 1.6115 | 4.04 | 6.5385 | 2.2943 | 2.8498 | 0.83029 | 0.24489 | 3.3905 | 0.85843 | 0.37311 | 2.3007 | 7.9491 | 2.1819 | 3.6433
[18 empty] | 02/08 09:00:00 | 5.4385 | 2.2638 | 2.4024 | 5.4105 | 1.5921 | 3.3983 | 5.4028 | 1.4988 | 3.6048 | 0.30854 | 0.1622 | 1.9022 | 0.28055 | 0.10132 | 2.7688 | 6.5106 | 1.783 | 3.6515 | 6.5028 | 1.6856 | 3.8579 | 6.5275 | 2.2209 | 2.9392 | 3.2106 | 0.94638 | 3.3925 | 6.5106 | 1.6113 | 4.0406 | 6.5386 | 2.2939 | 2.8504 | 0.83056 | 0.24493 | 3.391 | 0.85855 | 0.37303 | 2.3015 | 7.9493 | 2.1816 | 3.6438
[18 empty] | 02/08 10:00:00 | 5.4392 | 2.2638 | 2.4026 | 5.4112 | 1.5922 | 3.3986 | 5.4034 | 1.4988 | 3.6051 | 0.30917 | 0.16251 | 1.9024 | 0.28122 | 0.10155 | 2.7692 | 6.5112 | 1.7829 | 3.652 | 6.5034 | 1.6856 | 3.8583 | 6.5281 | 2.2208 | 2.9395 | 3.2112 | 0.94649 | 3.3928 | 6.5113 | 1.6114 | 4.0408 | 6.5392 | 2.294 | 2.8505 | 0.83123 | 0.24529 | 3.3887 | 0.85918 | 0.37353 | 2.3002 | 7.9499 | 2.1815 | 3.6442
[18 empty] | 02/08 11:00:00 | 5.4399 | 2.2638 | 2.403 | 5.4122 | 1.5923 | 3.3991 | 5.4045 | 1.4989 | 3.6056 | 0.3099 | 0.16286 | 1.9028 | 0.28224 | 0.1019 | 2.7697 | 6.5124 | 1.7831 | 3.6523 | 6.5045 | 1.6857 | 3.8587 | 6.5289 | 2.2208 | 2.9398 | 3.2124 | 0.94674 | 3.3931 | 6.5124 | 1.6115 | 4.0411 | 6.5399 | 2.294 | 2.8509 | 0.83224 | 0.24578 | 3.3862 | 0.85991 | 0.37393 | 2.2996 | 7.9509 | 2.1816 | 3.6445
[18 empty] | 02/08 12:00:00 | 5.4404 | 2.2641 | 2.4029 | 5.4128 | 1.5925 | 3.399 | 5.405 | 1.4991 | 3.6055 | 0.31036 | 0.16311 | 1.9027 | 0.28276 | 0.10209 | 2.7696 | 6.5129 | 1.7831 | 3.6525 | 6.505 | 1.6857 | 3.859 | 6.5294 | 2.2209 | 2.94 | 3.2129 | 0.94682 | 3.3933 | 6.5129 | 1.6116 | 4.0412 | 6.5404 | 2.2942 | 2.8509 | 0.83277 | 0.24583 | 3.3876 | 0.86037 | 0.37406 | 2.3001 | 7.9514 | 2.1816 | 3.6448
[18 empty] | 02/08 13:00:00 | 5.4403 | 2.2645 | 2.4025 | 5.4129 | 1.5928 | 3.3984 | 5.4052 | 1.4994 | 3.6049 | 0.31033 | 0.16314 | 1.9022 | 0.28288 | 0.10216 | 2.7689 | 6.513 | 1.7834 | 3.6521 | 6.5052 | 1.6859 | 3.8586 | 6.5294 | 2.2212 | 2.9396 | 3.213 | 0.94697 | 3.3929 | 6.513 | 1.6119 | 4.0406 | 6.5404 | 2.2946 | 2.8504 | 0.83289 | 0.24572 | 3.3896 | 0.86034 | 0.37387 | 2.3012 | 7.9515 | 2.1819 | 3.6444
[18 empty] | 02/08 14:00:00 | 5.4401 | 2.2646 | 2.4023 | 5.4128 | 1.5929 | 3.3981 | 5.4052 | 1.4995 | 3.6046 | 0.31014 | 0.16305 | 1.902 | 0.28281 | 0.10215 | 2.7687 | 6.5129 | 1.7835 | 3.6517 | 6.5052 | 1.6861 | 3.8582 | 6.5293 | 2.2214 | 2.9393 | 3.2129 | 0.94704 | 3.3925 | 6.5129 | 1.6119 | 4.0405 | 6.5402 | 2.2947 | 2.8502 | 0.83282 | 0.24559 | 3.3911 | 0.86014 | 0.37367 | 2.3019 | 7.9514 | 2.1821 | 3.644
[18 empty] | 02/08 15:00:00 | 5.4399 | 2.2648 | 2.402 | 5.4127 | 1.593 | 3.3977 | 5.4051 | 1.4997 | 3.6042 | 0.30993 | 0.16297 | 1.9017 | 0.28267 | 0.10211 | 2.7682 | 6.5127 | 1.7836 | 3.6514 | 6.5051 | 1.6862 | 3.8579 | 6.5291 | 2.2215 | 2.9391 | 3.2127 | 0.94708 | 3.3922 | 6.5128 | 1.612 | 4.0401 | 6.54 | 2.2949 | 2.8498 | 0.83268 | 0.2455 | 3.3917 | 0.85993 | 0.37357 | 2.3019 | 7.9513 | 2.1822 | 3.6437
[18 empty] | 02/08 16:00:00 | 5.4395 | 2.2648 | 2.4018 | 5.4123 | 1.593 | 3.3975 | 5.4047 | 1.4997 | 3.6039 | 0.3095 | 0.16277 | 1.9015 | 0.28229 | 0.10199 | 2.7679 | 6.5123 | 1.7837 | 3.6511 | 6.5048 | 1.6862 | 3.8576 | 6.5287 | 2.2216 | 2.9388 | 3.2123 | 0.94705 | 3.3919 | 6.5124 | 1.612 | 4.0399 | 6.5396 | 2.2949 | 2.8497 | 0.8323 | 0.24528 | 3.3933 | 0.85951 | 0.37327 | 2.3026 | 7.9509 | 2.1823 | 3.6434
[18 empty] | 02/08 17:00:00 | 5.4387 | 2.2645 | 2.4017 | 5.4115 | 1.5928 | 3.3974 | 5.4039 | 1.4995 | 3.6038 | 0.30875 | 0.16238 | 1.9014 | 0.28147 | 0.1017 | 2.7678 | 6.5115 | 1.7835 | 3.651 | 6.504 | 1.6861 | 3.8574 | 6.5279 | 2.2214 | 2.9386 | 3.2115 | 0.9468 | 3.392 | 6.5116 | 1.6117 | 4.0401 | 6.5388 | 2.2946 | 2.8497 | 0.83148 | 0.24477 | 3.397 | 0.85876 | 0.3727 | 2.3041 | 7.9501 | 2.1821 | 3.6433
[18 empty] | 02/08 18:00:00 | 5.437 | 2.2637 | 2.4018 | 5.4097 | 1.5922 | 3.3975 | 5.4022 | 1.4989 | 3.604 | 0.30704 | 0.16147 | 1.9016 | 0.2797 | 0.10105 | 2.768 | 6.5098 | 1.783 | 3.651 | 6.5023 | 1.6857 | 3.8574 | 6.5261 | 2.2208 | 2.9387 | 3.2098 | 0.94616 | 3.3924 | 6.5098 | 1.611 | 4.0407 | 6.5371 | 2.2935 | 2.8503 | 0.82972 | 0.24369 | 3.4048 | 0.85704 | 0.37122 | 2.3087 | 7.9483 | 2.1816 | 3.6433
[18 empty] | 02/08 19:00:00 | 5.4354 | 2.263 | 2.4018 | 5.408 | 1.5917 | 3.3976 | 5.4007 | 1.4985 | 3.6041 | 0.30539 | 0.1606 | 1.9016 | 0.27803 | 0.10044 | 2.7681 | 6.5081 | 1.7825 | 3.6511 | 6.5008 | 1.6853 | 3.8574 | 6.5245 | 2.2201 | 2.9388 | 3.2081 | 0.94562 | 3.3926 | 6.5082 | 1.6107 | 4.0405 | 6.5355 | 2.293 | 2.8502 | 0.82805 | 0.24307 | 3.4066 | 0.8554 | 0.37036 | 2.3096 | 7.9467 | 2.1811 | 3.6434
[18 empty] | 02/08 20:00:00 | 5.435 | 2.2627 | 2.4021 | 5.4076 | 1.5915 | 3.3979 | 5.4004 | 1.4982 | 3.6045 | 0.30503 | 0.16039 | 1.9018 | 0.27763 | 0.10028 | 2.7685 | 6.5077 | 1.7823 | 3.6513 | 6.5005 | 1.6851 | 3.8576 | 6.5241 | 2.2199 | 2.939 | 3.2077 | 0.94549 | 3.3926 | 6.5078 | 1.6105 | 4.0407 | 6.5351 | 2.2927 | 2.8504 | 0.82765 | 0.24335 | 3.401 | 0.85504 | 0.37071 | 2.3065 | 7.9463 | 2.1809 | 3.6436
[18 empty] | 02/08 21:00:00 | 5.4349 | 2.2624 | 2.4022 | 5.4074 | 1.5913 | 3.3981 | 5.4002 | 1.4981 | 3.6047 | 0.30489 | 0.1603 | 1.902 | 0.27742 | 0.1002 | 2.7687 | 6.5075 | 1.7821 | 3.6516 | 6.5003 | 1.6849 | 3.8579 | 6.524 | 2.2196 | 2.9392 | 3.2075 | 0.94535 | 3.3929 | 6.5075 | 1.6104 | 4.0409 | 6.5349 | 2.2925 | 2.8506 | 0.82743 | 0.24347 | 3.3985 | 0.8549 | 0.37086 | 2.3052 | 7.9461 | 2.1807 | 3.6439
[18 empty] | 02/08 22:00:00 | 5.4349 | 2.2622 | 2.4025 | 5.4074 | 1.5911 | 3.3985 | 5.4001 | 1.4979 | 3.6051 | 0.30491 | 0.16028 | 1.9023 | 0.27736 | 0.10016 | 2.7691 | 6.5074 | 1.782 | 3.6518 | 6.5002 | 1.6848 | 3.8581 | 6.524 | 2.2195 | 2.9394 | 3.2074 | 0.94525 | 3.3932 | 6.5075 | 1.6103 | 4.0413 | 6.535 | 2.2923 | 2.8509 | 0.82737 | 0.24354 | 3.3972 | 0.85491 | 0.37096 | 2.3046 | 7.9461 | 2.1805 | 3.6441
[18 empty] | 02/08 23:00:00 | 5.435 | 2.2621 | 2.4027 | 5.4074 | 1.591 | 3.3988 | 5.4001 | 1.4978 | 3.6054 | 0.30501 | 0.16032 | 1.9025 | 0.27739 | 0.10016 | 2.7694 | 6.5074 | 1.7818 | 3.6522 | 6.5002 | 1.6846 | 3.8585 | 6.5241 | 2.2193 | 2.9397 | 3.2074 | 0.94517 | 3.3935 | 6.5075 | 1.6102 | 4.0414 | 6.5351 | 2.2921 | 2.8511 | 0.8274 | 0.24361 | 3.3964 | 0.85502 | 0.37106 | 2.3043 | 7.9461 | 2.1803 | 3.6444
[18 empty] | 02/08 24:00:00 | 5.435 | 2.2621 | 2.4027 | 5.4074 | 1.591 | 3.3988 | 5.4 | 1.4978 | 3.6054 | 0.30501 | 0.16032 | 1.9025 | 0.27738 | 0.10016 | 2.7694 | 6.5074 | 1.7818 | 3.6522 | 6.5001 | 1.6846 | 3.8586 | 6.524 | 2.2193 | 2.9397 | 3.2074 | 0.94515 | 3.3936 | 6.5075 | 1.6102 | 4.0415 | 6.5351 | 2.2921 | 2.8511 | 0.82739 | 0.24361 | 3.3963 | 0.85502 | 0.37102 | 2.3045 | 7.9461 | 2.1803 | 3.6445
[18 empty] | 02/09 01:00:00 | 5.4349 | 2.262 | 2.4027 | 5.4073 | 1.591 | 3.3987 | 5.3999 | 1.4978 | 3.6054 | 0.30486 | 0.16024 | 1.9025 | 0.27726 | 0.10012 | 2.7694 | 6.5073 | 1.7817 | 3.6522 | 6.5 | 1.6846 | 3.8585 | 6.5239 | 2.2192 | 2.9397 | 3.2073 | 0.9451 | 3.3936 | 6.5073 | 1.6101 | 4.0415 | 6.5349 | 2.292 | 2.8511 | 0.82727 | 0.24353 | 3.3969 | 0.85487 | 0.37086 | 2.3051 | 7.946 | 2.1803 | 3.6445
[18 empty] | 02/09 02:00:00 | 5.4348 | 2.2622 | 2.4024 | 5.4072 | 1.5911 | 3.3983 | 5.3998 | 1.4979 | 3.6049 | 0.30475 | 0.16021 | 1.9022 | 0.27717 | 0.1001 | 2.7689 | 6.5072 | 1.7818 | 3.652 | 6.4999 | 1.6846 | 3.8584 | 6.5238 | 2.2193 | 2.9396 | 3.2072 | 0.94515 | 3.3933 | 6.5072 | 1.6103 | 4.041 | 6.5348 | 2.2923 | 2.8507 | 0.82718 | 0.24354 | 3.3965 | 0.85476 | 0.37088 | 2.3047 | 7.9459 | 2.1803 | 3.6443
[18 empty] | 02/09 03:00:00 | 5.4347 | 2.2624 | 2.4022 | 5.4071 | 1.5912 | 3.3981 | 5.3998 | 1.498 | 3.6047 | 0.30472 | 0.16021 | 1.902 | 0.27712 | 0.10009 | 2.7687 | 6.5072 | 1.782 | 3.6517 | 6.4998 | 1.6847 | 3.8581 | 6.5238 | 2.2195 | 2.9393 | 3.2072 | 0.94524 | 3.393 | 6.5072 | 1.6104 | 4.0408 | 6.5348 | 2.2925 | 2.8505 | 0.82713 | 0.24356 | 3.396 | 0.85473 | 0.37093 | 2.3043 | 7.9458 | 2.1805 | 3.644
[18 empty] | 02/09 04:00:00 | 5.4358 | 2.2627 | 2.4023 | 5.4079 | 1.5914 | 3.3982 | 5.4002 | 1.4981 | 3.6047 | 0.30576 | 0.16075 | 1.9021 | 0.27786 | 0.10036 | 2.7688 | 6.5079 | 1.7822 | 3.6517 | 6.5002 | 1.6849 | 3.858 | 6.5248 | 2.2198 | 2.9393 | 3.2079 | 0.94553 | 3.3927 | 6.5079 | 1.6107 | 4.0404 | 6.5358 | 2.2931 | 2.8502 | 0.82787 | 0.24418 | 3.3905 | 0.85577 | 0.37209 | 2.2999 | 7.9466 | 2.1808 | 3.644
[18 empty] | 02/09 05:00:00 | 5.4372 | 2.2632 | 2.4024 | 5.4091 | 1.5917 | 3.3983 | 5.4015 | 1.4984 | 3.6049 | 0.30719 | 0.16149 | 1.9022 | 0.27911 | 0.1008 | 2.7689 | 6.5091 | 1.7824 | 3.6518 | 6.5013 | 1.685 | 3.8583 | 6.5262 | 2.2202 | 2.9394 | 3.2091 | 0.94588 | 3.3927 | 6.5091 | 1.6109 | 4.0407 | 6.5372 | 2.2934 | 2.8505 | 0.82911 | 0.24482 | 3.3867 | 0.8572 | 0.37299 | 2.2982 | 7.9479 | 2.181 | 3.6441
[18 empty] | 02/09 06:00:00 | 5.4368 | 2.2631 | 2.4024 | 5.409 | 1.5917 | 3.3983 | 5.4014 | 1.4984 | 3.6049 | 0.3068 | 0.16129 | 1.9022 | 0.27898 | 0.10076 | 2.7689 | 6.509 | 1.7824 | 3.6518 | 6.5013 | 1.685 | 3.8582 | 6.5258 | 2.2201 | 2.9394 | 3.209 | 0.94577 | 3.393 | 6.509 | 1.6107 | 4.041 | 6.5369 | 2.293 | 2.8508 | 0.82899 | 0.24432 | 3.3931 | 0.85681 | 0.37195 | 2.3035 | 7.9477 | 2.181 | 3.6441
[18 empty] | 02/09 07:00:00 | 5.4357 | 2.2627 | 2.4023 | 5.4082 | 1.5915 | 3.3982 | 5.4009 | 1.4982 | 3.6048 | 0.30565 | 0.16069 | 1.9021 | 0.27821 | 0.10048 | 2.7688 | 6.5082 | 1.7822 | 3.6518 | 6.5009 | 1.685 | 3.8581 | 6.5248 | 2.2198 | 2.9393 | 3.2082 | 0.94552 | 3.3931 | 6.5083 | 1.6105 | 4.0411 | 6.5357 | 2.2926 | 2.8507 | 0.82822 | 0.24369 | 3.3987 | 0.85566 | 0.37086 | 2.3072 | 7.9469 | 2.1808 | 3.6441
[18 empty] | 02/09 08:00:00 | 5.4355 | 2.2624 | 2.4025 | 5.408 | 1.5913 | 3.3986 | 5.4006 | 1.498 | 3.6052 | 0.30546 | 0.16057 | 1.9024 | 0.27801 | 0.10039 | 2.7692 | 6.5081 | 1.7821 | 3.6519 | 6.5007 | 1.6849 | 3.8582 | 6.5246 | 2.2196 | 2.9395 | 3.2081 | 0.94543 | 3.3932 | 6.5081 | 1.6104 | 4.0412 | 6.5355 | 2.2925 | 2.8509 | 0.82802 | 0.24372 | 3.3974 | 0.85547 | 0.37108 | 2.3054 | 7.9467 | 2.1807 | 3.6442
[18 empty] | 02/09 09:00:00 | 5.4366 | 2.2626 | 2.4028 | 5.4091 | 1.5914 | 3.399 | 5.4014 | 1.4981 | 3.6055 | 0.3066 | 0.16114 | 1.9027 | 0.2791 | 0.10077 | 2.7696 | 6.5091 | 1.7822 | 3.6523 | 6.5014 | 1.6849 | 3.8587 | 6.5257 | 2.2198 | 2.9398 | 3.2091 | 0.94573 | 3.3933 | 6.5092 | 1.6107 | 4.0411 | 6.5367 | 2.2929 | 2.8508 | 0.82911 | 0.24462 | 3.3894 | 0.85661 | 0.37237 | 2.3005 | 7.9478 | 2.1807 | 3.6446
[18 empty] | 02/09 10:00:00 | 5.4385 | 2.2632 | 2.403 | 5.4109 | 1.5918 | 3.3992 | 5.4032 | 1.4985 | 3.6057 | 0.3085 | 0.16212 | 1.9029 | 0.28094 | 0.10143 | 2.7698 | 6.5109 | 1.7826 | 3.6525 | 6.5033 | 1.6852 | 3.859 | 6.5276 | 2.2203 | 2.94 | 3.2109 | 0.94628 | 3.3932 | 6.511 | 1.6112 | 4.041 | 6.5385 | 2.2936 | 2.8508 | 0.83095 | 0.24569 | 3.3821 | 0.85851 | 0.37385 | 2.2964 | 7.9496 | 2.1811 | 3.6448
[18 empty] | 02/09 11:00:00 | 5.4401 | 2.2635 | 2.4034 | 5.4125 | 1.592 | 3.3998 | 5.4048 | 1.4987 | 3.6063 | 0.31011 | 0.16293 | 1.9033 | 0.2825 | 0.10197 | 2.7705 | 6.5125 | 1.7828 | 3.6529 | 6.5048 | 1.6855 | 3.8593 | 6.5291 | 2.2205 | 2.9403 | 3.2125 | 0.94663 | 3.3936 | 6.5125 | 1.6113 | 4.0417 | 6.5401 | 2.2937 | 2.8514 | 0.83251 | 0.24618 | 3.3818 | 0.86012 | 0.37453 | 2.2965 | 7.9511 | 2.1813 | 3.6451
[18 empty] | 02/09 12:00:00 | 5.4406 | 2.2637 | 2.4034 | 5.413 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.31057 | 0.16318 | 1.9032 | 0.28302 | 0.10216 | 2.7704 | 6.513 | 1.7829 | 3.6531 | 6.5053 | 1.6855 | 3.8596 | 6.5296 | 2.2206 | 2.9405 | 3.213 | 0.94669 | 3.394 | 6.513 | 1.6114 | 4.0418 | 6.5406 | 2.2938 | 2.8515 | 0.83303 | 0.24597 | 3.3868 | 0.86057 | 0.37421 | 2.2997 | 7.9516 | 2.1813 | 3.6454
[18 empty] | 02/09 13:00:00 | 5.4403 | 2.2641 | 2.4029 | 5.413 | 1.5925 | 3.399 | 5.4053 | 1.4992 | 3.6056 | 0.31033 | 0.1631 | 1.9027 | 0.28299 | 0.10217 | 2.7697 | 6.513 | 1.7831 | 3.6527 | 6.5053 | 1.6857 | 3.8592 | 6.5295 | 2.2208 | 2.9401 | 3.213 | 0.94679 | 3.3936 | 6.513 | 1.6116 | 4.0413 | 6.5404 | 2.2941 | 2.851 | 0.83299 | 0.24568 | 3.3906 | 0.86034 | 0.37371 | 2.3021 | 7.9516 | 2.1815 | 3.6449
[18 empty] | 02/09 14:00:00 | 5.4402 | 2.2644 | 2.4025 | 5.4129 | 1.5928 | 3.3984 | 5.4053 | 1.4994 | 3.6049 | 0.31019 | 0.16306 | 1.9022 | 0.28293 | 0.10218 | 2.7689 | 6.513 | 1.7833 | 3.6521 | 6.5053 | 1.6859 | 3.8586 | 6.5294 | 2.2212 | 2.9396 | 3.213 | 0.94696 | 3.3929 | 6.513 | 1.6119 | 4.0406 | 6.5402 | 2.2945 | 2.8504 | 0.83294 | 0.24561 | 3.3913 | 0.86019 | 0.37367 | 2.302 | 7.9515 | 2.1819 | 3.6444
[18 empty] | 02/09 15:00:00 | 5.44 | 2.2645 | 2.4023 | 5.4127 | 1.5929 | 3.3981 | 5.4051 | 1.4995 | 3.6046 | 0.30998 | 0.16297 | 1.902 | 0.28274 | 0.10212 | 2.7687 | 6.5128 | 1.7835 | 3.6517 | 6.5052 | 1.6861 | 3.8582 | 6.5292 | 2.2213 | 2.9393 | 3.2128 | 0.947 | 3.3926 | 6.5128 | 1.6119 | 4.0405 | 6.54 | 2.2946 | 2.8502 | 0.83275 | 0.24547 | 3.3925 | 0.85999 | 0.37354 | 2.3023 | 7.9513 | 2.182 | 3.644
[18 empty] | 02/09 16:00:00 | 5.4395 | 2.2644 | 2.4022 | 5.4123 | 1.5927 | 3.3981 | 5.4047 | 1.4994 | 3.6046 | 0.3095 | 0.16273 | 1.902 | 0.28227 | 0.10195 | 2.7686 | 6.5123 | 1.7834 | 3.6516 | 6.5048 | 1.686 | 3.8581 | 6.5287 | 2.2212 | 2.9392 | 3.2123 | 0.94687 | 3.3926 | 6.5123 | 1.6117 | 4.0406 | 6.5396 | 2.2944 | 2.8502 | 0.83228 | 0.24517 | 3.3947 | 0.85951 | 0.37315 | 2.3034 | 7.9509 | 2.182 | 3.6439
[18 empty] | 02/09 17:00:00 | 5.4386 | 2.2641 | 2.4021 | 5.4113 | 1.5925 | 3.398 | 5.4038 | 1.4992 | 3.6045 | 0.3086 | 0.16226 | 1.9019 | 0.2813 | 0.10161 | 2.7685 | 6.5114 | 1.7832 | 3.6515 | 6.5038 | 1.6858 | 3.858 | 6.5277 | 2.221 | 2.9391 | 3.2113 | 0.94656 | 3.3927 | 6.5114 | 1.6114 | 4.0408 | 6.5386 | 2.294 | 2.8504 | 0.83131 | 0.24459 | 3.3988 | 0.85861 | 0.37244 | 2.3054 | 7.95 | 2.1818 | 3.6438
[18 empty] | 02/09 18:00:00 | 5.437 | 2.2636 | 2.402 | 5.4096 | 1.5921 | 3.3978 | 5.4021 | 1.4988 | 3.6043 | 0.307 | 0.16143 | 1.9017 | 0.27957 | 0.10099 | 2.7683 | 6.5096 | 1.7828 | 3.6514 | 6.5022 | 1.6855 | 3.8578 | 6.5261 | 2.2205 | 2.939 | 3.2096 | 0.94602 | 3.3928 | 6.5097 | 1.611 | 4.0409 | 6.5371 | 2.2934 | 2.8504 | 0.82959 | 0.24364 | 3.405 | 0.85701 | 0.37123 | 2.3086 | 7.9483 | 2.1814 | 3.6437
[18 empty] | 02/09 19:00:00 | 5.4356 | 2.2628 | 2.4021 | 5.408 | 1.5915 | 3.398 | 5.4007 | 1.4983 | 3.6045 | 0.30555 | 0.16066 | 1.9019 | 0.27799 | 0.10041 | 2.7685 | 6.5081 | 1.7824 | 3.6514 | 6.5008 | 1.6852 | 3.8577 | 6.5247 | 2.22 | 2.939 | 3.2081 | 0.94552 | 3.3929 | 6.5081 | 1.6105 | 4.0409 | 6.5356 | 2.2927 | 2.8506 | 0.82801 | 0.24305 | 3.4067 | 0.85556 | 0.37047 | 2.3094 | 7.9468 | 2.181 | 3.6437
[18 empty] | 02/09 20:00:00 | 5.4349 | 2.2624 | 2.4022 | 5.4074 | 1.5913 | 3.3981 | 5.4003 | 1.4981 | 3.6047 | 0.30488 | 0.16029 | 1.902 | 0.27744 | 0.10021 | 2.7687 | 6.5075 | 1.7821 | 3.6516 | 6.5004 | 1.685 | 3.8579 | 6.524 | 2.2196 | 2.9392 | 3.2075 | 0.94533 | 3.393 | 6.5076 | 1.6104 | 4.041 | 6.535 | 2.2924 | 2.8507 | 0.82746 | 0.24322 | 3.4022 | 0.85489 | 0.37047 | 2.3076 | 7.9462 | 2.1807 | 3.6439
[18 empty] | 02/09 21:00:00 | 5.4346 | 2.2624 | 2.4022 | 5.4071 | 1.5912 | 3.3981 | 5.4001 | 1.4981 | 3.6047 | 0.30461 | 0.16015 | 1.902 | 0.27715 | 0.1001 | 2.7687 | 6.5072 | 1.782 | 3.6516 | 6.5002 | 1.6849 | 3.858 | 6.5237 | 2.2195 | 2.9392 | 3.2072 | 0.94525 | 3.393 | 6.5073 | 1.6104 | 4.0409 | 6.5347 | 2.2924 | 2.8505 | 0.82716 | 0.24334 | 3.3992 | 0.85461 | 0.37063 | 2.3058 | 7.9459 | 2.1806 | 3.6439
[18 empty] | 02/09 22:00:00 | 5.4347 | 2.2624 | 2.4022 | 5.4071 | 1.5912 | 3.3981 | 5.4 | 1.498 | 3.6047 | 0.30468 | 0.16019 | 1.902 | 0.27713 | 0.10009 | 2.7687 | 6.5072 | 1.782 | 3.6516 | 6.5001 | 1.6848 | 3.858 | 6.5237 | 2.2195 | 2.9392 | 3.2072 | 0.94526 | 3.3929 | 6.5072 | 1.6104 | 4.0408 | 6.5347 | 2.2925 | 2.8505 | 0.82714 | 0.2435 | 3.3968 | 0.85468 | 0.37091 | 2.3043 | 7.9459 | 2.1806 | 3.6439
[18 empty] | 02/09 23:00:00 | 5.4347 | 2.2621 | 2.4025 | 5.4071 | 1.591 | 3.3985 | 5.3999 | 1.4978 | 3.6051 | 0.30473 | 0.16019 | 1.9023 | 0.27713 | 0.10008 | 2.7691 | 6.5072 | 1.7819 | 3.6518 | 6.5 | 1.6848 | 3.8581 | 6.5238 | 2.2194 | 2.9394 | 3.2072 | 0.94519 | 3.3932 | 6.5072 | 1.6102 | 4.0412 | 6.5348 | 2.2922 | 2.8509 | 0.82714 | 0.24353 | 3.3965 | 0.85474 | 0.37092 | 2.3044 | 7.9459 | 2.1805 | 3.6441
[18 empty] | 02/09 24:00:00 | 5.4347 | 2.262 | 2.4026 | 5.4071 | 1.5909 | 3.3987 | 5.3998 | 1.4977 | 3.6053 | 0.30468 | 0.16015 | 1.9025 | 0.27708 | 0.10005 | 2.7694 | 6.5071 | 1.7817 | 3.6521 | 6.4999 | 1.6846 | 3.8584 | 6.5237 | 2.2192 | 2.9397 | 3.2071 | 0.94507 | 3.3935 | 6.5072 | 1.6101 | 4.0415 | 6.5347 | 2.292 | 2.8511 | 0.82709 | 0.24349 | 3.3968 | 0.85469 | 0.37083 | 2.3048 | 7.9458 | 2.1803 | 3.6444
[18 empty] | 02/10 01:00:00 | 5.4346 | 2.2619 | 2.4026 | 5.407 | 1.5909 | 3.3987 | 5.3997 | 1.4977 | 3.6053 | 0.3046 | 0.16011 | 1.9025 | 0.27701 | 0.10003 | 2.7694 | 6.5071 | 1.7817 | 3.6522 | 6.4998 | 1.6845 | 3.8585 | 6.5237 | 2.2191 | 2.9397 | 3.207 | 0.94504 | 3.3936 | 6.5071 | 1.6101 | 4.0415 | 6.5347 | 2.292 | 2.8511 | 0.82702 | 0.24346 | 3.3969 | 0.85461 | 0.37077 | 2.305 | 7.9457 | 2.1802 | 3.6445
[18 empty] | 02/10 02:00:00 | 5.4345 | 2.2622 | 2.4023 | 5.4069 | 1.5911 | 3.3983 | 5.3996 | 1.4979 | 3.6049 | 0.3045 | 0.16008 | 1.9022 | 0.27692 | 0.10001 | 2.7689 | 6.507 | 1.7818 | 3.652 | 6.4997 | 1.6845 | 3.8584 | 6.5235 | 2.2192 | 2.9395 | 3.207 | 0.94508 | 3.3933 | 6.507 | 1.6102 | 4.041 | 6.5346 | 2.2922 | 2.8507 | 0.82693 | 0.24346 | 3.3966 | 0.85451 | 0.37076 | 2.3048 | 7.9456 | 2.1803 | 3.6443
[18 empty] | 02/10 03:00:00 | 5.4346 | 2.2623 | 2.4022 | 5.4069 | 1.5912 | 3.3981 | 5.3996 | 1.4979 | 3.6046 | 0.30455 | 0.16012 | 1.902 | 0.27693 | 0.10003 | 2.7686 | 6.507 | 1.7819 | 3.6516 | 6.4996 | 1.6847 | 3.8581 | 6.5236 | 2.2195 | 2.9393 | 3.207 | 0.94519 | 3.3929 | 6.507 | 1.6103 | 4.0408 | 6.5346 | 2.2924 | 2.8505 | 0.82694 | 0.24353 | 3.3957 | 0.85456 | 0.3709 | 2.304 | 7.9456 | 2.1805 | 3.644
[18 empty] | 02/10 04:00:00 | 5.4349 | 2.2622 | 2.4025 | 5.4072 | 1.5911 | 3.3985 | 5.3997 | 1.4978 | 3.6051 | 0.30494 | 0.1603 | 1.9023 | 0.27719 | 0.1001 | 2.7691 | 6.5072 | 1.7819 | 3.6518 | 6.4997 | 1.6847 | 3.8581 | 6.524 | 2.2195 | 2.9394 | 3.2072 | 0.94522 | 3.3931 | 6.5073 | 1.6103 | 4.0411 | 6.535 | 2.2924 | 2.8508 | 0.8272 | 0.24369 | 3.3945 | 0.85495 | 0.37124 | 2.303 | 7.9459 | 2.1805 | 3.6441
[18 empty] | 02/10 05:00:00 | 5.4356 | 2.2623 | 2.4027 | 5.4077 | 1.5911 | 3.3988 | 5.3999 | 1.4977 | 3.6053 | 0.3056 | 0.16062 | 1.9026 | 0.27767 | 0.10026 | 2.7694 | 6.5077 | 1.7819 | 3.6522 | 6.5 | 1.6846 | 3.8584 | 6.5246 | 2.2194 | 2.9397 | 3.2077 | 0.94527 | 3.3934 | 6.5077 | 1.6103 | 4.0413 | 6.5356 | 2.2924 | 2.851 | 0.82768 | 0.24394 | 3.3929 | 0.85561 | 0.37168 | 2.302 | 7.9464 | 2.1804 | 3.6445
[18 empty] | 02/10 06:00:00 | 5.4361 | 2.2624 | 2.4028 | 5.4081 | 1.5912 | 3.3988 | 5.4002 | 1.4978 | 3.6054 | 0.3061 | 0.16088 | 1.9026 | 0.27809 | 0.10041 | 2.7695 | 6.5081 | 1.7819 | 3.6523 | 6.5002 | 1.6846 | 3.8586 | 6.525 | 2.2195 | 2.9398 | 3.2081 | 0.94538 | 3.3935 | 6.5081 | 1.6104 | 4.0413 | 6.5361 | 2.2926 | 2.851 | 0.8281 | 0.24411 | 3.3924 | 0.85611 | 0.37192 | 2.3019 | 7.9468 | 2.1805 | 3.6446
[18 empty] | 02/10 07:00:00 | 5.4369 | 2.2627 | 2.4029 | 5.4087 | 1.5913 | 3.3989 | 5.4009 | 1.498 | 3.6055 | 0.30689 | 0.16129 | 1.9027 | 0.27873 | 0.10064 | 2.7696 | 6.5087 | 1.7821 | 3.6523 | 6.5008 | 1.6847 | 3.8588 | 6.5258 | 2.2197 | 2.9399 | 3.2087 | 0.94557 | 3.3935 | 6.5088 | 1.6106 | 4.0413 | 6.5369 | 2.2929 | 2.851 | 0.82873 | 0.24441 | 3.3908 | 0.8569 | 0.37244 | 2.3008 | 7.9475 | 2.1806 | 3.6446
[18 empty] | 02/10 08:00:00 | 5.4374 | 2.2626 | 2.4032 | 5.4093 | 1.5913 | 3.3994 | 5.4014 | 1.4979 | 3.6059 | 0.30738 | 0.16152 | 1.903 | 0.27929 | 0.10082 | 2.7701 | 6.5093 | 1.7821 | 3.6526 | 6.5013 | 1.6847 | 3.8589 | 6.5263 | 2.2197 | 2.9401 | 3.2093 | 0.94565 | 3.3938 | 6.5093 | 1.6105 | 4.0418 | 6.5374 | 2.2926 | 2.8515 | 0.82929 | 0.24455 | 3.3911 | 0.85738 | 0.37248 | 2.3019 | 7.9481 | 2.1806 | 3.6449
[18 empty] | 02/10 09:00:00 | 5.4376 | 2.2622 | 2.4036 | 5.4098 | 1.5911 | 3.4001 | 5.4021 | 1.4978 | 3.6067 | 0.30762 | 0.1616 | 1.9036 | 0.27983 | 0.10099 | 2.7709 | 6.5099 | 1.782 | 3.6532 | 6.5021 | 1.6847 | 3.8595 | 6.5266 | 2.2195 | 2.9406 | 3.2098 | 0.94564 | 3.3944 | 6.5099 | 1.6104 | 4.0424 | 6.5377 | 2.2923 | 2.852 | 0.82984 | 0.24469 | 3.3914 | 0.85763 | 0.37239 | 2.303 | 7.9484 | 2.1804 | 3.6454
[18 empty] | 02/10 10:00:00 | 5.4385 | 2.2624 | 2.4039 | 5.4108 | 1.5912 | 3.4004 | 5.4031 | 1.4979 | 3.6071 | 0.30849 | 0.16204 | 1.9038 | 0.28083 | 0.10134 | 2.7712 | 6.5108 | 1.782 | 3.6536 | 6.5032 | 1.6847 | 3.86 | 6.5275 | 2.2195 | 2.941 | 3.2108 | 0.94584 | 3.3947 | 6.5108 | 1.6106 | 4.0426 | 6.5385 | 2.2925 | 2.8521 | 0.83084 | 0.24519 | 3.3886 | 0.8585 | 0.37307 | 2.3012 | 7.9494 | 2.1804 | 3.6458
[18 empty] | 02/10 11:00:00 | 5.4399 | 2.2628 | 2.404 | 5.4122 | 1.5915 | 3.4006 | 5.4045 | 1.4982 | 3.6072 | 0.30994 | 0.16278 | 1.904 | 0.28222 | 0.10183 | 2.7714 | 6.5122 | 1.7823 | 3.6538 | 6.5045 | 1.685 | 3.8603 | 6.529 | 2.2199 | 2.9411 | 3.2122 | 0.94624 | 3.3947 | 6.5122 | 1.6109 | 4.0426 | 6.54 | 2.293 | 2.8522 | 0.83223 | 0.24585 | 3.3851 | 0.85995 | 0.3741 | 2.2987 | 7.9508 | 2.1807 | 3.646
[18 empty] | 02/10 12:00:00 | 5.4402 | 2.2632 | 2.4038 | 5.4126 | 1.5918 | 3.4003 | 5.4049 | 1.4985 | 3.6069 | 0.31019 | 0.16294 | 1.9037 | 0.28262 | 0.10199 | 2.771 | 6.5126 | 1.7825 | 3.6537 | 6.5049 | 1.6851 | 3.8602 | 6.5293 | 2.2201 | 2.941 | 3.2126 | 0.94636 | 3.3947 | 6.5127 | 1.6111 | 4.0424 | 6.5402 | 2.2932 | 2.852 | 0.83263 | 0.24568 | 3.389 | 0.8602 | 0.37377 | 2.3014 | 7.9512 | 2.1808 | 3.6459
[18 empty] | 02/10 13:00:00 | 5.4406 | 2.2637 | 2.4034 | 5.413 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.31057 | 0.16318 | 1.9032 | 0.28305 | 0.10217 | 2.7704 | 6.5131 | 1.7828 | 3.6532 | 6.5053 | 1.6854 | 3.8597 | 6.5297 | 2.2205 | 2.9406 | 3.2131 | 0.94666 | 3.3941 | 6.5131 | 1.6114 | 4.0418 | 6.5406 | 2.2938 | 2.8514 | 0.83305 | 0.24581 | 3.389 | 0.86058 | 0.37402 | 2.3009 | 7.9516 | 2.1812 | 3.6455
[18 empty] | 02/10 14:00:00 | 5.4409 | 2.264 | 2.4032 | 5.4133 | 1.5924 | 3.3995 | 5.4056 | 1.499 | 3.606 | 0.31092 | 0.16338 | 1.9031 | 0.28331 | 0.10227 | 2.7701 | 6.5133 | 1.7831 | 3.6529 | 6.5056 | 1.6857 | 3.8594 | 6.53 | 2.2208 | 2.9403 | 3.2133 | 0.94682 | 3.3938 | 6.5134 | 1.6116 | 4.0417 | 6.541 | 2.2941 | 2.8513 | 0.83331 | 0.24581 | 3.39 | 0.86093 | 0.37418 | 2.3009 | 7.9519 | 2.1815 | 3.6451
[18 empty] | 02/10 15:00:00 | 5.4408 | 2.2639 | 2.4032 | 5.4132 | 1.5924 | 3.3995 | 5.4056 | 1.4991 | 3.606 | 0.31078 | 0.16331 | 1.9031 | 0.28325 | 0.10225 | 2.7701 | 6.5133 | 1.7831 | 3.6529 | 6.5056 | 1.6857 | 3.8593 | 6.5299 | 2.2208 | 2.9403 | 3.2133 | 0.9468 | 3.3938 | 6.5133 | 1.6115 | 4.0418 | 6.5408 | 2.2939 | 2.8514 | 0.83325 | 0.24563 | 3.3924 | 0.86079 | 0.37384 | 2.3026 | 7.9519 | 2.1815 | 3.6451
[18 empty] | 02/10 16:00:00 | 5.4401 | 2.264 | 2.4029 | 5.4128 | 1.5925 | 3.399 | 5.4053 | 1.4992 | 3.6056 | 0.31015 | 0.163 | 1.9027 | 0.28277 | 0.1021 | 2.7696 | 6.5128 | 1.7831 | 3.6526 | 6.5053 | 1.6857 | 3.8591 | 6.5293 | 2.2208 | 2.9401 | 3.2128 | 0.94672 | 3.3936 | 6.5128 | 1.6115 | 4.0414 | 6.5402 | 2.294 | 2.851 | 0.83278 | 0.24531 | 3.3948 | 0.86015 | 0.37332 | 2.3041 | 7.9515 | 2.1816 | 3.6449
[18 empty] | 02/10 17:00:00 | 5.4398 | 2.2638 | 2.403 | 5.4122 | 1.5922 | 3.3991 | 5.4047 | 1.499 | 3.6057 | 0.30977 | 0.1628 | 1.9028 | 0.28219 | 0.10188 | 2.7697 | 6.5122 | 1.783 | 3.6524 | 6.5048 | 1.6857 | 3.8589 | 6.5288 | 2.2207 | 2.9399 | 3.2122 | 0.94656 | 3.3936 | 6.5123 | 1.6112 | 4.0418 | 6.5398 | 2.2937 | 2.8512 | 0.8322 | 0.24496 | 3.3973 | 0.85977 | 0.37311 | 2.3044 | 7.9509 | 2.1815 | 3.6447
[18 empty] | 02/10 18:00:00 | 5.4383 | 2.2631 | 2.403 | 5.4107 | 1.5918 | 3.3992 | 5.4032 | 1.4985 | 3.6057 | 0.30829 | 0.16201 | 1.9028 | 0.28066 | 0.10133 | 2.7698 | 6.5107 | 1.7825 | 3.6526 | 6.5032 | 1.6852 | 3.859 | 6.5274 | 2.2202 | 2.94 | 3.2107 | 0.946 | 3.394 | 6.5108 | 1.6108 | 4.042 | 6.5384 | 2.2929 | 2.8516 | 0.83067 | 0.24404 | 3.4038 | 0.85829 | 0.3718 | 2.3085 | 7.9494 | 2.181 | 3.6448
[18 empty] | 02/10 19:00:00 | 5.4372 | 2.2625 | 2.4032 | 5.4096 | 1.5913 | 3.3994 | 5.4022 | 1.4981 | 3.606 | 0.30718 | 0.16142 | 1.903 | 0.27964 | 0.10095 | 2.7701 | 6.5097 | 1.7822 | 3.6527 | 6.5023 | 1.685 | 3.859 | 6.5263 | 2.2197 | 2.9402 | 3.2097 | 0.94565 | 3.3942 | 6.5098 | 1.6104 | 4.0422 | 6.5372 | 2.2924 | 2.8517 | 0.82966 | 0.24375 | 3.4037 | 0.85719 | 0.37128 | 2.3087 | 7.9484 | 2.1807 | 3.6449
[18 empty] | 02/10 20:00:00 | 5.4367 | 2.2622 | 2.4033 | 5.4092 | 1.5911 | 3.3996 | 5.4018 | 1.4979 | 3.6062 | 0.30673 | 0.16117 | 1.9032 | 0.27916 | 0.10077 | 2.7703 | 6.5092 | 1.7819 | 3.6529 | 6.5019 | 1.6847 | 3.8593 | 6.5258 | 2.2194 | 2.9404 | 3.2092 | 0.94545 | 3.3944 | 6.5093 | 1.6103 | 4.0423 | 6.5368 | 2.2922 | 2.8518 | 0.82917 | 0.24379 | 3.4012 | 0.85674 | 0.37135 | 2.3071 | 7.9479 | 2.1804 | 3.6452
[18 empty] | 02/10 21:00:00 | 5.4364 | 2.2619 | 2.4035 | 5.4088 | 1.5908 | 3.4 | 5.4014 | 1.4976 | 3.6066 | 0.30643 | 0.16099 | 1.9034 | 0.2788 | 0.10062 | 2.7707 | 6.5089 | 1.7817 | 3.6532 | 6.5015 | 1.6846 | 3.8595 | 6.5255 | 2.2191 | 2.9405 | 3.2088 | 0.94527 | 3.3946 | 6.5089 | 1.6101 | 4.0427 | 6.5365 | 2.2918 | 2.8521 | 0.82881 | 0.24376 | 3.4001 | 0.85644 | 0.3713 | 2.3066 | 7.9476 | 2.1802 | 3.6454
[18 empty] | 02/10 22:00:00 | 5.4365 | 2.2617 | 2.4037 | 5.4087 | 1.5907 | 3.4002 | 5.4013 | 1.4975 | 3.6068 | 0.30648 | 0.161 | 1.9036 | 0.27873 | 0.10059 | 2.771 | 6.5088 | 1.7815 | 3.6535 | 6.5014 | 1.6844 | 3.8598 | 6.5255 | 2.2189 | 2.9408 | 3.2088 | 0.94518 | 3.3949 | 6.5088 | 1.61 | 4.0428 | 6.5365 | 2.2917 | 2.8523 | 0.82874 | 0.24387 | 3.3983 | 0.85648 | 0.37151 | 2.3054 | 7.9475 | 2.18 | 3.6457
[18 empty] | 02/10 23:00:00 | 5.4368 | 2.2618 | 2.4037 | 5.4089 | 1.5908 | 3.4002 | 5.4014 | 1.4975 | 3.6069 | 0.30676 | 0.16114 | 1.9037 | 0.27887 | 0.10064 | 2.771 | 6.5089 | 1.7815 | 3.6535 | 6.5014 | 1.6843 | 3.8599 | 6.5257 | 2.219 | 2.9409 | 3.2089 | 0.94521 | 3.3949 | 6.509 | 1.61 | 4.0427 | 6.5368 | 2.2918 | 2.8522 | 0.82888 | 0.24405 | 3.3964 | 0.85676 | 0.37181 | 2.3043 | 7.9476 | 2.18 | 3.6458
[18 empty] | 02/10 24:00:00 | 5.437 | 2.2619 | 2.4038 | 5.409 | 1.5908 | 3.4002 | 5.4015 | 1.4975 | 3.6069 | 0.307 | 0.16127 | 1.9037 | 0.27904 | 0.1007 | 2.771 | 6.5091 | 1.7816 | 3.6535 | 6.5015 | 1.6844 | 3.8599 | 6.5259 | 2.219 | 2.9409 | 3.2091 | 0.94526 | 3.3949 | 6.5091 | 1.6101 | 4.0427 | 6.5371 | 2.2919 | 2.8522 | 0.82905 | 0.24415 | 3.3956 | 0.85701 | 0.37197 | 2.304 | 7.9478 | 2.18 | 3.6458
[18 empty] | 02/11 01:00:00 | 5.4375 | 2.262 | 2.4038 | 5.4094 | 1.5909 | 3.4003 | 5.4017 | 1.4976 | 3.6069 | 0.30749 | 0.16152 | 1.9037 | 0.27939 | 0.10082 | 2.7711 | 6.5094 | 1.7817 | 3.6536 | 6.5017 | 1.6844 | 3.86 | 6.5264 | 2.2192 | 2.9409 | 3.2094 | 0.94537 | 3.3949 | 6.5095 | 1.6102 | 4.0427 | 6.5375 | 2.2921 | 2.8522 | 0.8294 | 0.24437 | 3.3941 | 0.8575 | 0.37235 | 2.3029 | 7.9482 | 2.1801 | 3.6458
[18 empty] | 02/11 02:00:00 | 5.4381 | 2.2623 | 2.4039 | 5.4099 | 1.591 | 3.4003 | 5.4021 | 1.4977 | 3.6069 | 0.30814 | 0.16185 | 1.9038 | 0.27988 | 0.101 | 2.7711 | 6.5099 | 1.7818 | 3.6536 | 6.5021 | 1.6845 | 3.86 | 6.527 | 2.2193 | 2.941 | 3.2099 | 0.94552 | 3.3949 | 6.5099 | 1.6103 | 4.0427 | 6.5382 | 2.2923 | 2.8522 | 0.82988 | 0.24461 | 3.3927 | 0.85815 | 0.37276 | 2.3021 | 7.9487 | 2.1802 | 3.6459
[18 empty] | 02/11 03:00:00 | 5.4385 | 2.2624 | 2.4039 | 5.4102 | 1.5911 | 3.4004 | 5.4024 | 1.4978 | 3.607 | 0.3085 | 0.16204 | 1.9038 | 0.28021 | 0.10112 | 2.7712 | 6.5102 | 1.7818 | 3.6537 | 6.5024 | 1.6845 | 3.86 | 6.5273 | 2.2194 | 2.941 | 3.2102 | 0.9456 | 3.3949 | 6.5103 | 1.6104 | 4.0428 | 6.5386 | 2.2924 | 2.8523 | 0.83022 | 0.24468 | 3.3931 | 0.85851 | 0.37283 | 2.3027 | 7.9491 | 2.1803 | 3.6459
[18 empty] | 02/11 04:00:00 | 5.4387 | 2.2624 | 2.4039 | 5.4104 | 1.5911 | 3.4004 | 5.4026 | 1.4978 | 3.607 | 0.30867 | 0.16213 | 1.9038 | 0.2804 | 0.10118 | 2.7712 | 6.5104 | 1.7819 | 3.6537 | 6.5026 | 1.6846 | 3.8601 | 6.5275 | 2.2195 | 2.941 | 3.2104 | 0.94565 | 3.395 | 6.5105 | 1.6104 | 4.0428 | 6.5387 | 2.2924 | 2.8523 | 0.83041 | 0.24468 | 3.3939 | 0.85868 | 0.37279 | 2.3034 | 7.9493 | 2.1803 | 3.6459
[18 empty] | 02/11 05:00:00 | 5.4387 | 2.2622 | 2.4042 | 5.4105 | 1.591 | 3.4008 | 5.4028 | 1.4977 | 3.6074 | 0.30875 | 0.16214 | 1.9042 | 0.28051 | 0.10121 | 2.7716 | 6.5105 | 1.7818 | 3.6539 | 6.5028 | 1.6846 | 3.8602 | 6.5276 | 2.2194 | 2.9412 | 3.2105 | 0.9456 | 3.3952 | 6.5106 | 1.6102 | 4.0432 | 6.5388 | 2.2921 | 2.8527 | 0.83051 | 0.24462 | 3.3951 | 0.85876 | 0.37269 | 2.3042 | 7.9494 | 2.1802 | 3.6461
[18 empty] | 02/11 06:00:00 | 5.4388 | 2.2621 | 2.4044 | 5.4106 | 1.5909 | 3.401 | 5.4029 | 1.4976 | 3.6077 | 0.30881 | 0.16216 | 1.9043 | 0.28058 | 0.10122 | 2.7719 | 6.5106 | 1.7817 | 3.6542 | 6.5029 | 1.6844 | 3.8606 | 6.5277 | 2.2192 | 2.9415 | 3.2106 | 0.94552 | 3.3956 | 6.5106 | 1.6102 | 4.0435 | 6.5389 | 2.292 | 2.8529 | 0.83059 | 0.2446 | 3.3957 | 0.85881 | 0.37265 | 2.3046 | 7.9495 | 2.1801 | 3.6464
[18 empty] | 02/11 07:00:00 | 5.4388 | 2.2621 | 2.4044 | 5.4106 | 1.5909 | 3.401 | 5.403 | 1.4976 | 3.6077 | 0.30884 | 0.16218 | 1.9043 | 0.28063 | 0.10124 | 2.7719 | 6.5107 | 1.7816 | 3.6543 | 6.503 | 1.6844 | 3.8607 | 6.5277 | 2.2191 | 2.9415 | 3.2107 | 0.94552 | 3.3957 | 6.5107 | 1.6102 | 4.0435 | 6.5389 | 2.292 | 2.8529 | 0.83064 | 0.2446 | 3.3959 | 0.85885 | 0.37265 | 2.3047 | 7.9495 | 2.18 | 3.6465
[18 empty] | 02/11 08:00:00 | 5.4389 | 2.2618 | 2.4047 | 5.4107 | 1.5907 | 3.4015 | 5.4031 | 1.4975 | 3.6081 | 0.30895 | 0.16221 | 1.9047 | 0.28074 | 0.10126 | 2.7724 | 6.5108 | 1.7816 | 3.6545 | 6.5031 | 1.6844 | 3.8608 | 6.5278 | 2.219 | 2.9417 | 3.2108 | 0.94548 | 3.3959 | 6.5108 | 1.61 | 4.0439 | 6.539 | 2.2918 | 2.8533 | 0.83075 | 0.24462 | 3.396 | 0.85895 | 0.37268 | 2.3048 | 7.9496 | 2.18 | 3.6467
[18 empty] | 02/11 09:00:00 | 5.4393 | 2.2619 | 2.4047 | 5.4111 | 1.5907 | 3.4016 | 5.4034 | 1.4975 | 3.6084 | 0.3093 | 0.16237 | 1.9049 | 0.28107 | 0.10137 | 2.7728 | 6.5111 | 1.7874 | 3.6428 | 6.5034 | 1.6903 | 3.8476 | 6.5282 | 2.2274 | 2.9309 | 3.2111 | 0.95027 | 3.3792 | 6.5111 | 1.6195 | 4.0206 | 6.5394 | 2.3074 | 2.8341 | 0.83108 | 0.24796 | 3.3517 | 0.85931 | 0.37833 | 2.2713 | 7.95 | 2.188 | 3.6334
[18 empty] | 02/11 10:00:00 | 5.4401 | 2.2621 | 2.4048 | 5.4121 | 1.5909 | 3.4018 | 5.4043 | 1.4976 | 3.6086 | 0.31008 | 0.16277 | 1.9051 | 0.28206 | 0.10172 | 2.773 | 6.5121 | 1.7834 | 3.6515 | 6.5042 | 1.6862 | 3.8574 | 6.5289 | 2.2216 | 2.9388 | 3.2121 | 0.94712 | 3.3914 | 6.5121 | 1.6112 | 4.0417 | 6.5401 | 2.294 | 2.851 | 0.83206 | 0.24659 | 3.3742 | 0.86008 | 0.37544 | 2.2908 | 7.9508 | 2.1823 | 3.6434
[18 empty] | 02/11 11:00:00 | 5.4407 | 2.2625 | 2.4048 | 5.4126 | 1.5912 | 3.4017 | 5.4049 | 1.4978 | 3.6084 | 0.31072 | 0.16311 | 1.905 | 0.28265 | 0.10193 | 2.7729 | 6.5127 | 1.7833 | 3.652 | 6.5048 | 1.6859 | 3.8584 | 6.5296 | 2.2214 | 2.9394 | 3.2127 | 0.94693 | 3.3927 | 6.5127 | 1.6119 | 4.0405 | 6.5408 | 2.295 | 2.85 | 0.83265 | 0.24604 | 3.3843 | 0.86073 | 0.37469 | 2.2972 | 7.9514 | 2.182 | 3.6441
[18 empty] | 02/11 12:00:00 | 5.441 | 2.2626 | 2.4048 | 5.4129 | 1.5912 | 3.4017 | 5.4052 | 1.4979 | 3.6085 | 0.31103 | 0.16327 | 1.905 | 0.28294 | 0.10204 | 2.7729 | 6.513 | 1.7835 | 3.6519 | 6.5051 | 1.686 | 3.8582 | 6.5299 | 2.2216 | 2.9393 | 3.213 | 0.94705 | 3.3926 | 6.513 | 1.6119 | 4.0405 | 6.5411 | 2.2951 | 2.85 | 0.83295 | 0.24588 | 3.3876 | 0.86104 | 0.37453 | 2.2989 | 7.9517 | 2.1821 | 3.644
[18 empty] | 02/11 13:00:00 | 5.4414 | 2.2627 | 2.4048 | 5.4133 | 1.5913 | 3.4017 | 5.4055 | 1.498 | 3.6085 | 0.31141 | 0.16347 | 1.905 | 0.28331 | 0.10217 | 2.7729 | 6.5133 | 1.7836 | 3.6519 | 6.5055 | 1.6861 | 3.8583 | 6.5303 | 2.2217 | 2.9393 | 3.2133 | 0.94716 | 3.3926 | 6.5134 | 1.6121 | 4.0404 | 6.5415 | 2.2953 | 2.8499 | 0.83332 | 0.24596 | 3.388 | 0.86142 | 0.37468 | 2.2991 | 7.9521 | 2.1822 | 3.644
[18 empty] | 02/11 14:00:00 | 5.4416 | 2.2628 | 2.4048 | 5.4136 | 1.5914 | 3.4017 | 5.4058 | 1.4981 | 3.6083 | 0.31162 | 0.16359 | 1.9049 | 0.28356 | 0.10227 | 2.7726 | 6.5135 | 1.7787 | 3.6619 | 6.5058 | 1.6813 | 3.8696 | 6.5305 | 2.2148 | 2.9486 | 3.2136 | 0.94331 | 3.4067 | 6.5136 | 1.6036 | 4.062 | 6.5417 | 2.2814 | 2.8674 | 0.83356 | 0.24355 | 3.4225 | 0.86162 | 0.37045 | 2.3259 | 7.9523 | 2.1755 | 3.6553
[18 empty] | 02/11 15:00:00 | 5.4416 | 2.263 | 2.4046 | 5.4136 | 1.5916 | 3.4014 | 5.4059 | 1.4983 | 3.6081 | 0.31165 | 0.16363 | 1.9046 | 0.28363 | 0.10231 | 2.7723 | 6.5137 | 1.7817 | 3.6558 | 6.506 | 1.6842 | 3.863 | 6.5306 | 2.2189 | 2.9431 | 3.2137 | 0.94568 | 3.3983 | 6.5137 | 1.6112 | 4.0428 | 6.5417 | 2.2932 | 2.8526 | 0.83364 | 0.24449 | 3.4097 | 0.86166 | 0.37229 | 2.3145 | 7.9525 | 2.1797 | 3.6484
[18 empty] | 02/11 16:00:00 | 5.4414 | 2.2629 | 2.4046 | 5.4134 | 1.5915 | 3.4014 | 5.4058 | 1.4983 | 3.608 | 0.3114 | 0.1635 | 1.9046 | 0.28344 | 0.10224 | 2.7723 | 6.5135 | 1.7822 | 3.6547 | 6.5059 | 1.6849 | 3.8612 | 6.5304 | 2.2198 | 2.9419 | 3.2135 | 0.94622 | 3.3961 | 6.5135 | 1.6108 | 4.0437 | 6.5415 | 2.2928 | 2.8531 | 0.83345 | 0.24508 | 3.4007 | 0.86141 | 0.37328 | 2.3077 | 7.9523 | 2.1805 | 3.6469
[18 empty] | 02/11 17:00:00 | 5.4408 | 2.2627 | 2.4046 | 5.4129 | 1.5914 | 3.4013 | 5.4054 | 1.4982 | 3.608 | 0.31082 | 0.1632 | 1.9045 | 0.28293 | 0.10206 | 2.7722 | 6.513 | 1.7821 | 3.6546 | 6.5054 | 1.6849 | 3.861 | 6.5298 | 2.2197 | 2.9418 | 3.213 | 0.94612 | 3.3959 | 6.513 | 1.6106 | 4.0438 | 6.5409 | 2.2925 | 2.8531 | 0.83294 | 0.24499 | 3.3998 | 0.86082 | 0.37313 | 2.3071 | 7.9518 | 2.1805 | 3.6467
[18 empty] | 02/11 18:00:00 | 5.4394 | 2.2622 | 2.4044 | 5.4116 | 1.5911 | 3.4012 | 5.4041 | 1.4979 | 3.6078 | 0.30941 | 0.16247 | 1.9044 | 0.28163 | 0.1016 | 2.7721 | 6.5117 | 1.7818 | 3.6545 | 6.5042 | 1.6846 | 3.8609 | 6.5284 | 2.2193 | 2.9417 | 3.2117 | 0.9457 | 3.3961 | 6.5117 | 1.6102 | 4.0441 | 6.5395 | 2.2919 | 2.8534 | 0.83165 | 0.24426 | 3.4048 | 0.85942 | 0.37203 | 2.3101 | 7.9504 | 2.1802 | 3.6466
[18 empty] | 02/11 19:00:00 | 5.4378 | 2.2617 | 2.4043 | 5.4101 | 1.5907 | 3.401 | 5.4026 | 1.4975 | 3.6077 | 0.30782 | 0.16165 | 1.9042 | 0.28008 | 0.10105 | 2.7719 | 6.5102 | 1.7815 | 3.6543 | 6.5028 | 1.6844 | 3.8607 | 6.5269 | 2.2189 | 2.9415 | 3.2101 | 0.94527 | 3.396 | 6.5102 | 1.6099 | 4.0438 | 6.5379 | 2.2915 | 2.8531 | 0.8301 | 0.2436 | 3.4076 | 0.85783 | 0.37113 | 2.3114 | 7.9489 | 2.1799 | 3.6465
[18 empty] | 02/11 20:00:00 | 5.4371 | 2.2612 | 2.4045 | 5.4094 | 1.5904 | 3.4013 | 5.4019 | 1.4972 | 3.608 | 0.30709 | 0.16125 | 1.9045 | 0.27936 | 0.10077 | 2.7722 | 6.5094 | 1.7813 | 3.6544 | 6.502 | 1.6841 | 3.8607 | 6.5261 | 2.2186 | 2.9416 | 3.2094 | 0.94503 | 3.3961 | 6.5095 | 1.6096 | 4.0442 | 6.5372 | 2.291 | 2.8534 | 0.82938 | 0.24356 | 3.4053 | 0.8571 | 0.37104 | 2.31 | 7.9482 | 2.1796 | 3.6466
[18 empty] | 02/11 21:00:00 | 5.4361 | 2.2609 | 2.4043 | 5.4085 | 1.5902 | 3.4011 | 5.4011 | 1.497 | 3.608 | 0.30607 | 0.16071 | 1.9045 | 0.27846 | 0.10044 | 2.7723 | 6.5086 | 1.7858 | 3.6446 | 6.5013 | 1.6887 | 3.8498 | 6.5252 | 2.225 | 2.9326 | 3.2085 | 0.94859 | 3.3824 | 6.5086 | 1.618 | 4.0225 | 6.5361 | 2.3047 | 2.836 | 0.82847 | 0.24574 | 3.3713 | 0.85608 | 0.37473 | 2.2846 | 7.9473 | 2.186 | 3.6356
[18 empty] | 02/11 22:00:00 | 5.4356 | 2.2608 | 2.4043 | 5.408 | 1.5901 | 3.4011 | 5.4008 | 1.4969 | 3.6079 | 0.30562 | 0.16047 | 1.9045 | 0.27805 | 0.1003 | 2.7723 | 6.5081 | 1.783 | 3.6501 | 6.5009 | 1.6861 | 3.8557 | 6.5247 | 2.2212 | 2.9374 | 3.2081 | 0.94636 | 3.3899 | 6.5082 | 1.6105 | 4.0411 | 6.5357 | 2.293 | 2.8503 | 0.82806 | 0.24484 | 3.3821 | 0.85562 | 0.37297 | 2.2941 | 7.9468 | 2.1821 | 3.6418
[18 empty] | 02/11 23:00:00 | 5.4352 | 2.2607 | 2.4042 | 5.4075 | 1.59 | 3.401 | 5.4003 | 1.4968 | 3.6079 | 0.30515 | 0.16023 | 1.9044 | 0.27754 | 0.10012 | 2.7722 | 6.5076 | 1.7823 | 3.6512 | 6.5004 | 1.6852 | 3.8574 | 6.5242 | 2.2201 | 2.9387 | 3.2076 | 0.94555 | 3.3923 | 6.5076 | 1.6106 | 4.0406 | 6.5352 | 2.2931 | 2.85 | 0.82755 | 0.24382 | 3.3941 | 0.85516 | 0.37142 | 2.3024 | 7.9463 | 2.181 | 3.6433
[18 empty] | 02/11 24:00:00 | 5.4346 | 2.2605 | 2.4042 | 5.4068 | 1.5898 | 3.4009 | 5.3994 | 1.4966 | 3.6078 | 0.30463 | 0.15996 | 1.9044 | 0.27683 | 0.099863 | 2.7721 | 6.5069 | 1.7821 | 3.6512 | 6.4996 | 1.6849 | 3.8575 | 6.5236 | 2.2199 | 2.9387 | 3.2069 | 0.94528 | 3.3925 | 6.5069 | 1.6105 | 4.0403 | 6.5347 | 2.293 | 2.8498 | 0.82685 | 0.24331 | 3.3983 | 0.85464 | 0.37087 | 2.3044 | 7.9456 | 2.1808 | 3.6434
[18 empty] | 02/12 01:00:00 | 5.4349 | 2.2606 | 2.4042 | 5.4071 | 1.5899 | 3.401 | 5.3996 | 1.4966 | 3.6078 | 0.30495 | 0.16013 | 1.9044 | 0.27711 | 0.09996 | 2.7722 | 6.5072 | 1.7822 | 3.6512 | 6.4997 | 1.6849 | 3.8575 | 6.5239 | 2.22 | 2.9387 | 3.2071 | 0.94539 | 3.3924 | 6.5072 | 1.6106 | 4.0402 | 6.535 | 2.2932 | 2.8498 | 0.82712 | 0.24366 | 3.3945 | 0.85495 | 0.3713 | 2.3026 | 7.9459 | 2.1809 | 3.6434
[18 empty] | 02/12 02:00:00 | 5.435 | 2.2606 | 2.4042 | 5.4072 | 1.5899 | 3.401 | 5.3996 | 1.4967 | 3.6078 | 0.30504 | 0.16018 | 1.9044 | 0.27723 | 0.1 | 2.7722 | 6.5073 | 1.7822 | 3.6512 | 6.4997 | 1.6849 | 3.8575 | 6.524 | 2.22 | 2.9388 | 3.2073 | 0.94542 | 3.3924 | 6.5073 | 1.6106 | 4.0402 | 6.5351 | 2.2932 | 2.8498 | 0.82724 | 0.24373 | 3.3941 | 0.85505 | 0.37133 | 2.3027 | 7.946 | 2.1809 | 3.6434
[18 empty] | 02/12 03:00:00 | 5.4352 | 2.2607 | 2.4042 | 5.4074 | 1.5899 | 3.401 | 5.3997 | 1.4967 | 3.6078 | 0.30517 | 0.16024 | 1.9044 | 0.27736 | 0.10005 | 2.7722 | 6.5074 | 1.7822 | 3.6512 | 6.4998 | 1.685 | 3.8575 | 6.5242 | 2.22 | 2.9388 | 3.2074 | 0.94546 | 3.3924 | 6.5074 | 1.6106 | 4.0403 | 6.5352 | 2.2932 | 2.8498 | 0.82737 | 0.24378 | 3.3939 | 0.85518 | 0.37139 | 2.3027 | 7.9461 | 2.1809 | 3.6435
[18 empty] | 02/12 04:00:00 | 5.4351 | 2.2606 | 2.4042 | 5.4073 | 1.5899 | 3.401 | 5.3997 | 1.4967 | 3.6078 | 0.30509 | 0.1602 | 1.9044 | 0.27733 | 0.10004 | 2.7722 | 6.5074 | 1.7822 | 3.6512 | 6.4998 | 1.685 | 3.8575 | 6.5241 | 2.22 | 2.9388 | 3.2074 | 0.94544 | 3.3925 | 6.5074 | 1.6106 | 4.0403 | 6.5351 | 2.2932 | 2.8498 | 0.82734 | 0.24372 | 3.3947 | 0.8551 | 0.37125 | 2.3033 | 7.9461 | 2.1809 | 3.6435
[18 empty] | 02/12 05:00:00 | 5.4349 | 2.2605 | 2.4043 | 5.4073 | 1.5899 | 3.4011 | 5.3997 | 1.4967 | 3.6078 | 0.30494 | 0.16013 | 1.9044 | 0.27725 | 0.10001 | 2.7721 | 6.5073 | 1.7783 | 3.6593 | 6.4997 | 1.681 | 3.8665 | 6.5239 | 2.2144 | 2.9462 | 3.2073 | 0.94232 | 3.4036 | 6.5073 | 1.6024 | 4.061 | 6.535 | 2.2798 | 2.8665 | 0.82726 | 0.24182 | 3.421 | 0.85495 | 0.36793 | 2.3237 | 7.9459 | 2.1755 | 3.6525
[18 empty] | 02/12 06:00:00 | 5.4345 | 2.2602 | 2.4044 | 5.407 | 1.5897 | 3.4012 | 5.3995 | 1.4966 | 3.608 | 0.30452 | 0.1599 | 1.9044 | 0.27696 | 0.099908 | 2.7722 | 6.507 | 1.7795 | 3.6567 | 6.4996 | 1.682 | 3.8641 | 6.5236 | 2.2159 | 2.944 | 3.207 | 0.94306 | 3.4006 | 6.5071 | 1.6093 | 4.0433 | 6.5346 | 2.2903 | 2.8531 | 0.82697 | 0.24157 | 3.4233 | 0.85453 | 0.36767 | 2.3242 | 7.9457 | 2.1771 | 3.6496
[18 empty] | 02/12 07:00:00 | 5.4343 | 2.2604 | 2.4042 | 5.4068 | 1.5898 | 3.4009 | 5.3994 | 1.4966 | 3.6077 | 0.3043 | 0.15979 | 1.9043 | 0.27677 | 0.099842 | 2.7721 | 6.5069 | 1.7853 | 3.6447 | 6.4994 | 1.6881 | 3.8501 | 6.5234 | 2.2244 | 2.9327 | 3.2068 | 0.948 | 3.3827 | 6.5069 | 1.6177 | 4.0224 | 6.5344 | 2.3042 | 2.8358 | 0.82678 | 0.2451 | 3.3732 | 0.85431 | 0.3737 | 2.2861 | 7.9455 | 2.1854 | 3.6358
[18 empty] | 02/12 08:00:00 | 5.4349 | 2.2604 | 2.4044 | 5.4073 | 1.5897 | 3.4013 | 5.3997 | 1.4965 | 3.6082 | 0.30492 | 0.16009 | 1.9047 | 0.27726 | 0.1 | 2.7726 | 6.5073 | 1.7832 | 3.6493 | 6.4997 | 1.6862 | 3.8547 | 6.524 | 2.2215 | 2.9367 | 3.2073 | 0.94645 | 3.3888 | 6.5073 | 1.6111 | 4.0391 | 6.535 | 2.294 | 2.8487 | 0.82727 | 0.24511 | 3.3751 | 0.85493 | 0.37346 | 2.2892 | 7.946 | 2.1824 | 3.6408
[18 empty] | 02/12 09:00:00 | 5.4364 | 2.2607 | 2.4047 | 5.4088 | 1.59 | 3.4017 | 5.4011 | 1.4967 | 3.6085 | 0.30643 | 0.16086 | 1.905 | 0.27881 | 0.10054 | 2.773 | 6.5088 | 1.7827 | 3.6512 | 6.501 | 1.6854 | 3.8572 | 6.5257 | 2.2207 | 2.9386 | 3.2088 | 0.94612 | 3.3915 | 6.5088 | 1.6111 | 4.0399 | 6.5365 | 2.2938 | 2.8496 | 0.82881 | 0.24533 | 3.3783 | 0.85644 | 0.37343 | 2.2934 | 7.9475 | 2.1815 | 3.6432
[18 empty] | 02/12 10:00:00 | 5.4379 | 2.2612 | 2.4049 | 5.4105 | 1.5904 | 3.4019 | 5.4027 | 1.4971 | 3.6087 | 0.30794 | 0.16164 | 1.9051 | 0.2805 | 0.10115 | 2.7732 | 6.5105 | 1.7829 | 3.6517 | 6.5026 | 1.6855 | 3.8581 | 6.5269 | 2.2207 | 2.9391 | 3.2105 | 0.94641 | 3.3923 | 6.5105 | 1.6114 | 4.0402 | 6.538 | 2.2942 | 2.8498 | 0.83051 | 0.24574 | 3.3796 | 0.85795 | 0.37381 | 2.2952 | 7.9491 | 2.1815 | 3.6438
[18 empty] | 02/12 11:00:00 | 5.4388 | 2.2615 | 2.405 | 5.4115 | 1.5907 | 3.4021 | 5.4038 | 1.4974 | 3.6089 | 0.30875 | 0.16206 | 1.9052 | 0.28154 | 0.10152 | 2.7733 | 6.5115 | 1.7831 | 3.6519 | 6.5037 | 1.6857 | 3.8582 | 6.5278 | 2.2209 | 2.9392 | 3.2115 | 0.94665 | 3.3925 | 6.5116 | 1.6116 | 4.0403 | 6.5388 | 2.2944 | 2.8499 | 0.83155 | 0.24581 | 3.3829 | 0.85876 | 0.37377 | 2.2976 | 7.9499 | 2.1817 | 3.644
[18 empty] | 02/12 12:00:00 | 5.4394 | 2.2617 | 2.405 | 5.4122 | 1.5908 | 3.4021 | 5.4045 | 1.4975 | 3.609 | 0.30942 | 0.1624 | 1.9053 | 0.28219 | 0.10175 | 2.7734 | 6.5122 | 1.7832 | 3.6519 | 6.5045 | 1.6858 | 3.8583 | 6.5285 | 2.2211 | 2.9393 | 3.2122 | 0.9468 | 3.3927 | 6.5122 | 1.6117 | 4.0405 | 6.5395 | 2.2946 | 2.85 | 0.83219 | 0.24579 | 3.3858 | 0.85942 | 0.3739 | 2.2985 | 7.9506 | 2.1818 | 3.644
[18 empty] | 02/12 13:00:00 | 5.4399 | 2.2621 | 2.4048 | 5.4126 | 1.5911 | 3.4019 | 5.4049 | 1.4978 | 3.6086 | 0.30985 | 0.16265 | 1.905 | 0.28259 | 0.10191 | 2.7731 | 6.5126 | 1.783 | 3.6527 | 6.5049 | 1.6855 | 3.8592 | 6.529 | 2.2208 | 2.94 | 3.2126 | 0.94663 | 3.3937 | 6.5126 | 1.6112 | 4.0422 | 6.5399 | 2.2936 | 2.8513 | 0.8326 | 0.24559 | 3.3902 | 0.85986 | 0.37365 | 2.3013 | 7.951 | 2.1814 | 3.6449
[18 empty] | 02/12 14:00:00 | 5.4401 | 2.2622 | 2.4048 | 5.4128 | 1.5912 | 3.4017 | 5.4051 | 1.4979 | 3.6085 | 0.31012 | 0.16281 | 1.9049 | 0.28284 | 0.10201 | 2.7728 | 6.5128 | 1.7794 | 3.6602 | 6.5051 | 1.682 | 3.8675 | 6.5292 | 2.2156 | 2.9469 | 3.2128 | 0.9438 | 3.4042 | 6.5129 | 1.6037 | 4.0612 | 6.5402 | 2.2815 | 2.8666 | 0.83285 | 0.24381 | 3.416 | 0.86013 | 0.37059 | 2.321 | 7.9513 | 2.1764 | 3.6534
[18 empty] | 02/12 15:00:00 | 5.44 | 2.262 | 2.4049 | 5.4128 | 1.5911 | 3.4019 | 5.4051 | 1.4978 | 3.6086 | 0.31 | 0.16274 | 1.9049 | 0.2828 | 0.10199 | 2.7729 | 6.5128 | 1.7808 | 3.6574 | 6.5052 | 1.6832 | 3.8648 | 6.5292 | 2.2174 | 2.9445 | 3.2128 | 0.94472 | 3.4008 | 6.5129 | 1.6107 | 4.0435 | 6.5401 | 2.2921 | 2.8533 | 0.83281 | 0.24368 | 3.4176 | 0.86001 | 0.37056 | 2.3209 | 7.9513 | 2.1783 | 3.6502
[18 empty] | 02/12 16:00:00 | 5.4397 | 2.2619 | 2.4049 | 5.4126 | 1.591 | 3.4019 | 5.405 | 1.4978 | 3.6086 | 0.30969 | 0.16257 | 1.9049 | 0.28256 | 0.1019 | 2.7729 | 6.5126 | 1.7817 | 3.6553 | 6.505 | 1.6844 | 3.8619 | 6.5289 | 2.2189 | 2.9424 | 3.2126 | 0.94573 | 3.397 | 6.5126 | 1.6103 | 4.0444 | 6.5398 | 2.2917 | 2.8537 | 0.83257 | 0.24457 | 3.4042 | 0.8597 | 0.37209 | 2.3105 | 7.9511 | 2.1799 | 3.6475
[18 empty] | 02/12 17:00:00 | 5.4389 | 2.2617 | 2.4048 | 5.4118 | 1.5908 | 3.4018 | 5.4042 | 1.4976 | 3.6085 | 0.30888 | 0.16216 | 1.9048 | 0.28176 | 0.10162 | 2.7728 | 6.5118 | 1.7816 | 3.655 | 6.5043 | 1.6844 | 3.8615 | 6.5281 | 2.2188 | 2.9421 | 3.2118 | 0.94558 | 3.3967 | 6.5118 | 1.61 | 4.0445 | 6.5389 | 2.2914 | 2.8538 | 0.83177 | 0.24436 | 3.4039 | 0.85889 | 0.37187 | 2.3097 | 7.9503 | 2.1799 | 3.6472
[18 empty] | 02/12 18:00:00 | 5.4373 | 2.2612 | 2.4047 | 5.4101 | 1.5904 | 3.4016 | 5.4026 | 1.4973 | 3.6083 | 0.30733 | 0.16135 | 1.9047 | 0.28005 | 0.10101 | 2.7726 | 6.5101 | 1.7812 | 3.6549 | 6.5027 | 1.6841 | 3.8613 | 6.5265 | 2.2184 | 2.942 | 3.2101 | 0.94505 | 3.3967 | 6.5102 | 1.6096 | 4.0446 | 6.5374 | 2.2908 | 2.8538 | 0.83006 | 0.24347 | 3.4093 | 0.85734 | 0.37081 | 2.312 | 7.9487 | 2.1795 | 3.647
[18 empty] | 02/12 19:00:00 | 5.4361 | 2.261 | 2.4043 | 5.4087 | 1.5903 | 3.4012 | 5.4014 | 1.4971 | 3.608 | 0.30613 | 0.16074 | 1.9045 | 0.27875 | 0.10055 | 2.7723 | 6.5089 | 1.7858 | 3.6447 | 6.5015 | 1.6887 | 3.8499 | 6.5253 | 2.225 | 2.9327 | 3.2088 | 0.94863 | 3.3826 | 6.5089 | 1.6181 | 4.0226 | 6.5362 | 2.3047 | 2.836 | 0.82876 | 0.24559 | 3.3745 | 0.85615 | 0.3746 | 2.2855 | 7.9475 | 2.186 | 3.6357
[18 empty] | 02/12 20:00:00 | 5.4357 | 2.2608 | 2.4043 | 5.4083 | 1.5901 | 3.4011 | 5.401 | 1.497 | 3.608 | 0.30573 | 0.16053 | 1.9045 | 0.27827 | 0.10037 | 2.7723 | 6.5083 | 1.7831 | 3.6501 | 6.5011 | 1.6861 | 3.8557 | 6.5248 | 2.2213 | 2.9374 | 3.2083 | 0.94641 | 3.39 | 6.5084 | 1.6105 | 4.0411 | 6.5358 | 2.293 | 2.8503 | 0.82828 | 0.2448 | 3.3835 | 0.85574 | 0.373 | 2.2942 | 7.947 | 2.1822 | 3.6418
[18 empty] | 02/12 21:00:00 | 5.4346 | 2.2605 | 2.4042 | 5.407 | 1.5899 | 3.401 | 5.3997 | 1.4967 | 3.6078 | 0.30457 | 0.15993 | 1.9044 | 0.27703 | 0.099934 | 2.7722 | 6.5071 | 1.7822 | 3.6512 | 6.4999 | 1.6851 | 3.8574 | 6.5237 | 2.22 | 2.9386 | 3.2071 | 0.94535 | 3.3925 | 6.5071 | 1.6103 | 4.0409 | 6.5346 | 2.2927 | 2.8502 | 0.82704 | 0.2433 | 3.3993 | 0.85457 | 0.37071 | 2.3052 | 7.9458 | 2.1809 | 3.6433
[18 empty] | 02/12 22:00:00 | 5.4327 | 2.2596 | 2.4042 | 5.4053 | 1.5893 | 3.4011 | 5.3975 | 1.496 | 3.6079 | 0.30271 | 0.15895 | 1.9045 | 0.27533 | 0.099313 | 2.7723 | 6.5054 | 1.7821 | 3.6504 | 6.4973 | 1.6846 | 3.8568 | 6.5219 | 2.2199 | 2.938 | 3.2054 | 0.94507 | 3.3917 | 6.5055 | 1.6108 | 4.0388 | 6.5328 | 2.2933 | 2.8487 | 0.82535 | 0.24251 | 3.4034 | 0.85271 | 0.36947 | 2.3079 | 7.9442 | 2.181 | 3.6425
[18 empty] | 02/12 23:00:00 | 5.4324 | 2.2594 | 2.4043 | 5.405 | 1.5891 | 3.4013 | 5.3973 | 1.4959 | 3.6081 | 0.30238 | 0.15877 | 1.9046 | 0.275 | 0.099188 | 2.7725 | 6.5051 | 1.7818 | 3.6509 | 6.4972 | 1.6844 | 3.8573 | 6.5215 | 2.2194 | 2.9384 | 3.2051 | 0.94483 | 3.3922 | 6.5051 | 1.61 | 4.0404 | 6.5324 | 2.2922 | 2.8499 | 0.82502 | 0.24272 | 3.3991 | 0.85239 | 0.36973 | 2.3054 | 7.9438 | 2.1805 | 3.6431
[18 empty] | 02/12 24:00:00 | 5.4322 | 2.2594 | 2.4043 | 5.4048 | 1.5891 | 3.4012 | 5.3972 | 1.4959 | 3.6081 | 0.30223 | 0.15869 | 1.9046 | 0.27481 | 0.099118 | 2.7725 | 6.5049 | 1.7816 | 3.6511 | 6.4971 | 1.6843 | 3.8576 | 6.5213 | 2.2192 | 2.9386 | 3.2049 | 0.94467 | 3.3926 | 6.5049 | 1.61 | 4.0404 | 6.5323 | 2.2921 | 2.8499 | 0.82482 | 0.24271 | 3.3984 | 0.85224 | 0.36971 | 2.3052 | 7.9436 | 2.1803 | 3.6433
[18 empty] | 02/13 01:00:00 | 5.4326 | 2.2597 | 2.4041 | 5.405 | 1.5893 | 3.4009 | 5.3974 | 1.4961 | 3.6078 | 0.30263 | 0.15891 | 1.9043 | 0.275 | 0.099202 | 2.7721 | 6.505 | 1.7813 | 3.6519 | 6.4974 | 1.684 | 3.8584 | 6.5217 | 2.2188 | 2.9393 | 3.205 | 0.94447 | 3.3935 | 6.5051 | 1.6094 | 4.0419 | 6.5327 | 2.2913 | 2.851 | 0.82501 | 0.24277 | 3.3983 | 0.85263 | 0.36991 | 2.305 | 7.9437 | 2.1798 | 3.6442
[18 empty] | 02/13 02:00:00 | 5.4332 | 2.26 | 2.404 | 5.4054 | 1.5895 | 3.4008 | 5.3978 | 1.4962 | 3.6076 | 0.30321 | 0.15923 | 1.9042 | 0.27543 | 0.099363 | 2.772 | 6.5055 | 1.7817 | 3.6513 | 6.4979 | 1.6844 | 3.8578 | 6.5222 | 2.2193 | 2.9389 | 3.2055 | 0.9448 | 3.3927 | 6.5055 | 1.6102 | 4.0401 | 6.5333 | 2.2926 | 2.8497 | 0.82544 | 0.2431 | 3.3954 | 0.85321 | 0.37045 | 2.3032 | 7.9442 | 2.1803 | 3.6436
[18 empty] | 02/13 03:00:00 | 5.4337 | 2.2601 | 2.4042 | 5.4058 | 1.5895 | 3.4009 | 5.3982 | 1.4963 | 3.6076 | 0.30366 | 0.15947 | 1.9042 | 0.27583 | 0.099508 | 2.772 | 6.5058 | 1.7779 | 3.6592 | 6.4982 | 1.6807 | 3.8664 | 6.5226 | 2.214 | 2.946 | 3.2058 | 0.94193 | 3.4035 | 6.5059 | 1.6021 | 4.0608 | 6.5337 | 2.2795 | 2.8663 | 0.82584 | 0.24153 | 3.4192 | 0.85367 | 0.36763 | 2.3221 | 7.9445 | 2.1752 | 3.6524
[18 empty] | 02/13 04:00:00 | 5.4337 | 2.26 | 2.4043 | 5.4059 | 1.5895 | 3.4011 | 5.3983 | 1.4963 | 3.6078 | 0.30367 | 0.15946 | 1.9043 | 0.27594 | 0.099544 | 2.7721 | 6.506 | 1.7792 | 3.6566 | 6.4984 | 1.6818 | 3.864 | 6.5227 | 2.2156 | 2.9439 | 3.206 | 0.94278 | 3.4005 | 6.506 | 1.6091 | 4.0432 | 6.5337 | 2.29 | 2.8531 | 0.82595 | 0.24141 | 3.4213 | 0.85367 | 0.36751 | 2.3229 | 7.9447 | 2.1769 | 3.6495
[18 empty] | 02/13 05:00:00 | 5.4334 | 2.2599 | 2.4043 | 5.4058 | 1.5894 | 3.4011 | 5.3983 | 1.4963 | 3.6078 | 0.30341 | 0.15933 | 1.9043 | 0.27584 | 0.099507 | 2.772 | 6.5059 | 1.7802 | 3.6545 | 6.4983 | 1.683 | 3.8611 | 6.5225 | 2.2172 | 2.9418 | 3.2059 | 0.94384 | 3.3966 | 6.5059 | 1.6088 | 4.0439 | 6.5335 | 2.2898 | 2.8533 | 0.82585 | 0.24241 | 3.4069 | 0.85342 | 0.36911 | 2.3121 | 7.9446 | 2.1785 | 3.6468
[18 empty] | 02/13 06:00:00 | 5.434 | 2.2603 | 2.4041 | 5.4063 | 1.5897 | 3.4009 | 5.3986 | 1.4964 | 3.6077 | 0.30403 | 0.15966 | 1.9043 | 0.2763 | 0.099674 | 2.772 | 6.5064 | 1.7853 | 3.6444 | 6.4988 | 1.6881 | 3.8497 | 6.5231 | 2.2244 | 2.9325 | 3.2063 | 0.94802 | 3.3822 | 6.5064 | 1.6176 | 4.0221 | 6.5341 | 2.3043 | 2.8356 | 0.82631 | 0.24559 | 3.3645 | 0.85404 | 0.37451 | 2.2805 | 7.9451 | 2.1855 | 3.6354
[18 empty] | 02/13 07:00:00 | 5.4342 | 2.2604 | 2.4041 | 5.4065 | 1.5897 | 3.4009 | 5.3988 | 1.4965 | 3.6077 | 0.30423 | 0.15976 | 1.9043 | 0.2765 | 0.099742 | 2.7721 | 6.5065 | 1.7827 | 3.6499 | 6.4989 | 1.6856 | 3.8555 | 6.5232 | 2.2208 | 2.9373 | 3.2065 | 0.94595 | 3.3897 | 6.5065 | 1.6102 | 4.0409 | 6.5343 | 2.2926 | 2.8501 | 0.8265 | 0.24472 | 3.3774 | 0.85424 | 0.37279 | 2.2915 | 7.9452 | 2.1818 | 3.6416
[18 empty] | 02/13 08:00:00 | 5.4348 | 2.2605 | 2.4042 | 5.4071 | 1.5899 | 3.401 | 5.3993 | 1.4966 | 3.6078 | 0.30479 | 0.16005 | 1.9044 | 0.27711 | 0.099963 | 2.7722 | 6.5071 | 1.7822 | 3.6511 | 6.4994 | 1.685 | 3.8573 | 6.5238 | 2.2201 | 2.9386 | 3.2071 | 0.94551 | 3.3919 | 6.5072 | 1.6107 | 4.04 | 6.5348 | 2.2932 | 2.8496 | 0.82712 | 0.24429 | 3.3858 | 0.85479 | 0.37196 | 2.2981 | 7.9457 | 2.181 | 3.6432
[18 empty] | 02/13 09:00:00 | 5.4364 | 2.2608 | 2.4046 | 5.4087 | 1.5901 | 3.4015 | 5.401 | 1.4968 | 3.6083 | 0.30636 | 0.16084 | 1.9048 | 0.27873 | 0.10052 | 2.7728 | 6.5087 | 1.7829 | 3.6506 | 6.501 | 1.6856 | 3.8567 | 6.5254 | 2.2209 | 2.9382 | 3.2087 | 0.94623 | 3.3911 | 6.5088 | 1.6118 | 4.0382 | 6.5364 | 2.2949 | 2.8482 | 0.82873 | 0.24522 | 3.3795 | 0.85637 | 0.37327 | 2.2942 | 7.9474 | 2.1817 | 3.6427
[18 empty] | 02/13 10:00:00 | 5.4379 | 2.2612 | 2.4049 | 5.4106 | 1.5904 | 3.4019 | 5.4028 | 1.4971 | 3.6087 | 0.30794 | 0.16164 | 1.9051 | 0.28055 | 0.10117 | 2.7732 | 6.5106 | 1.783 | 3.6515 | 6.5027 | 1.6856 | 3.8578 | 6.5271 | 2.221 | 2.9389 | 3.2106 | 0.94654 | 3.3919 | 6.5105 | 1.6115 | 4.0401 | 6.5381 | 2.2943 | 2.8497 | 0.83056 | 0.24588 | 3.3779 | 0.85794 | 0.37392 | 2.2945 | 7.9491 | 2.1817 | 3.6435
[18 empty] | 02/13 11:00:00 | 5.4392 | 2.2616 | 2.405 | 5.4119 | 1.5907 | 3.4021 | 5.404 | 1.4974 | 3.6089 | 0.30917 | 0.16227 | 1.9052 | 0.28189 | 0.10164 | 2.7734 | 6.5119 | 1.7832 | 3.6519 | 6.504 | 1.6857 | 3.8582 | 6.5283 | 2.2211 | 2.9392 | 3.2119 | 0.94678 | 3.3924 | 6.5119 | 1.6117 | 4.0403 | 6.5393 | 2.2946 | 2.8498 | 0.8319 | 0.24608 | 3.3807 | 0.85917 | 0.37423 | 2.2959 | 7.9504 | 2.1818 | 3.644
[18 empty] | 02/13 12:00:00 | 5.44 | 2.2619 | 2.4051 | 5.4127 | 1.5909 | 3.4022 | 5.4048 | 1.4976 | 3.609 | 0.31003 | 0.16272 | 1.9053 | 0.28266 | 0.10192 | 2.7735 | 6.5127 | 1.7833 | 3.652 | 6.5048 | 1.6859 | 3.8584 | 6.5291 | 2.2213 | 2.9393 | 3.2127 | 0.94695 | 3.3927 | 6.5127 | 1.6118 | 4.0406 | 6.5401 | 2.2948 | 2.85 | 0.83267 | 0.24604 | 3.3843 | 0.86004 | 0.37436 | 2.2974 | 7.9512 | 2.182 | 3.6441
[18 empty] | 02/13 13:00:00 | 5.4404 | 2.2622 | 2.4049 | 5.413 | 1.5912 | 3.4019 | 5.4052 | 1.4978 | 3.6087 | 0.31037 | 0.16292 | 1.9051 | 0.28297 | 0.10204 | 2.7731 | 6.513 | 1.7831 | 3.6527 | 6.5051 | 1.6856 | 3.8592 | 6.5295 | 2.2209 | 2.94 | 3.213 | 0.94674 | 3.3938 | 6.513 | 1.6112 | 4.0422 | 6.5404 | 2.2938 | 2.8514 | 0.83298 | 0.24571 | 3.3901 | 0.86038 | 0.37389 | 2.3011 | 7.9515 | 2.1815 | 3.6449
[18 empty] | 02/13 14:00:00 | 5.4406 | 2.2624 | 2.4048 | 5.4132 | 1.5913 | 3.4018 | 5.4054 | 1.498 | 3.6085 | 0.31057 | 0.16303 | 1.9049 | 0.2832 | 0.10213 | 2.7729 | 6.5132 | 1.7795 | 3.6602 | 6.5054 | 1.682 | 3.8676 | 6.5297 | 2.2158 | 2.9469 | 3.2132 | 0.9439 | 3.4042 | 6.5132 | 1.6038 | 4.0612 | 6.5406 | 2.2816 | 2.8666 | 0.83321 | 0.24392 | 3.4158 | 0.86057 | 0.37078 | 2.321 | 7.9517 | 2.1765 | 3.6534
[18 empty] | 02/13 15:00:00 | 5.4405 | 2.2622 | 2.405 | 5.4132 | 1.5912 | 3.402 | 5.4055 | 1.4979 | 3.6087 | 0.31051 | 0.163 | 1.905 | 0.28321 | 0.10213 | 2.773 | 6.5132 | 1.7808 | 3.6574 | 6.5055 | 1.6833 | 3.8648 | 6.5297 | 2.2175 | 2.9446 | 3.2132 | 0.94484 | 3.4008 | 6.5133 | 1.6108 | 4.0435 | 6.5406 | 2.2923 | 2.8533 | 0.83322 | 0.24383 | 3.4172 | 0.86052 | 0.37083 | 2.3205 | 7.9518 | 2.1784 | 3.6502
[18 empty] | 02/13 16:00:00 | 5.44 | 2.262 | 2.4049 | 5.4128 | 1.5911 | 3.4019 | 5.4052 | 1.4978 | 3.6086 | 0.31 | 0.16273 | 1.9049 | 0.28278 | 0.10198 | 2.7729 | 6.5128 | 1.7818 | 3.6553 | 6.5052 | 1.6845 | 3.8619 | 6.5292 | 2.219 | 2.9424 | 3.2128 | 0.94577 | 3.397 | 6.5129 | 1.6103 | 4.0445 | 6.5401 | 2.2918 | 2.8537 | 0.83279 | 0.24457 | 3.4051 | 0.86001 | 0.37215 | 2.3109 | 7.9514 | 2.1799 | 3.6475
[18 empty] | 02/13 17:00:00 | 5.4389 | 2.2616 | 2.4048 | 5.4116 | 1.5908 | 3.4018 | 5.4041 | 1.4976 | 3.6085 | 0.30885 | 0.16214 | 1.9048 | 0.28156 | 0.10155 | 2.7727 | 6.5116 | 1.7815 | 3.655 | 6.5041 | 1.6844 | 3.8615 | 6.5281 | 2.2188 | 2.9421 | 3.2116 | 0.94549 | 3.3968 | 6.5117 | 1.6099 | 4.0447 | 6.5389 | 2.2913 | 2.8539 | 0.83157 | 0.24411 | 3.4066 | 0.85886 | 0.37164 | 2.311 | 7.9502 | 2.1798 | 3.6472
[18 empty] | 02/13 18:00:00 | 5.437 | 2.261 | 2.4046 | 5.4097 | 1.5904 | 3.4016 | 5.4024 | 1.4972 | 3.6083 | 0.30697 | 0.16117 | 1.9046 | 0.27971 | 0.10089 | 2.7725 | 6.5098 | 1.7811 | 3.6548 | 6.5024 | 1.684 | 3.8612 | 6.5262 | 2.2183 | 2.942 | 3.2098 | 0.94495 | 3.3968 | 6.5098 | 1.6095 | 4.0446 | 6.537 | 2.2906 | 2.8538 | 0.82972 | 0.24326 | 3.4109 | 0.85697 | 0.37042 | 2.3135 | 7.9484 | 2.1794 | 3.647
[18 empty] | 02/13 19:00:00 | 5.4356 | 2.2606 | 2.4045 | 5.4084 | 1.59 | 3.4014 | 5.4009 | 1.4969 | 3.6081 | 0.30562 | 0.16047 | 1.9045 | 0.27839 | 0.10042 | 2.7724 | 6.5083 | 1.7808 | 3.6547 | 6.5011 | 1.6838 | 3.861 | 6.5248 | 2.2179 | 2.9418 | 3.2083 | 0.94456 | 3.3966 | 6.5084 | 1.6092 | 4.0444 | 6.5357 | 2.2903 | 2.8536 | 0.8284 | 0.24295 | 3.4097 | 0.85563 | 0.36997 | 2.3127 | 7.9471 | 2.1792 | 3.6469
[18 empty] | 02/13 20:00:00 | 5.4351 | 2.2606 | 2.4042 | 5.4078 | 1.59 | 3.4011 | 5.4005 | 1.4969 | 3.6079 | 0.3051 | 0.16021 | 1.9044 | 0.27781 | 0.10021 | 2.7722 | 6.5078 | 1.7856 | 3.6446 | 6.5007 | 1.6886 | 3.8498 | 6.5243 | 2.2248 | 2.9326 | 3.2078 | 0.94838 | 3.3824 | 6.5078 | 1.6179 | 4.0224 | 6.5352 | 2.3045 | 2.8358 | 0.82782 | 0.24557 | 3.371 | 0.85511 | 0.37441 | 2.2839 | 7.9466 | 2.1858 | 3.6356
[18 empty] | 02/13 21:00:00 | 5.4348 | 2.2605 | 2.4042 | 5.4074 | 1.5899 | 3.401 | 5.4003 | 1.4968 | 3.6079 | 0.30479 | 0.16005 | 1.9044 | 0.27743 | 0.10007 | 2.7722 | 6.5074 | 1.7829 | 3.65 | 6.5004 | 1.686 | 3.8556 | 6.5239 | 2.221 | 2.9374 | 3.2074 | 0.94617 | 3.3899 | 6.5075 | 1.6103 | 4.041 | 6.5348 | 2.2927 | 2.8502 | 0.82744 | 0.24465 | 3.3821 | 0.8548 | 0.37267 | 2.2937 | 7.9461 | 2.182 | 3.6417
[18 empty] | 02/13 22:00:00 | 5.4347 | 2.2605 | 2.4042 | 5.4072 | 1.5899 | 3.401 | 5.4001 | 1.4968 | 3.6079 | 0.30468 | 0.15999 | 1.9044 | 0.27723 | 0.1 | 2.7722 | 6.5072 | 1.7823 | 3.6511 | 6.5002 | 1.6851 | 3.8573 | 6.5237 | 2.22 | 2.9386 | 3.2072 | 0.94548 | 3.3922 | 6.5073 | 1.6106 | 4.0403 | 6.5347 | 2.293 | 2.8498 | 0.82724 | 0.24387 | 3.3921 | 0.85469 | 0.37143 | 2.3011 | 7.9459 | 2.181 | 3.6433
[18 empty] | 02/13 23:00:00 | 5.4346 | 2.2605 | 2.4042 | 5.4071 | 1.5899 | 3.401 | 5.3999 | 1.4967 | 3.6078 | 0.3046 | 0.15995 | 1.9044 | 0.2771 | 0.099956 | 2.7722 | 6.5071 | 1.7822 | 3.6512 | 6.5 | 1.685 | 3.8575 | 6.5237 | 2.2199 | 2.9387 | 3.2071 | 0.94537 | 3.3924 | 6.5072 | 1.6106 | 4.0403 | 6.5347 | 2.293 | 2.8498 | 0.82711 | 0.24364 | 3.3948 | 0.85461 | 0.37109 | 2.303 | 7.9458 | 2.1809 | 3.6434
[18 empty] | 02/13 24:00:00 | 5.4346 | 2.2605 | 2.4042 | 5.407 | 1.5899 | 3.401 | 5.3998 | 1.4967 | 3.6078 | 0.30462 | 0.15996 | 1.9044 | 0.27705 | 0.099939 | 2.7722 | 6.5071 | 1.7822 | 3.6512 | 6.4999 | 1.685 | 3.8575 | 6.5237 | 2.2199 | 2.9387 | 3.2071 | 0.94536 | 3.3924 | 6.5071 | 1.6106 | 4.0402 | 6.5347 | 2.2931 | 2.8498 | 0.82706 | 0.2436 | 3.3951 | 0.85463 | 0.37108 | 2.3031 | 7.9457 | 2.1809 | 3.6434
[18 empty] | 02/14 01:00:00 | 5.435 | 2.2606 | 2.4042 | 5.4073 | 1.5899 | 3.401 | 5.3999 | 1.4967 | 3.6078 | 0.30501 | 0.16016 | 1.9044 | 0.27727 | 0.10002 | 2.7722 | 6.5073 | 1.7822 | 3.6512 | 6.5 | 1.685 | 3.8575 | 6.524 | 2.22 | 2.9387 | 3.2073 | 0.94544 | 3.3924 | 6.5073 | 1.6106 | 4.0402 | 6.5351 | 2.2932 | 2.8497 | 0.82728 | 0.24378 | 3.3936 | 0.85502 | 0.37144 | 2.3019 | 7.946 | 2.1809 | 3.6434
[18 empty] | 02/14 02:00:00 | 5.4354 | 2.2607 | 2.4043 | 5.4075 | 1.59 | 3.401 | 5.4 | 1.4967 | 3.6078 | 0.30538 | 0.16035 | 1.9044 | 0.27754 | 0.10011 | 2.7722 | 6.5076 | 1.7823 | 3.6513 | 6.5 | 1.685 | 3.8576 | 6.5244 | 2.2201 | 2.9388 | 3.2076 | 0.94552 | 3.3924 | 6.5076 | 1.6107 | 4.0402 | 6.5354 | 2.2933 | 2.8498 | 0.82755 | 0.24391 | 3.3929 | 0.85539 | 0.37165 | 2.3016 | 7.9463 | 2.181 | 3.6435
[18 empty] | 02/14 03:00:00 | 5.4356 | 2.2607 | 2.4043 | 5.4077 | 1.59 | 3.4011 | 5.4 | 1.4967 | 3.6079 | 0.30559 | 0.16046 | 1.9044 | 0.27772 | 0.10018 | 2.7722 | 6.5077 | 1.7784 | 3.6594 | 6.5001 | 1.6811 | 3.8665 | 6.5245 | 2.2146 | 2.9462 | 3.2077 | 0.94247 | 3.4035 | 6.5078 | 1.6025 | 4.0609 | 6.5356 | 2.2801 | 2.8664 | 0.82772 | 0.24212 | 3.4187 | 0.85559 | 0.3685 | 2.3218 | 7.9464 | 2.1756 | 3.6526
[18 empty] | 02/14 04:00:00 | 5.4356 | 2.2606 | 2.4045 | 5.4078 | 1.5899 | 3.4013 | 5.4001 | 1.4967 | 3.608 | 0.30564 | 0.16048 | 1.9045 | 0.27779 | 0.1002 | 2.7723 | 6.5078 | 1.7797 | 3.6568 | 6.5002 | 1.6822 | 3.8641 | 6.5246 | 2.2162 | 2.9441 | 3.2078 | 0.94331 | 3.4006 | 6.5079 | 1.6096 | 4.0432 | 6.5357 | 2.2908 | 2.8531 | 0.8278 | 0.24204 | 3.4201 | 0.85565 | 0.36853 | 2.3218 | 7.9466 | 2.1773 | 3.6497
[18 empty] | 02/14 05:00:00 | 5.4356 | 2.2606 | 2.4045 | 5.4078 | 1.5899 | 3.4013 | 5.4001 | 1.4967 | 3.608 | 0.30559 | 0.16046 | 1.9045 | 0.27778 | 0.1002 | 2.7723 | 6.5078 | 1.7807 | 3.6547 | 6.5002 | 1.6835 | 3.8612 | 6.5246 | 2.2178 | 2.942 | 3.2078 | 0.94439 | 3.3967 | 6.5079 | 1.6092 | 4.0441 | 6.5357 | 2.2904 | 2.8535 | 0.82779 | 0.24307 | 3.4056 | 0.8556 | 0.37024 | 2.3109 | 7.9466 | 2.1789 | 3.647
[18 empty] | 02/14 06:00:00 | 5.4354 | 2.2607 | 2.4043 | 5.4076 | 1.59 | 3.401 | 5.4001 | 1.4968 | 3.6078 | 0.30536 | 0.16034 | 1.9044 | 0.27764 | 0.10015 | 2.7722 | 6.5077 | 1.7856 | 3.6446 | 6.5001 | 1.6884 | 3.8498 | 6.5244 | 2.2248 | 2.9326 | 3.2077 | 0.94837 | 3.3823 | 6.5077 | 1.6179 | 4.0224 | 6.5354 | 2.3046 | 2.8358 | 0.82766 | 0.24579 | 3.3674 | 0.85537 | 0.37472 | 2.2827 | 7.9464 | 2.1857 | 3.6356
[18 empty] | 02/14 07:00:00 | 5.435 | 2.2606 | 2.4042 | 5.4074 | 1.5899 | 3.401 | 5.3999 | 1.4967 | 3.6078 | 0.30503 | 0.16017 | 1.9044 | 0.2774 | 0.10007 | 2.7722 | 6.5074 | 1.7829 | 3.65 | 6.5 | 1.6859 | 3.8555 | 6.524 | 2.221 | 2.9374 | 3.2074 | 0.94618 | 3.3899 | 6.5075 | 1.6104 | 4.041 | 6.5351 | 2.2929 | 2.8502 | 0.82741 | 0.24478 | 3.3802 | 0.85504 | 0.37285 | 2.2932 | 7.946 | 2.182 | 3.6417
[18 empty] | 02/14 08:00:00 | 5.436 | 2.2609 | 2.4043 | 5.4082 | 1.5901 | 3.4011 | 5.4003 | 1.4968 | 3.6079 | 0.30603 | 0.16069 | 1.9045 | 0.2782 | 0.10035 | 2.7723 | 6.5082 | 1.7825 | 3.6512 | 6.5004 | 1.6852 | 3.8574 | 6.525 | 2.2204 | 2.9387 | 3.2082 | 0.94583 | 3.3919 | 6.5083 | 1.611 | 4.04 | 6.5361 | 2.2937 | 2.8496 | 0.82821 | 0.24466 | 3.3851 | 0.85604 | 0.37271 | 2.2968 | 7.9469 | 2.1812 | 3.6433
[18 empty] | 02/14 09:00:00 | 5.4375 | 2.2612 | 2.4047 | 5.4097 | 1.5903 | 3.4016 | 5.402 | 1.4971 | 3.6084 | 0.30754 | 0.16145 | 1.9049 | 0.27975 | 0.10089 | 2.7729 | 6.5098 | 1.7831 | 3.6508 | 6.502 | 1.6857 | 3.8571 | 6.5266 | 2.2212 | 2.9383 | 3.2098 | 0.94651 | 3.3912 | 6.5098 | 1.612 | 4.0383 | 6.5376 | 2.2952 | 2.8483 | 0.82975 | 0.24552 | 3.3796 | 0.85755 | 0.37381 | 2.2941 | 7.9484 | 2.182 | 3.6428
[18 empty] | 02/14 10:00:00 | 5.4389 | 2.2615 | 2.405 | 5.4112 | 1.5906 | 3.402 | 5.4034 | 1.4973 | 3.6088 | 0.30885 | 0.16211 | 1.9052 | 0.28122 | 0.1014 | 2.7733 | 6.5112 | 1.7831 | 3.6515 | 6.5034 | 1.6858 | 3.8578 | 6.5279 | 2.2212 | 2.9389 | 3.2112 | 0.94671 | 3.392 | 6.5112 | 1.6116 | 4.0402 | 6.5389 | 2.2945 | 2.8497 | 0.83122 | 0.24595 | 3.3796 | 0.85886 | 0.37427 | 2.2948 | 7.9499 | 2.1819 | 3.6436
[18 empty] | 02/14 11:00:00 | 5.4396 | 2.2618 | 2.405 | 5.412 | 1.5908 | 3.4021 | 5.4042 | 1.4975 | 3.6089 | 0.30962 | 0.1625 | 1.9053 | 0.28197 | 0.10167 | 2.7734 | 6.512 | 1.7832 | 3.6519 | 6.5042 | 1.6858 | 3.8583 | 6.5286 | 2.2212 | 2.9393 | 3.212 | 0.94676 | 3.3926 | 6.512 | 1.6117 | 4.0405 | 6.5397 | 2.2946 | 2.85 | 0.83198 | 0.24583 | 3.3844 | 0.85962 | 0.37416 | 2.2975 | 7.9506 | 2.1818 | 3.644
[18 empty] | 02/14 12:00:00 | 5.44 | 2.2619 | 2.4051 | 5.4123 | 1.5909 | 3.4022 | 5.4046 | 1.4975 | 3.609 | 0.30996 | 0.16268 | 1.9053 | 0.28235 | 0.1018 | 2.7734 | 6.5124 | 1.7833 | 3.652 | 6.5046 | 1.6859 | 3.8583 | 6.529 | 2.2213 | 2.9393 | 3.2124 | 0.94683 | 3.3927 | 6.5124 | 1.6117 | 4.0406 | 6.54 | 2.2947 | 2.8501 | 0.83235 | 0.2457 | 3.3876 | 0.85997 | 0.374 | 2.2994 | 7.951 | 2.1819 | 3.6441
[18 empty] | 02/14 13:00:00 | 5.4403 | 2.2622 | 2.4049 | 5.4127 | 1.5911 | 3.4019 | 5.4049 | 1.4978 | 3.6086 | 0.31029 | 0.16288 | 1.9051 | 0.28268 | 0.10194 | 2.7731 | 6.5127 | 1.783 | 3.6527 | 6.5049 | 1.6856 | 3.8592 | 6.5294 | 2.2209 | 2.94 | 3.2127 | 0.94666 | 3.3937 | 6.5127 | 1.6112 | 4.0422 | 6.5403 | 2.2938 | 2.8514 | 0.83269 | 0.24556 | 3.391 | 0.8603 | 0.37378 | 2.3016 | 7.9513 | 2.1815 | 3.6449
[18 empty] | 02/14 14:00:00 | 5.4407 | 2.2624 | 2.4048 | 5.4132 | 1.5913 | 3.4018 | 5.4054 | 1.498 | 3.6085 | 0.31074 | 0.16312 | 1.9049 | 0.28316 | 0.10212 | 2.7729 | 6.5132 | 1.7794 | 3.6602 | 6.5054 | 1.682 | 3.8675 | 6.5298 | 2.2158 | 2.9469 | 3.2132 | 0.94391 | 3.4041 | 6.5132 | 1.6038 | 4.0611 | 6.5408 | 2.2817 | 2.8666 | 0.83316 | 0.24399 | 3.4147 | 0.86074 | 0.37096 | 2.3203 | 7.9518 | 2.1765 | 3.6534
[18 empty] | 02/14 15:00:00 | 5.4408 | 2.2623 | 2.405 | 5.4133 | 1.5912 | 3.402 | 5.4055 | 1.4979 | 3.6087 | 0.31077 | 0.16313 | 1.905 | 0.28326 | 0.10215 | 2.773 | 6.5133 | 1.7809 | 3.6574 | 6.5056 | 1.6833 | 3.8648 | 6.5299 | 2.2176 | 2.9446 | 3.2133 | 0.94486 | 3.4008 | 6.5133 | 1.6108 | 4.0436 | 6.5408 | 2.2924 | 2.8533 | 0.83327 | 0.2439 | 3.4164 | 0.86078 | 0.37102 | 2.32 | 7.9519 | 2.1785 | 3.6503
[18 empty] | 02/14 16:00:00 | 5.4402 | 2.2621 | 2.4049 | 5.4128 | 1.5911 | 3.4019 | 5.4052 | 1.4979 | 3.6086 | 0.31023 | 0.16285 | 1.905 | 0.2828 | 0.10199 | 2.7729 | 6.5129 | 1.7818 | 3.6553 | 6.5053 | 1.6845 | 3.8619 | 6.5294 | 2.219 | 2.9424 | 3.2128 | 0.94578 | 3.397 | 6.5129 | 1.6103 | 4.0445 | 6.5403 | 2.2918 | 2.8538 | 0.83281 | 0.24459 | 3.405 | 0.86023 | 0.37226 | 2.3109 | 7.9515 | 2.18 | 3.6475
[18 empty] | 02/14 17:00:00 | 5.4395 | 2.2621 | 2.4046 | 5.412 | 1.5911 | 3.4014 | 5.4045 | 1.4979 | 3.6081 | 0.30949 | 0.16249 | 1.9046 | 0.282 | 0.10172 | 2.7724 | 6.5121 | 1.7817 | 3.6549 | 6.5046 | 1.6845 | 3.8614 | 6.5287 | 2.2191 | 2.942 | 3.212 | 0.94572 | 3.3964 | 6.5121 | 1.6103 | 4.0441 | 6.5396 | 2.2919 | 2.8533 | 0.83201 | 0.24447 | 3.4034 | 0.8595 | 0.37226 | 2.3089 | 7.9507 | 2.18 | 3.6471
[18 empty] | 02/14 18:00:00 | 5.4382 | 2.2616 | 2.4046 | 5.4105 | 1.5907 | 3.4014 | 5.4032 | 1.4975 | 3.6081 | 0.30816 | 0.1618 | 1.9046 | 0.28051 | 0.10118 | 2.7724 | 6.5106 | 1.7815 | 3.6546 | 6.5033 | 1.6844 | 3.861 | 6.5272 | 2.2188 | 2.9418 | 3.2106 | 0.94529 | 3.3964 | 6.5106 | 1.6098 | 4.0444 | 6.5382 | 2.2912 | 2.8536 | 0.83052 | 0.24373 | 3.4076 | 0.85817 | 0.37135 | 2.3109 | 7.9492 | 2.1798 | 3.6468
[18 empty] | 02/14 19:00:00 | 5.4367 | 2.261 | 2.4046 | 5.4093 | 1.5903 | 3.4015 | 5.4019 | 1.4971 | 3.6082 | 0.30674 | 0.16105 | 1.9046 | 0.27926 | 0.10073 | 2.7725 | 6.5093 | 1.7811 | 3.6547 | 6.5019 | 1.684 | 3.8611 | 6.5258 | 2.2183 | 2.9419 | 3.2093 | 0.94488 | 3.3965 | 6.5094 | 1.6095 | 4.0443 | 6.5368 | 2.2907 | 2.8537 | 0.82927 | 0.24334 | 3.4079 | 0.85675 | 0.37058 | 2.3119 | 7.948 | 2.1794 | 3.6469
[18 empty] | 02/14 20:00:00 | 5.4361 | 2.2609 | 2.4043 | 5.4086 | 1.5902 | 3.4012 | 5.4011 | 1.497 | 3.608 | 0.30605 | 0.1607 | 1.9045 | 0.27861 | 0.1005 | 2.7723 | 6.5086 | 1.7858 | 3.6447 | 6.5013 | 1.6887 | 3.8499 | 6.5252 | 2.225 | 2.9327 | 3.2086 | 0.94859 | 3.3825 | 6.5086 | 1.618 | 4.0226 | 6.5361 | 2.3047 | 2.8359 | 0.82853 | 0.24574 | 3.3715 | 0.85607 | 0.37479 | 2.2841 | 7.9473 | 2.1859 | 3.6357
[18 empty] | 02/14 21:00:00 | 5.4357 | 2.2608 | 2.4043 | 5.4082 | 1.5901 | 3.4011 | 5.4007 | 1.4969 | 3.6079 | 0.30569 | 0.16051 | 1.9045 | 0.27819 | 0.10035 | 2.7723 | 6.508 | 1.783 | 3.6501 | 6.5008 | 1.686 | 3.8557 | 6.5247 | 2.2212 | 2.9374 | 3.208 | 0.94633 | 3.3899 | 6.5081 | 1.6105 | 4.041 | 6.5357 | 2.2931 | 2.8502 | 0.82798 | 0.24478 | 3.3826 | 0.85569 | 0.3731 | 2.2935 | 7.9467 | 2.1821 | 3.6417
[18 empty] | 02/14 22:00:00 | 5.4361 | 2.261 | 2.4043 | 5.4083 | 1.5902 | 3.4011 | 5.4007 | 1.4969 | 3.6079 | 0.30608 | 0.16071 | 1.9045 | 0.27834 | 0.1004 | 2.7723 | 6.5082 | 1.7825 | 3.6512 | 6.5008 | 1.6853 | 3.8575 | 6.525 | 2.2204 | 2.9387 | 3.2082 | 0.94579 | 3.3921 | 6.5083 | 1.6108 | 4.0403 | 6.5361 | 2.2935 | 2.8498 | 0.82822 | 0.24435 | 3.3895 | 0.85608 | 0.37235 | 2.2991 | 7.9469 | 2.1812 | 3.6434
[18 empty] | 02/14 23:00:00 | 5.4359 | 2.2609 | 2.4043 | 5.4082 | 1.5901 | 3.4011 | 5.4007 | 1.4969 | 3.6079 | 0.30594 | 0.16064 | 1.9045 | 0.27822 | 0.10036 | 2.7723 | 6.5082 | 1.7824 | 3.6513 | 6.5008 | 1.6852 | 3.8577 | 6.5249 | 2.2202 | 2.9388 | 3.2082 | 0.94568 | 3.3925 | 6.5082 | 1.6108 | 4.0403 | 6.536 | 2.2934 | 2.8499 | 0.82815 | 0.24406 | 3.3933 | 0.85595 | 0.37178 | 2.3023 | 7.9469 | 2.1811 | 3.6435
[18 empty] | 02/14 24:00:00 | 5.4358 | 2.2609 | 2.4043 | 5.4081 | 1.5901 | 3.4011 | 5.4006 | 1.4969 | 3.6079 | 0.3058 | 0.16057 | 1.9045 | 0.27809 | 0.10031 | 2.7723 | 6.5081 | 1.7824 | 3.6513 | 6.5007 | 1.6851 | 3.8577 | 6.5248 | 2.2202 | 2.9388 | 3.2081 | 0.94564 | 3.3925 | 6.5081 | 1.6108 | 4.0403 | 6.5359 | 2.2934 | 2.8499 | 0.82806 | 0.24393 | 3.3946 | 0.85581 | 0.37158 | 2.3031 | 7.9468 | 2.1811 | 3.6435
[18 empty] | 02/15 01:00:00 | 5.4357 | 2.2608 | 2.4043 | 5.408 | 1.5901 | 3.4011 | 5.4005 | 1.4969 | 3.6079 | 0.30571 | 0.16052 | 1.9045 | 0.27799 | 0.10028 | 2.7723 | 6.508 | 1.7824 | 3.6513 | 6.5006 | 1.6851 | 3.8577 | 6.5247 | 2.2202 | 2.9388 | 3.208 | 0.94562 | 3.3925 | 6.508 | 1.6108 | 4.0403 | 6.5358 | 2.2934 | 2.8499 | 0.82798 | 0.24388 | 3.395 | 0.85572 | 0.37152 | 2.3033 | 7.9467 | 2.1811 | 3.6435
[18 empty] | 02/15 02:00:00 | 5.4359 | 2.2608 | 2.4044 | 5.4081 | 1.5901 | 3.4012 | 5.4005 | 1.4968 | 3.6079 | 0.30589 | 0.16061 | 1.9045 | 0.27807 | 0.10031 | 2.7722 | 6.5081 | 1.7784 | 3.6594 | 6.5006 | 1.6812 | 3.8666 | 6.5248 | 2.2146 | 2.9462 | 3.2081 | 0.94256 | 3.4036 | 6.5081 | 1.6026 | 4.0609 | 6.5359 | 2.2802 | 2.8664 | 0.82806 | 0.24217 | 3.4194 | 0.85589 | 0.36859 | 2.3221 | 7.9468 | 2.1757 | 3.6526
[18 empty] | 02/15 03:00:00 | 5.4368 | 2.261 | 2.4046 | 5.4087 | 1.5901 | 3.4014 | 5.4009 | 1.4969 | 3.6081 | 0.30678 | 0.16107 | 1.9046 | 0.27868 | 0.10052 | 2.7724 | 6.5087 | 1.7799 | 3.6569 | 6.501 | 1.6823 | 3.8643 | 6.5257 | 2.2165 | 2.9442 | 3.2087 | 0.94361 | 3.4005 | 6.5087 | 1.6099 | 4.0431 | 6.5368 | 2.2913 | 2.8529 | 0.82868 | 0.24255 | 3.4166 | 0.85679 | 0.36953 | 2.3186 | 7.9475 | 2.1775 | 3.6498
[18 empty] | 02/15 04:00:00 | 5.4374 | 2.2615 | 2.4044 | 5.4092 | 1.5904 | 3.4011 | 5.4014 | 1.4972 | 3.6078 | 0.30744 | 0.16144 | 1.9044 | 0.27924 | 0.10073 | 2.772 | 6.5093 | 1.7811 | 3.6547 | 6.5015 | 1.6837 | 3.8613 | 6.5263 | 2.2184 | 2.942 | 3.2093 | 0.9449 | 3.3964 | 6.5093 | 1.6097 | 4.0437 | 6.5375 | 2.2913 | 2.8531 | 0.82924 | 0.24386 | 3.4005 | 0.85745 | 0.37163 | 2.3073 | 7.9482 | 2.1794 | 3.647
[18 empty] | 02/15 05:00:00 | 5.4368 | 2.2614 | 2.4042 | 5.4089 | 1.5905 | 3.4008 | 5.4013 | 1.4972 | 3.6075 | 0.30681 | 0.16113 | 1.9041 | 0.2789 | 0.10062 | 2.7717 | 6.5089 | 1.7812 | 3.6542 | 6.5013 | 1.684 | 3.8606 | 6.5258 | 2.2186 | 2.9415 | 3.2089 | 0.94497 | 3.3958 | 6.509 | 1.6097 | 4.0435 | 6.5369 | 2.2912 | 2.853 | 0.82891 | 0.24377 | 3.4003 | 0.85682 | 0.37121 | 2.3082 | 7.9478 | 2.1796 | 3.6464
[18 empty] | 02/15 06:00:00 | 5.4357 | 2.2611 | 2.4041 | 5.4081 | 1.5903 | 3.4007 | 5.4006 | 1.4971 | 3.6074 | 0.30575 | 0.16058 | 1.904 | 0.27807 | 0.10033 | 2.7716 | 6.5081 | 1.7811 | 3.6541 | 6.5007 | 1.6839 | 3.8604 | 6.5248 | 2.2183 | 2.9413 | 3.2081 | 0.94472 | 3.3958 | 6.5082 | 1.6094 | 4.0438 | 6.5358 | 2.2907 | 2.8532 | 0.82808 | 0.24327 | 3.404 | 0.85575 | 0.37038 | 2.3105 | 7.9469 | 2.1794 | 3.6463
[18 empty] | 02/15 07:00:00 | 5.4341 | 2.2603 | 2.4042 | 5.4065 | 1.5897 | 3.4009 | 5.3993 | 1.4966 | 3.6077 | 0.30407 | 0.15969 | 1.9042 | 0.27654 | 0.099767 | 2.7719 | 6.5066 | 1.7806 | 3.6541 | 6.4994 | 1.6836 | 3.8604 | 6.5232 | 2.2177 | 2.9414 | 3.2066 | 0.9442 | 3.3961 | 6.5067 | 1.609 | 4.0439 | 6.5341 | 2.29 | 2.8533 | 0.82656 | 0.24245 | 3.4091 | 0.85408 | 0.36924 | 2.3131 | 7.9453 | 2.179 | 3.6463
[18 empty] | 02/15 08:00:00 | 5.4345 | 2.2604 | 2.4042 | 5.4069 | 1.5898 | 3.401 | 5.3994 | 1.4966 | 3.6078 | 0.30453 | 0.15992 | 1.9043 | 0.27688 | 0.09988 | 2.7721 | 6.507 | 1.7855 | 3.6444 | 6.4995 | 1.6884 | 3.8496 | 6.5237 | 2.2247 | 2.9324 | 3.2069 | 0.94822 | 3.3821 | 6.507 | 1.6178 | 4.0221 | 6.5346 | 2.3045 | 2.8356 | 0.82689 | 0.24569 | 3.3655 | 0.85455 | 0.37466 | 2.2808 | 7.9457 | 2.1856 | 3.6354
[18 empty] | 02/15 09:00:00 | 5.4364 | 2.2611 | 2.4044 | 5.4087 | 1.5902 | 3.4012 | 5.4009 | 1.497 | 3.608 | 0.30644 | 0.1609 | 1.9046 | 0.27866 | 0.10051 | 2.7724 | 6.5087 | 1.7832 | 3.6501 | 6.5009 | 1.6861 | 3.8556 | 6.5254 | 2.2215 | 2.9374 | 3.2087 | 0.94668 | 3.3894 | 6.5087 | 1.6109 | 4.0403 | 6.5365 | 2.2937 | 2.8497 | 0.82866 | 0.24608 | 3.3674 | 0.85644 | 0.37479 | 2.2851 | 7.9474 | 2.1823 | 3.6417
[18 empty] | 02/15 10:00:00 | 5.4385 | 2.2617 | 2.4046 | 5.4108 | 1.5907 | 3.4014 | 5.4031 | 1.4974 | 3.6082 | 0.30847 | 0.16195 | 1.9048 | 0.28081 | 0.10128 | 2.7726 | 6.5108 | 1.7831 | 3.6515 | 6.503 | 1.6857 | 3.8578 | 6.5275 | 2.2211 | 2.9389 | 3.2108 | 0.94666 | 3.3917 | 6.5108 | 1.6116 | 4.0399 | 6.5385 | 2.2945 | 2.8496 | 0.83082 | 0.24629 | 3.3734 | 0.85848 | 0.37469 | 2.2912 | 7.9495 | 2.1818 | 3.6435
[18 empty] | 02/15 11:00:00 | 5.4398 | 2.2622 | 2.4047 | 5.4122 | 1.5911 | 3.4016 | 5.4044 | 1.4977 | 3.6084 | 0.30977 | 0.16262 | 1.9049 | 0.28219 | 0.10177 | 2.7728 | 6.5122 | 1.7833 | 3.6517 | 6.5043 | 1.6859 | 3.8581 | 6.5287 | 2.2213 | 2.9391 | 3.2122 | 0.94692 | 3.3922 | 6.5122 | 1.6119 | 4.0402 | 6.5398 | 2.2949 | 2.8497 | 0.83219 | 0.24629 | 3.3789 | 0.85978 | 0.37469 | 2.2946 | 7.9508 | 2.182 | 3.6438
[18 empty] | 02/15 12:00:00 | 5.4402 | 2.2623 | 2.4047 | 5.4126 | 1.5912 | 3.4016 | 5.4048 | 1.4978 | 3.6084 | 0.31019 | 0.16283 | 1.9049 | 0.2826 | 0.10192 | 2.7728 | 6.5126 | 1.7834 | 3.6518 | 6.5048 | 1.686 | 3.8582 | 6.5292 | 2.2214 | 2.9392 | 3.2126 | 0.94696 | 3.3925 | 6.5126 | 1.6118 | 4.0405 | 6.5402 | 2.2948 | 2.85 | 0.8326 | 0.24592 | 3.3857 | 0.86019 | 0.37427 | 2.2983 | 7.9512 | 2.182 | 3.6439
[18 empty] | 02/15 13:00:00 | 5.4398 | 2.2622 | 2.4047 | 5.4123 | 1.5911 | 3.4016 | 5.4046 | 1.4978 | 3.6084 | 0.30983 | 0.16265 | 1.9049 | 0.28231 | 0.10181 | 2.7728 | 6.5123 | 1.7833 | 3.6518 | 6.5046 | 1.6859 | 3.8582 | 6.5289 | 2.2213 | 2.9392 | 3.2123 | 0.94684 | 3.3927 | 6.5124 | 1.6117 | 4.0406 | 6.5399 | 2.2946 | 2.8501 | 0.83232 | 0.2454 | 3.3916 | 0.85984 | 0.37356 | 2.3017 | 7.951 | 2.182 | 3.6439
[18 empty] | 02/15 14:00:00 | 5.4399 | 2.2623 | 2.4047 | 5.4123 | 1.5911 | 3.4015 | 5.4047 | 1.4979 | 3.6082 | 0.30994 | 0.16273 | 1.9047 | 0.28231 | 0.10183 | 2.7725 | 6.5123 | 1.7784 | 3.6618 | 6.5046 | 1.681 | 3.8694 | 6.5289 | 2.2144 | 2.9484 | 3.2123 | 0.94294 | 3.4067 | 6.5124 | 1.6033 | 4.0619 | 6.54 | 2.2809 | 2.8673 | 0.83232 | 0.24299 | 3.4253 | 0.85995 | 0.36952 | 2.3272 | 7.9509 | 2.1752 | 3.6552
[18 empty] | 02/15 15:00:00 | 5.4407 | 2.2629 | 2.4043 | 5.4129 | 1.5916 | 3.4009 | 5.4052 | 1.4983 | 3.6075 | 0.31073 | 0.16318 | 1.9042 | 0.28289 | 0.10206 | 2.7718 | 6.5129 | 1.7817 | 3.6555 | 6.5053 | 1.6841 | 3.8627 | 6.5297 | 2.2188 | 2.9429 | 3.2129 | 0.94558 | 3.3979 | 6.513 | 1.6112 | 4.0422 | 6.5408 | 2.2934 | 2.852 | 0.8329 | 0.24444 | 3.4074 | 0.86074 | 0.37225 | 2.3123 | 7.9516 | 2.1796 | 3.6482
[18 empty] | 02/15 16:00:00 | 5.441 | 2.2632 | 2.4041 | 5.4132 | 1.5918 | 3.4007 | 5.4055 | 1.4985 | 3.6073 | 0.31101 | 0.16334 | 1.9041 | 0.28318 | 0.10218 | 2.7715 | 6.5132 | 1.7824 | 3.6541 | 6.5056 | 1.6851 | 3.8607 | 6.53 | 2.22 | 2.9414 | 3.2132 | 0.94634 | 3.3954 | 6.5132 | 1.611 | 4.0429 | 6.5411 | 2.2932 | 2.8524 | 0.83319 | 0.24528 | 3.3969 | 0.86102 | 0.37351 | 2.3052 | 7.9519 | 2.1808 | 3.6464
[18 empty] | 02/15 17:00:00 | 5.4401 | 2.2629 | 2.4041 | 5.4125 | 1.5916 | 3.4006 | 5.4049 | 1.4983 | 3.6073 | 0.31015 | 0.16289 | 1.904 | 0.28252 | 0.10194 | 2.7715 | 6.5126 | 1.7823 | 3.654 | 6.505 | 1.6851 | 3.8604 | 6.5292 | 2.2199 | 2.9412 | 3.2126 | 0.94617 | 3.3953 | 6.5126 | 1.6107 | 4.0433 | 6.5402 | 2.2926 | 2.8527 | 0.83253 | 0.24489 | 3.3996 | 0.86016 | 0.3728 | 2.3073 | 7.9512 | 2.1807 | 3.6462
[18 empty] | 02/15 18:00:00 | 5.4379 | 2.2619 | 2.4041 | 5.4104 | 1.5909 | 3.4008 | 5.4028 | 1.4977 | 3.6074 | 0.30788 | 0.16169 | 1.9041 | 0.28038 | 0.10116 | 2.7716 | 6.5104 | 1.7817 | 3.654 | 6.5029 | 1.6846 | 3.8603 | 6.527 | 2.2191 | 2.9412 | 3.2104 | 0.94541 | 3.3958 | 6.5105 | 1.6099 | 4.0439 | 6.5379 | 2.2914 | 2.8532 | 0.83039 | 0.24353 | 3.4097 | 0.85788 | 0.37088 | 2.3131 | 7.9491 | 2.1801 | 3.6462
[18 empty] | 02/15 19:00:00 | 5.436 | 2.2614 | 2.4038 | 5.4086 | 1.5906 | 3.4004 | 5.4011 | 1.4974 | 3.6071 | 0.30603 | 0.16075 | 1.9038 | 0.27857 | 0.10052 | 2.7712 | 6.5086 | 1.7813 | 3.6539 | 6.5012 | 1.6841 | 3.8602 | 6.525 | 2.2185 | 2.9411 | 3.2086 | 0.94491 | 3.3957 | 6.5087 | 1.6097 | 4.0434 | 6.5361 | 2.2911 | 2.8528 | 0.82858 | 0.24292 | 3.4109 | 0.85604 | 0.37007 | 2.3132 | 7.9473 | 2.1797 | 3.6461
[18 empty] | 02/15 20:00:00 | 5.4354 | 2.2611 | 2.4039 | 5.4079 | 1.5903 | 3.4005 | 5.4007 | 1.4972 | 3.6072 | 0.30535 | 0.16039 | 1.9038 | 0.27795 | 0.10029 | 2.7713 | 6.508 | 1.7812 | 3.6537 | 6.5008 | 1.6841 | 3.86 | 6.5244 | 2.2184 | 2.941 | 3.208 | 0.94481 | 3.3954 | 6.5081 | 1.6096 | 4.0433 | 6.5354 | 2.2909 | 2.8527 | 0.82796 | 0.24313 | 3.4055 | 0.85536 | 0.37027 | 2.3101 | 7.9467 | 2.1796 | 3.6459
[18 empty] | 02/15 21:00:00 | 5.435 | 2.2608 | 2.404 | 5.4075 | 1.5901 | 3.4007 | 5.4004 | 1.497 | 3.6074 | 0.30495 | 0.16017 | 1.904 | 0.27754 | 0.10014 | 2.7715 | 6.5076 | 1.781 | 3.6539 | 6.5005 | 1.684 | 3.8602 | 6.524 | 2.2182 | 2.9412 | 3.2076 | 0.94463 | 3.3956 | 6.5077 | 1.6094 | 4.0435 | 6.535 | 2.2907 | 2.8529 | 0.82756 | 0.24319 | 3.4029 | 0.85496 | 0.37032 | 2.3087 | 7.9462 | 2.1794 | 3.6461
[18 empty] | 02/15 22:00:00 | 5.4347 | 2.2607 | 2.404 | 5.4073 | 1.5901 | 3.4006 | 5.4002 | 1.497 | 3.6074 | 0.30474 | 0.16006 | 1.9039 | 0.27728 | 0.10005 | 2.7715 | 6.5073 | 1.7809 | 3.6539 | 6.5003 | 1.6839 | 3.8603 | 6.5238 | 2.2181 | 2.9412 | 3.2073 | 0.94455 | 3.3956 | 6.5074 | 1.6094 | 4.0434 | 6.5348 | 2.2906 | 2.8528 | 0.8273 | 0.24323 | 3.4013 | 0.85474 | 0.37038 | 2.3078 | 7.946 | 2.1793 | 3.6462
[18 empty] | 02/15 23:00:00 | 5.4346 | 2.2607 | 2.404 | 5.4071 | 1.59 | 3.4006 | 5.4 | 1.4969 | 3.6074 | 0.30458 | 0.15997 | 1.9039 | 0.27709 | 0.09998 | 2.7715 | 6.5071 | 1.7809 | 3.6539 | 6.5001 | 1.6838 | 3.8603 | 6.5236 | 2.218 | 2.9412 | 3.2071 | 0.9445 | 3.3956 | 6.5072 | 1.6093 | 4.0434 | 6.5346 | 2.2906 | 2.8528 | 0.82711 | 0.24323 | 3.4005 | 0.85459 | 0.37037 | 2.3074 | 7.9458 | 2.1792 | 3.6461
[18 empty] | 02/15 24:00:00 | 5.4345 | 2.2606 | 2.4039 | 5.4069 | 1.59 | 3.4006 | 5.3998 | 1.4969 | 3.6073 | 0.30446 | 0.15991 | 1.9039 | 0.27694 | 0.099927 | 2.7715 | 6.507 | 1.7808 | 3.6539 | 6.4999 | 1.6838 | 3.8602 | 6.5235 | 2.218 | 2.9412 | 3.207 | 0.94446 | 3.3956 | 6.507 | 1.6093 | 4.0434 | 6.5345 | 2.2905 | 2.8528 | 0.82696 | 0.24322 | 3.4 | 0.85447 | 0.37035 | 2.3072 | 7.9456 | 2.1792 | 3.6461
[18 empty] | 02/16 01:00:00 | 5.4344 | 2.2606 | 2.4039 | 5.4069 | 1.59 | 3.4006 | 5.3997 | 1.4969 | 3.6073 | 0.30443 | 0.1599 | 1.9039 | 0.27688 | 0.099904 | 2.7715 | 6.5069 | 1.7808 | 3.6539 | 6.4998 | 1.6838 | 3.8603 | 6.5235 | 2.218 | 2.9412 | 3.2069 | 0.94445 | 3.3955 | 6.507 | 1.6093 | 4.0433 | 6.5345 | 2.2906 | 2.8528 | 0.82689 | 0.24324 | 3.3994 | 0.85444 | 0.3704 | 2.3068 | 7.9456 | 2.1792 | 3.6461
[18 empty] | 02/16 02:00:00 | 5.4345 | 2.2609 | 2.4037 | 5.4069 | 1.5902 | 3.4002 | 5.3996 | 1.497 | 3.6069 | 0.30447 | 0.15994 | 1.9036 | 0.27688 | 0.099918 | 2.771 | 6.5069 | 1.7809 | 3.6537 | 6.4997 | 1.6838 | 3.8601 | 6.5235 | 2.2181 | 2.941 | 3.2069 | 0.94452 | 3.3953 | 6.507 | 1.6095 | 4.0429 | 6.5345 | 2.2909 | 2.8524 | 0.82689 | 0.24331 | 3.3984 | 0.85447 | 0.37051 | 2.3062 | 7.9456 | 2.1793 | 3.646
[18 empty] | 02/16 03:00:00 | 5.4344 | 2.261 | 2.4035 | 5.4068 | 1.5903 | 3.4 | 5.3995 | 1.4971 | 3.6066 | 0.30443 | 0.15994 | 1.9034 | 0.27684 | 0.099914 | 2.7708 | 6.5069 | 1.7811 | 3.6534 | 6.4996 | 1.6839 | 3.8598 | 6.5235 | 2.2183 | 2.9407 | 3.2069 | 0.9446 | 3.3949 | 6.5069 | 1.6096 | 4.0427 | 6.5345 | 2.291 | 2.8522 | 0.82685 | 0.24332 | 3.3982 | 0.85444 | 0.37052 | 2.306 | 7.9455 | 2.1795 | 3.6456
[18 empty] | 02/16 04:00:00 | 5.4348 | 2.2612 | 2.4035 | 5.4071 | 1.5903 | 3.4 | 5.3996 | 1.4971 | 3.6066 | 0.30477 | 0.16011 | 1.9035 | 0.27705 | 0.09999 | 2.7708 | 6.5071 | 1.7811 | 3.6533 | 6.4997 | 1.684 | 3.8597 | 6.5238 | 2.2184 | 2.9407 | 3.2071 | 0.9447 | 3.3948 | 6.5071 | 1.6096 | 4.0426 | 6.5348 | 2.2912 | 2.8521 | 0.82706 | 0.2435 | 3.3966 | 0.85478 | 0.37089 | 2.3047 | 7.9458 | 2.1796 | 3.6456
[18 empty] | 02/16 05:00:00 | 5.4356 | 2.2614 | 2.4036 | 5.4076 | 1.5904 | 3.4 | 5.3999 | 1.4972 | 3.6067 | 0.30555 | 0.16052 | 1.9035 | 0.2776 | 0.10018 | 2.7708 | 6.5076 | 1.7813 | 3.6534 | 6.5 | 1.6841 | 3.8596 | 6.5245 | 2.2187 | 2.9408 | 3.2076 | 0.94487 | 3.3948 | 6.5077 | 1.6098 | 4.0425 | 6.5356 | 2.2915 | 2.8521 | 0.8276 | 0.24384 | 3.394 | 0.85556 | 0.37154 | 2.3027 | 7.9463 | 2.1797 | 3.6456
[18 empty] | 02/16 06:00:00 | 5.4362 | 2.2613 | 2.4039 | 5.4081 | 1.5904 | 3.4005 | 5.4002 | 1.4971 | 3.6071 | 0.30616 | 0.16081 | 1.9039 | 0.2781 | 0.10035 | 2.7714 | 6.5081 | 1.7813 | 3.6536 | 6.5002 | 1.6841 | 3.8599 | 6.5251 | 2.2187 | 2.941 | 3.2081 | 0.94494 | 3.3951 | 6.5081 | 1.6097 | 4.0431 | 6.5362 | 2.2913 | 2.8526 | 0.8281 | 0.24399 | 3.394 | 0.85617 | 0.37173 | 2.3032 | 7.9469 | 2.1797 | 3.6458
[18 empty] | 02/16 07:00:00 | 5.4361 | 2.2612 | 2.4041 | 5.4082 | 1.5903 | 3.4007 | 5.4003 | 1.497 | 3.6074 | 0.30614 | 0.16078 | 1.9041 | 0.27819 | 0.10037 | 2.7716 | 6.5082 | 1.7811 | 3.654 | 6.5003 | 1.6839 | 3.8603 | 6.5251 | 2.2185 | 2.9413 | 3.2082 | 0.94485 | 3.3955 | 6.5082 | 1.6096 | 4.0434 | 6.5362 | 2.2911 | 2.8529 | 0.8282 | 0.24385 | 3.3963 | 0.85615 | 0.37138 | 2.3053 | 7.9469 | 2.1795 | 3.6462
[18 empty] | 02/16 08:00:00 | 5.4365 | 2.2613 | 2.4041 | 5.4085 | 1.5904 | 3.4008 | 5.4007 | 1.4971 | 3.6074 | 0.3065 | 0.16097 | 1.9041 | 0.27855 | 0.1005 | 2.7717 | 6.5086 | 1.7812 | 3.654 | 6.5007 | 1.6839 | 3.8604 | 6.5255 | 2.2186 | 2.9413 | 3.2086 | 0.94496 | 3.3955 | 6.5086 | 1.6098 | 4.0432 | 6.5366 | 2.2914 | 2.8527 | 0.82856 | 0.24406 | 3.3948 | 0.85651 | 0.37171 | 2.3042 | 7.9473 | 2.1796 | 3.6463
[18 empty] | 02/16 09:00:00 | 5.4379 | 2.2615 | 2.4046 | 5.41 | 1.5905 | 3.4014 | 5.4023 | 1.4973 | 3.608 | 0.30791 | 0.16167 | 1.9046 | 0.28003 | 0.10101 | 2.7723 | 6.51 | 1.7814 | 3.6544 | 6.5022 | 1.6842 | 3.8608 | 6.5269 | 2.2188 | 2.9416 | 3.21 | 0.94537 | 3.3955 | 6.5101 | 1.61 | 4.0434 | 6.538 | 2.2916 | 2.853 | 0.83004 | 0.24499 | 3.3881 | 0.85792 | 0.37287 | 2.3009 | 7.9488 | 2.1798 | 3.6465
[18 empty] | 02/16 10:00:00 | 5.4384 | 2.2615 | 2.4048 | 5.4106 | 1.5906 | 3.4017 | 5.4029 | 1.4973 | 3.6084 | 0.30841 | 0.16191 | 1.9048 | 0.28064 | 0.10122 | 2.7726 | 6.5107 | 1.7814 | 3.6548 | 6.5028 | 1.6842 | 3.8612 | 6.5274 | 2.2187 | 2.9419 | 3.2107 | 0.94539 | 3.3961 | 6.5107 | 1.61 | 4.044 | 6.5384 | 2.2914 | 2.8534 | 0.83065 | 0.24494 | 3.3912 | 0.85841 | 0.37273 | 2.303 | 7.9494 | 2.1797 | 3.647
[18 empty] | 02/16 11:00:00 | 5.4391 | 2.2617 | 2.4048 | 5.4115 | 1.5908 | 3.4018 | 5.4038 | 1.4975 | 3.6085 | 0.30906 | 0.16225 | 1.9049 | 0.28151 | 0.10153 | 2.7727 | 6.5116 | 1.7816 | 3.6549 | 6.5037 | 1.6843 | 3.8613 | 6.5281 | 2.2189 | 2.942 | 3.2116 | 0.94569 | 3.3961 | 6.5116 | 1.6103 | 4.0438 | 6.5391 | 2.2917 | 2.8533 | 0.83152 | 0.24531 | 3.3896 | 0.85907 | 0.37309 | 2.3025 | 7.9502 | 2.1799 | 3.6471
[18 empty] | 02/16 12:00:00 | 5.44 | 2.2623 | 2.4046 | 5.4125 | 1.5912 | 3.4015 | 5.4049 | 1.498 | 3.6082 | 0.30999 | 0.16275 | 1.9046 | 0.2825 | 0.1019 | 2.7724 | 6.5126 | 1.7819 | 3.6549 | 6.5048 | 1.6846 | 3.8613 | 6.529 | 2.2193 | 2.942 | 3.2126 | 0.94601 | 3.3959 | 6.5126 | 1.6106 | 4.0436 | 6.54 | 2.2923 | 2.853 | 0.83251 | 0.2457 | 3.3883 | 0.85999 | 0.37372 | 2.3011 | 7.9512 | 2.1802 | 3.647
[18 empty] | 02/16 13:00:00 | 5.4403 | 2.2625 | 2.4045 | 5.4127 | 1.5914 | 3.4013 | 5.4051 | 1.4981 | 3.608 | 0.3103 | 0.16293 | 1.9045 | 0.28274 | 0.10199 | 2.7722 | 6.5128 | 1.7821 | 3.6546 | 6.5051 | 1.6848 | 3.861 | 6.5293 | 2.2195 | 2.9417 | 3.2128 | 0.94612 | 3.3958 | 6.5128 | 1.6107 | 4.0436 | 6.5404 | 2.2925 | 2.853 | 0.83274 | 0.24552 | 3.3917 | 0.86031 | 0.37363 | 2.3026 | 7.9514 | 2.1804 | 3.6467
[18 empty] | 02/16 14:00:00 | 5.4402 | 2.2628 | 2.4042 | 5.4126 | 1.5915 | 3.4009 | 5.405 | 1.4983 | 3.6075 | 0.31024 | 0.16293 | 1.9042 | 0.28265 | 0.10197 | 2.7717 | 6.5127 | 1.7822 | 3.6543 | 6.5051 | 1.6849 | 3.8608 | 6.5293 | 2.2197 | 2.9415 | 3.2127 | 0.94616 | 3.3955 | 6.5127 | 1.6108 | 4.0432 | 6.5403 | 2.2927 | 2.8526 | 0.83266 | 0.24532 | 3.3941 | 0.86025 | 0.37341 | 2.3037 | 7.9513 | 2.1805 | 3.6465
[18 empty] | 02/16 15:00:00 | 5.4403 | 2.263 | 2.4041 | 5.4127 | 1.5917 | 3.4007 | 5.4051 | 1.4984 | 3.6073 | 0.31034 | 0.16299 | 1.904 | 0.28268 | 0.102 | 2.7715 | 6.5127 | 1.7824 | 3.654 | 6.5051 | 1.6851 | 3.8604 | 6.5294 | 2.2199 | 2.9413 | 3.2127 | 0.94627 | 3.3951 | 6.5127 | 1.6109 | 4.0429 | 6.5404 | 2.293 | 2.8524 | 0.83269 | 0.24534 | 3.394 | 0.86035 | 0.37353 | 2.3033 | 7.9514 | 2.1807 | 3.6462
[18 empty] | 02/16 16:00:00 | 5.4404 | 2.263 | 2.4041 | 5.4127 | 1.5917 | 3.4007 | 5.4051 | 1.4984 | 3.6073 | 0.31041 | 0.16303 | 1.904 | 0.28271 | 0.10201 | 2.7715 | 6.5128 | 1.7824 | 3.6539 | 6.5051 | 1.6851 | 3.8604 | 6.5294 | 2.22 | 2.9412 | 3.2127 | 0.94629 | 3.3951 | 6.5128 | 1.6109 | 4.043 | 6.5405 | 2.2929 | 2.8524 | 0.83272 | 0.24534 | 3.3941 | 0.86041 | 0.37353 | 2.3034 | 7.9514 | 2.1808 | 3.6461
[18 empty] | 02/16 17:00:00 | 5.4398 | 2.2628 | 2.404 | 5.4122 | 1.5915 | 3.4006 | 5.4046 | 1.4983 | 3.6072 | 0.30979 | 0.16271 | 1.904 | 0.28221 | 0.10183 | 2.7714 | 6.5122 | 1.7823 | 3.6539 | 6.5047 | 1.685 | 3.8603 | 6.5288 | 2.2198 | 2.9412 | 3.2122 | 0.9461 | 3.3952 | 6.5123 | 1.6106 | 4.0433 | 6.5398 | 2.2925 | 2.8527 | 0.83221 | 0.24492 | 3.3979 | 0.85979 | 0.37282 | 2.3062 | 7.9509 | 2.1806 | 3.6461
[18 empty] | 02/16 18:00:00 | 5.4378 | 2.2622 | 2.4038 | 5.4105 | 1.5911 | 3.4004 | 5.403 | 1.4979 | 3.607 | 0.30783 | 0.1617 | 1.9038 | 0.28045 | 0.1012 | 2.7712 | 6.5105 | 1.7819 | 3.6538 | 6.503 | 1.6847 | 3.8602 | 6.527 | 2.2193 | 2.941 | 3.2105 | 0.94554 | 3.3954 | 6.5106 | 1.6102 | 4.0433 | 6.5379 | 2.2919 | 2.8527 | 0.83046 | 0.24381 | 3.4061 | 0.85784 | 0.37118 | 2.3111 | 7.9492 | 2.1803 | 3.646
[18 empty] | 02/16 19:00:00 | 5.4368 | 2.2618 | 2.4037 | 5.4094 | 1.5909 | 3.4003 | 5.402 | 1.4977 | 3.6069 | 0.3068 | 0.16116 | 1.9037 | 0.27939 | 0.10082 | 2.7711 | 6.5095 | 1.7816 | 3.6536 | 6.502 | 1.6845 | 3.86 | 6.5259 | 2.219 | 2.9409 | 3.2094 | 0.94528 | 3.3952 | 6.5095 | 1.61 | 4.0431 | 6.5369 | 2.2916 | 2.8525 | 0.82941 | 0.24356 | 3.4054 | 0.85681 | 0.37092 | 2.31 | 7.9481 | 2.1801 | 3.6458
[18 empty] | 02/16 20:00:00 | 5.436 | 2.2613 | 2.4039 | 5.4086 | 1.5905 | 3.4006 | 5.4011 | 1.4973 | 3.6072 | 0.306 | 0.16073 | 1.9039 | 0.27863 | 0.10054 | 2.7714 | 6.5087 | 1.7814 | 3.6537 | 6.5012 | 1.6842 | 3.86 | 6.5251 | 2.2187 | 2.941 | 3.2087 | 0.94501 | 3.3954 | 6.5088 | 1.6097 | 4.0434 | 6.5361 | 2.2911 | 2.8528 | 0.82864 | 0.2434 | 3.4044 | 0.85601 | 0.37064 | 2.3096 | 7.9474 | 2.1798 | 3.6459
[18 empty] | 02/16 21:00:00 | 5.4353 | 2.2609 | 2.404 | 5.408 | 1.5902 | 3.4007 | 5.4005 | 1.4971 | 3.6074 | 0.3053 | 0.16035 | 1.904 | 0.27796 | 0.10029 | 2.7716 | 6.508 | 1.7811 | 3.654 | 6.5006 | 1.684 | 3.8603 | 6.5244 | 2.2183 | 2.9412 | 3.208 | 0.94474 | 3.3957 | 6.5081 | 1.6095 | 4.0435 | 6.5354 | 2.2907 | 2.8529 | 0.82798 | 0.24325 | 3.4039 | 0.85531 | 0.37036 | 2.3094 | 7.9467 | 2.1795 | 3.6462
[18 empty] | 02/16 22:00:00 | 5.4351 | 2.2609 | 2.404 | 5.4077 | 1.5902 | 3.4007 | 5.4003 | 1.497 | 3.6074 | 0.30512 | 0.16026 | 1.904 | 0.27768 | 0.10019 | 2.7716 | 6.5077 | 1.781 | 3.654 | 6.5004 | 1.6839 | 3.8603 | 6.5242 | 2.2182 | 2.9412 | 3.2077 | 0.94467 | 3.3956 | 6.5078 | 1.6095 | 4.0434 | 6.5352 | 2.2908 | 2.8528 | 0.82769 | 0.24334 | 3.4014 | 0.85513 | 0.37057 | 2.3076 | 7.9464 | 2.1794 | 3.6462
[18 empty] | 02/16 23:00:00 | 5.4354 | 2.2609 | 2.404 | 5.4078 | 1.5902 | 3.4007 | 5.4003 | 1.497 | 3.6074 | 0.3054 | 0.1604 | 1.904 | 0.27777 | 0.10022 | 2.7716 | 6.5078 | 1.781 | 3.654 | 6.5004 | 1.6839 | 3.8603 | 6.5244 | 2.2183 | 2.9412 | 3.2078 | 0.94471 | 3.3955 | 6.5079 | 1.6095 | 4.0433 | 6.5355 | 2.2909 | 2.8528 | 0.82778 | 0.24356 | 3.3986 | 0.85541 | 0.37101 | 2.3056 | 7.9465 | 2.1794 | 3.6462
[18 empty] | 02/16 24:00:00 | 5.4356 | 2.261 | 2.4041 | 5.4079 | 1.5902 | 3.4007 | 5.4004 | 1.497 | 3.6074 | 0.30564 | 0.16052 | 1.904 | 0.2779 | 0.10027 | 2.7716 | 6.5079 | 1.781 | 3.654 | 6.5004 | 1.6839 | 3.8603 | 6.5246 | 2.2183 | 2.9413 | 3.2079 | 0.94475 | 3.3955 | 6.508 | 1.6096 | 4.0433 | 6.5357 | 2.291 | 2.8528 | 0.82791 | 0.24368 | 3.3975 | 0.85565 | 0.37117 | 2.3053 | 7.9466 | 2.1794 | 3.6462
[18 empty] | 02/17 01:00:00 | 5.4357 | 2.2613 | 2.4038 | 5.4079 | 1.5904 | 3.4003 | 5.4004 | 1.4972 | 3.607 | 0.30572 | 0.16059 | 1.9037 | 0.27794 | 0.1003 | 2.7712 | 6.508 | 1.7811 | 3.6538 | 6.5004 | 1.684 | 3.8602 | 6.5247 | 2.2185 | 2.9411 | 3.208 | 0.94483 | 3.3953 | 6.508 | 1.6097 | 4.0429 | 6.5358 | 2.2913 | 2.8524 | 0.82795 | 0.24373 | 3.3971 | 0.85572 | 0.37121 | 2.3052 | 7.9467 | 2.1795 | 3.6461
[18 empty] | 02/17 02:00:00 | 5.4359 | 2.2615 | 2.4036 | 5.4081 | 1.5906 | 3.4001 | 5.4004 | 1.4973 | 3.6067 | 0.3059 | 0.1607 | 1.9036 | 0.27807 | 0.10035 | 2.7709 | 6.5081 | 1.7813 | 3.6535 | 6.5005 | 1.6841 | 3.8599 | 6.5249 | 2.2187 | 2.9409 | 3.2081 | 0.94496 | 3.395 | 6.5081 | 1.6098 | 4.0427 | 6.536 | 2.2915 | 2.8522 | 0.82808 | 0.24382 | 3.3963 | 0.85591 | 0.37137 | 2.3047 | 7.9468 | 2.1798 | 3.6458
[18 empty] | 02/17 03:00:00 | 5.4359 | 2.2618 | 2.4034 | 5.4081 | 1.5908 | 3.3997 | 5.4005 | 1.4975 | 3.6063 | 0.30589 | 0.16072 | 1.9033 | 0.27809 | 0.10038 | 2.7705 | 6.5081 | 1.7815 | 3.6533 | 6.5005 | 1.6842 | 3.8597 | 6.5249 | 2.2189 | 2.9406 | 3.2081 | 0.94505 | 3.3947 | 6.5082 | 1.61 | 4.0423 | 6.5359 | 2.2918 | 2.8519 | 0.8281 | 0.24382 | 3.3964 | 0.8559 | 0.37133 | 2.305 | 7.9468 | 2.1799 | 3.6455
[18 empty] | 02/17 04:00:00 | 5.4357 | 2.2619 | 2.4032 | 5.408 | 1.5908 | 3.3995 | 5.4004 | 1.4976 | 3.6061 | 0.30573 | 0.16065 | 1.9031 | 0.27799 | 0.10035 | 2.7702 | 6.508 | 1.7816 | 3.6529 | 6.5005 | 1.6844 | 3.8593 | 6.5247 | 2.219 | 2.9404 | 3.208 | 0.94511 | 3.3943 | 6.5081 | 1.6101 | 4.0421 | 6.5358 | 2.2919 | 2.8517 | 0.828 | 0.24375 | 3.3969 | 0.85574 | 0.3712 | 2.3053 | 7.9467 | 2.1801 | 3.6452
[18 empty] | 02/17 05:00:00 | 5.4357 | 2.2619 | 2.4032 | 5.408 | 1.5908 | 3.3995 | 5.4004 | 1.4976 | 3.6061 | 0.30575 | 0.16066 | 1.9031 | 0.27799 | 0.10035 | 2.7702 | 6.508 | 1.7816 | 3.6529 | 6.5005 | 1.6844 | 3.8592 | 6.5248 | 2.2191 | 2.9403 | 3.208 | 0.94513 | 3.3943 | 6.5081 | 1.6101 | 4.0421 | 6.5358 | 2.2919 | 2.8517 | 0.828 | 0.24378 | 3.3966 | 0.85575 | 0.37127 | 2.3049 | 7.9467 | 2.1801 | 3.6451
[18 empty] | 02/17 06:00:00 | 5.4359 | 2.2619 | 2.4032 | 5.4081 | 1.5909 | 3.3995 | 5.4005 | 1.4976 | 3.6061 | 0.30589 | 0.16073 | 1.9031 | 0.27809 | 0.10039 | 2.7702 | 6.5081 | 1.7816 | 3.6529 | 6.5005 | 1.6844 | 3.8592 | 6.5249 | 2.2191 | 2.9403 | 3.2081 | 0.94517 | 3.3942 | 6.5082 | 1.6101 | 4.0421 | 6.5359 | 2.292 | 2.8517 | 0.8281 | 0.24385 | 3.396 | 0.8559 | 0.37142 | 2.3044 | 7.9468 | 2.1801 | 3.6451
[18 empty] | 02/17 07:00:00 | 5.4362 | 2.2618 | 2.4035 | 5.4083 | 1.5907 | 3.3999 | 5.4006 | 1.4975 | 3.6065 | 0.30617 | 0.16085 | 1.9034 | 0.27829 | 0.10044 | 2.7707 | 6.5083 | 1.7816 | 3.6531 | 6.5006 | 1.6844 | 3.8594 | 6.5252 | 2.2191 | 2.9405 | 3.2083 | 0.94516 | 3.3945 | 6.5084 | 1.61 | 4.0425 | 6.5362 | 2.2918 | 2.852 | 0.82829 | 0.24394 | 3.3955 | 0.85618 | 0.37161 | 2.304 | 7.9471 | 2.1801 | 3.6453
[18 empty] | 02/17 08:00:00 | 5.4371 | 2.2619 | 2.4038 | 5.409 | 1.5908 | 3.4002 | 5.4013 | 1.4975 | 3.6069 | 0.30709 | 0.16131 | 1.9037 | 0.27899 | 0.10068 | 2.771 | 6.509 | 1.7816 | 3.6535 | 6.5013 | 1.6844 | 3.8598 | 6.526 | 2.2191 | 2.9408 | 3.209 | 0.9453 | 3.3947 | 6.509 | 1.6102 | 4.0425 | 6.5371 | 2.2921 | 2.852 | 0.829 | 0.24439 | 3.3921 | 0.8571 | 0.3724 | 2.3016 | 7.9478 | 2.1801 | 3.6457
[18 empty] | 02/17 09:00:00 | 5.4384 | 2.2621 | 2.4042 | 5.4102 | 1.5909 | 3.4008 | 5.4025 | 1.4976 | 3.6074 | 0.30835 | 0.16194 | 1.9041 | 0.28022 | 0.1011 | 2.7716 | 6.5102 | 1.7818 | 3.6538 | 6.5025 | 1.6845 | 3.8602 | 6.5273 | 2.2193 | 2.9412 | 3.2102 | 0.94559 | 3.3949 | 6.5102 | 1.6103 | 4.0429 | 6.5384 | 2.2922 | 2.8525 | 0.83023 | 0.24503 | 3.3882 | 0.85836 | 0.37317 | 2.3002 | 7.949 | 2.1802 | 3.646
[18 empty] | 02/17 10:00:00 | 5.4392 | 2.2622 | 2.4044 | 5.4113 | 1.591 | 3.4011 | 5.4035 | 1.4977 | 3.6078 | 0.30924 | 0.16238 | 1.9044 | 0.28128 | 0.10147 | 2.772 | 6.5113 | 1.7818 | 3.6543 | 6.5035 | 1.6846 | 3.8607 | 6.5282 | 2.2193 | 2.9415 | 3.2113 | 0.94578 | 3.3954 | 6.5113 | 1.6104 | 4.0433 | 6.5393 | 2.2923 | 2.8528 | 0.83128 | 0.24537 | 3.3879 | 0.85925 | 0.37346 | 2.3008 | 7.95 | 2.1802 | 3.6464
[18 empty] | 02/17 11:00:00 | 5.4399 | 2.2624 | 2.4045 | 5.4119 | 1.5912 | 3.4012 | 5.4041 | 1.4979 | 3.6078 | 0.30986 | 0.1627 | 1.9044 | 0.28192 | 0.1017 | 2.7721 | 6.5119 | 1.7819 | 3.6544 | 6.5041 | 1.6847 | 3.8608 | 6.5288 | 2.2195 | 2.9416 | 3.2119 | 0.94593 | 3.3955 | 6.5119 | 1.6105 | 4.0434 | 6.5399 | 2.2924 | 2.8529 | 0.83192 | 0.24543 | 3.3896 | 0.85986 | 0.37359 | 2.3016 | 7.9506 | 2.1803 | 3.6466
[18 empty] | 02/17 12:00:00 | 5.4403 | 2.2625 | 2.4045 | 5.4124 | 1.5913 | 3.4013 | 5.4046 | 1.498 | 3.6079 | 0.31026 | 0.16291 | 1.9045 | 0.28239 | 0.10187 | 2.7721 | 6.5124 | 1.782 | 3.6545 | 6.5046 | 1.6848 | 3.8609 | 6.5293 | 2.2196 | 2.9417 | 3.2124 | 0.94605 | 3.3956 | 6.5124 | 1.6106 | 4.0434 | 6.5403 | 2.2925 | 2.8529 | 0.8324 | 0.24548 | 3.3909 | 0.86026 | 0.37364 | 2.3024 | 7.9511 | 2.1804 | 3.6466
[18 empty] | 02/17 13:00:00 | 5.4403 | 2.2628 | 2.4042 | 5.4125 | 1.5915 | 3.4009 | 5.4048 | 1.4982 | 3.6075 | 0.31028 | 0.16295 | 1.9042 | 0.28252 | 0.10193 | 2.7717 | 6.5125 | 1.7822 | 3.6543 | 6.5048 | 1.6849 | 3.8607 | 6.5293 | 2.2197 | 2.9415 | 3.2125 | 0.94613 | 3.3955 | 6.5126 | 1.6108 | 4.0432 | 6.5403 | 2.2927 | 2.8527 | 0.83253 | 0.24537 | 3.3929 | 0.86029 | 0.37347 | 2.3035 | 7.9512 | 2.1805 | 3.6465
[18 empty] | 02/17 14:00:00 | 5.4399 | 2.2628 | 2.404 | 5.4123 | 1.5916 | 3.4006 | 5.4046 | 1.4983 | 3.6072 | 0.3099 | 0.16277 | 1.904 | 0.28226 | 0.10185 | 2.7714 | 6.5123 | 1.7823 | 3.654 | 6.5046 | 1.685 | 3.8604 | 6.529 | 2.2198 | 2.9412 | 3.2123 | 0.94613 | 3.3952 | 6.5123 | 1.6108 | 4.043 | 6.54 | 2.2927 | 2.8525 | 0.83227 | 0.24511 | 3.3955 | 0.85991 | 0.37307 | 2.3049 | 7.951 | 2.1806 | 3.6462
[18 empty] | 02/17 15:00:00 | 5.4397 | 2.263 | 2.4037 | 5.4121 | 1.5917 | 3.4002 | 5.4045 | 1.4984 | 3.6068 | 0.30967 | 0.16267 | 1.9036 | 0.28206 | 0.10179 | 2.771 | 6.5121 | 1.7823 | 3.6537 | 6.5045 | 1.685 | 3.8602 | 6.5288 | 2.2199 | 2.941 | 3.2121 | 0.94617 | 3.3949 | 6.5121 | 1.6109 | 4.0425 | 6.5397 | 2.293 | 2.8521 | 0.83207 | 0.24504 | 3.3956 | 0.85968 | 0.37303 | 2.3046 | 7.9508 | 2.1807 | 3.6459
[18 empty] | 02/17 16:00:00 | 5.4395 | 2.2631 | 2.4035 | 5.4119 | 1.5918 | 3.3999 | 5.4043 | 1.4985 | 3.6065 | 0.30947 | 0.16259 | 1.9034 | 0.28187 | 0.10174 | 2.7707 | 6.5119 | 1.7825 | 3.6533 | 6.5043 | 1.6852 | 3.8598 | 6.5286 | 2.2201 | 2.9407 | 3.2119 | 0.94621 | 3.3945 | 6.512 | 1.6109 | 4.0423 | 6.5395 | 2.2931 | 2.8519 | 0.83188 | 0.24499 | 3.3956 | 0.85948 | 0.37298 | 2.3043 | 7.9506 | 2.1809 | 3.6456
[18 empty] | 02/17 17:00:00 | 5.4393 | 2.263 | 2.4035 | 5.4117 | 1.5917 | 3.3999 | 5.4041 | 1.4984 | 3.6065 | 0.30926 | 0.16248 | 1.9034 | 0.28168 | 0.10166 | 2.7706 | 6.5117 | 1.7824 | 3.6533 | 6.5042 | 1.6852 | 3.8597 | 6.5283 | 2.22 | 2.9406 | 3.2117 | 0.94617 | 3.3945 | 6.5118 | 1.6109 | 4.0424 | 6.5393 | 2.293 | 2.8519 | 0.83169 | 0.24491 | 3.3959 | 0.85927 | 0.37287 | 2.3045 | 7.9504 | 2.1809 | 3.6455
[18 empty] | 02/17 18:00:00 | 5.4381 | 2.2627 | 2.4034 | 5.4107 | 1.5915 | 3.3998 | 5.4032 | 1.4982 | 3.6064 | 0.30815 | 0.1619 | 1.9033 | 0.28073 | 0.10133 | 2.7705 | 6.5108 | 1.7822 | 3.6532 | 6.5033 | 1.685 | 3.8596 | 6.5273 | 2.2197 | 2.9406 | 3.2108 | 0.94584 | 3.3946 | 6.5108 | 1.6105 | 4.0427 | 6.5382 | 2.2924 | 2.8521 | 0.83074 | 0.24427 | 3.401 | 0.85815 | 0.37182 | 2.308 | 7.9494 | 2.1807 | 3.6454
[18 empty] | 02/17 19:00:00 | 5.4364 | 2.2621 | 2.4033 | 5.409 | 1.5911 | 3.3996 | 5.4015 | 1.4978 | 3.6062 | 0.30645 | 0.16102 | 1.9031 | 0.279 | 0.10071 | 2.7703 | 6.5091 | 1.7818 | 3.653 | 6.5017 | 1.6846 | 3.8594 | 6.5256 | 2.2193 | 2.9404 | 3.2091 | 0.94532 | 3.3947 | 6.5091 | 1.6101 | 4.0426 | 6.5365 | 2.2919 | 2.852 | 0.82901 | 0.24333 | 3.407 | 0.85646 | 0.37064 | 2.3107 | 7.9477 | 2.1803 | 3.6453
[18 empty] | 02/17 20:00:00 | 5.4357 | 2.2616 | 2.4035 | 5.4083 | 1.5907 | 3.3999 | 5.401 | 1.4976 | 3.6066 | 0.30573 | 0.16063 | 1.9034 | 0.27834 | 0.10046 | 2.7707 | 6.5084 | 1.7816 | 3.6531 | 6.5012 | 1.6845 | 3.8594 | 6.5249 | 2.219 | 2.9405 | 3.2084 | 0.94511 | 3.3947 | 6.5085 | 1.6099 | 4.0427 | 6.5358 | 2.2915 | 2.8522 | 0.82835 | 0.24335 | 3.4039 | 0.85574 | 0.3706 | 2.309 | 7.947 | 2.1801 | 3.6453
[18 empty] | 02/17 21:00:00 | 5.4353 | 2.2613 | 2.4036 | 5.4079 | 1.5905 | 3.4001 | 5.4007 | 1.4974 | 3.6068 | 0.30535 | 0.16041 | 1.9035 | 0.27792 | 0.1003 | 2.7709 | 6.508 | 1.7814 | 3.6534 | 6.5008 | 1.6843 | 3.8597 | 6.5245 | 2.2187 | 2.9407 | 3.208 | 0.94492 | 3.395 | 6.508 | 1.6098 | 4.0428 | 6.5354 | 2.2913 | 2.8523 | 0.82794 | 0.24338 | 3.4018 | 0.85535 | 0.37064 | 2.3078 | 7.9466 | 2.1798 | 3.6456
[18 empty] | 02/17 22:00:00 | 5.4354 | 2.2613 | 2.4036 | 5.4078 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30535 | 0.16041 | 1.9035 | 0.27781 | 0.10026 | 2.7709 | 6.5079 | 1.7813 | 3.6534 | 6.5006 | 1.6842 | 3.8598 | 6.5244 | 2.2186 | 2.9408 | 3.2079 | 0.9449 | 3.3949 | 6.5079 | 1.6098 | 4.0427 | 6.5354 | 2.2913 | 2.8522 | 0.82782 | 0.24353 | 3.3993 | 0.85536 | 0.37091 | 2.3061 | 7.9465 | 2.1797 | 3.6457
[18 empty] | 02/17 23:00:00 | 5.4356 | 2.2614 | 2.4036 | 5.4079 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30564 | 0.16056 | 1.9035 | 0.27794 | 0.10031 | 2.7709 | 6.508 | 1.7813 | 3.6534 | 6.5006 | 1.6842 | 3.8598 | 6.5247 | 2.2187 | 2.9408 | 3.208 | 0.94495 | 3.3949 | 6.508 | 1.6098 | 4.0427 | 6.5357 | 2.2915 | 2.8522 | 0.82795 | 0.24372 | 3.3972 | 0.85565 | 0.37125 | 2.3048 | 7.9467 | 2.1798 | 3.6457
[18 empty] | 02/17 24:00:00 | 5.4358 | 2.2615 | 2.4036 | 5.408 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30575 | 0.16062 | 1.9036 | 0.27802 | 0.10033 | 2.7709 | 6.5081 | 1.7814 | 3.6534 | 6.5006 | 1.6842 | 3.8598 | 6.5248 | 2.2187 | 2.9408 | 3.2081 | 0.94496 | 3.3949 | 6.5081 | 1.6098 | 4.0427 | 6.5358 | 2.2914 | 2.8523 | 0.82803 | 0.24376 | 3.3968 | 0.85576 | 0.37127 | 2.305 | 7.9467 | 2.1798 | 3.6457
[18 empty] | 02/18 01:00:00 | 5.4357 | 2.2617 | 2.4033 | 5.408 | 1.5907 | 3.3997 | 5.4005 | 1.4975 | 3.6063 | 0.30568 | 0.16061 | 1.9032 | 0.27799 | 0.10034 | 2.7705 | 6.508 | 1.7814 | 3.6532 | 6.5006 | 1.6842 | 3.8597 | 6.5247 | 2.2188 | 2.9406 | 3.208 | 0.94502 | 3.3947 | 6.5081 | 1.61 | 4.0423 | 6.5357 | 2.2917 | 2.8519 | 0.828 | 0.24376 | 3.3968 | 0.85569 | 0.3712 | 2.3052 | 7.9467 | 2.1799 | 3.6455
[18 empty] | 02/18 02:00:00 | 5.4358 | 2.2622 | 2.4029 | 5.408 | 1.591 | 3.3991 | 5.4005 | 1.4978 | 3.6057 | 0.30576 | 0.16069 | 1.9028 | 0.27803 | 0.10038 | 2.7698 | 6.5081 | 1.7817 | 3.6527 | 6.5006 | 1.6844 | 3.8592 | 6.5248 | 2.2192 | 2.9402 | 3.2081 | 0.9452 | 3.394 | 6.5081 | 1.6103 | 4.0416 | 6.5358 | 2.2922 | 2.8513 | 0.82804 | 0.24385 | 3.3957 | 0.85577 | 0.37139 | 2.3042 | 7.9468 | 2.1802 | 3.645
[18 empty] | 02/18 03:00:00 | 5.4361 | 2.2627 | 2.4025 | 5.4083 | 1.5914 | 3.3985 | 5.4006 | 1.4981 | 3.605 | 0.30612 | 0.16092 | 1.9023 | 0.27827 | 0.10049 | 2.7691 | 6.5083 | 1.782 | 3.6522 | 6.5007 | 1.6847 | 3.8586 | 6.5251 | 2.2196 | 2.9397 | 3.2083 | 0.94546 | 3.3934 | 6.5083 | 1.6106 | 4.041 | 6.5362 | 2.2928 | 2.8507 | 0.82828 | 0.24407 | 3.3937 | 0.85613 | 0.37181 | 2.3026 | 7.947 | 2.1806 | 3.6445
[18 empty] | 02/18 04:00:00 | 5.4363 | 2.2629 | 2.4024 | 5.4084 | 1.5915 | 3.3982 | 5.4007 | 1.4982 | 3.6048 | 0.30634 | 0.16105 | 1.9022 | 0.27844 | 0.10056 | 2.7688 | 6.5085 | 1.7823 | 3.6518 | 6.5008 | 1.6849 | 3.8582 | 6.5253 | 2.2199 | 2.9394 | 3.2085 | 0.94562 | 3.393 | 6.5085 | 1.6107 | 4.0408 | 6.5364 | 2.293 | 2.8505 | 0.82845 | 0.24414 | 3.3934 | 0.85634 | 0.37192 | 2.3025 | 7.9472 | 2.1808 | 3.6441
[18 empty] | 02/18 05:00:00 | 5.4364 | 2.263 | 2.4024 | 5.4085 | 1.5916 | 3.3983 | 5.4008 | 1.4982 | 3.6048 | 0.30643 | 0.1611 | 1.9022 | 0.27854 | 0.1006 | 2.7688 | 6.5086 | 1.7823 | 3.6518 | 6.5009 | 1.685 | 3.8582 | 6.5254 | 2.22 | 2.9394 | 3.2086 | 0.94566 | 3.3929 | 6.5086 | 1.6107 | 4.0409 | 6.5365 | 2.293 | 2.8506 | 0.82855 | 0.24414 | 3.3938 | 0.85644 | 0.3719 | 2.3029 | 7.9473 | 2.1809 | 3.6441
[18 empty] | 02/18 06:00:00 | 5.4363 | 2.2627 | 2.4026 | 5.4085 | 1.5914 | 3.3987 | 5.4008 | 1.4981 | 3.6052 | 0.30634 | 0.16102 | 1.9025 | 0.27851 | 0.10057 | 2.7693 | 6.5085 | 1.7822 | 3.652 | 6.5009 | 1.6849 | 3.8583 | 6.5253 | 2.2198 | 2.9395 | 3.2085 | 0.94557 | 3.3932 | 6.5086 | 1.6105 | 4.0413 | 6.5364 | 2.2927 | 2.851 | 0.82851 | 0.24403 | 3.3951 | 0.85635 | 0.37168 | 2.304 | 7.9473 | 2.1808 | 3.6442
[18 empty] | 02/18 07:00:00 | 5.4362 | 2.2622 | 2.4031 | 5.4084 | 1.5911 | 3.3993 | 5.4008 | 1.4978 | 3.6059 | 0.30623 | 0.16092 | 1.9029 | 0.27844 | 0.10052 | 2.77 | 6.5085 | 1.7819 | 3.6525 | 6.5009 | 1.6847 | 3.8588 | 6.5252 | 2.2195 | 2.94 | 3.2085 | 0.94539 | 3.3938 | 6.5085 | 1.6102 | 4.0419 | 6.5363 | 2.2922 | 2.8515 | 0.82845 | 0.24392 | 3.3964 | 0.85623 | 0.3715 | 2.3048 | 7.9472 | 2.1805 | 3.6447
[18 empty] | 02/18 08:00:00 | 5.4364 | 2.2621 | 2.4033 | 5.4086 | 1.591 | 3.3995 | 5.401 | 1.4977 | 3.6061 | 0.30643 | 0.16101 | 1.9031 | 0.27862 | 0.10058 | 2.7703 | 6.5087 | 1.7818 | 3.6529 | 6.501 | 1.6845 | 3.8592 | 6.5254 | 2.2193 | 2.9403 | 3.2087 | 0.94535 | 3.3941 | 6.5087 | 1.6103 | 4.042 | 6.5365 | 2.2922 | 2.8516 | 0.82863 | 0.24407 | 3.3951 | 0.85643 | 0.37172 | 2.304 | 7.9474 | 2.1803 | 3.6451
[18 empty] | 02/18 09:00:00 | 5.4372 | 2.2624 | 2.4033 | 5.4096 | 1.5912 | 3.3997 | 5.4018 | 1.4979 | 3.6062 | 0.3072 | 0.16141 | 1.9032 | 0.27955 | 0.10091 | 2.7704 | 6.5096 | 1.782 | 3.653 | 6.5018 | 1.6847 | 3.8594 | 6.5262 | 2.2195 | 2.9404 | 3.2096 | 0.94565 | 3.3941 | 6.5096 | 1.6106 | 4.0418 | 6.5373 | 2.2925 | 2.8516 | 0.82956 | 0.24472 | 3.3898 | 0.85721 | 0.37243 | 2.3016 | 7.9482 | 2.1805 | 3.6452
[18 empty] | 02/18 10:00:00 | 5.4386 | 2.2625 | 2.4037 | 5.411 | 1.5914 | 3.4002 | 5.4032 | 1.4981 | 3.6068 | 0.30856 | 0.16209 | 1.9037 | 0.28103 | 0.10142 | 2.771 | 6.511 | 1.7822 | 3.6533 | 6.5032 | 1.6849 | 3.8597 | 6.5276 | 2.2198 | 2.9407 | 3.211 | 0.94602 | 3.3943 | 6.5111 | 1.6108 | 4.0422 | 6.5386 | 2.2928 | 2.8518 | 0.83103 | 0.24548 | 3.3854 | 0.85857 | 0.37342 | 2.2992 | 7.9496 | 2.1807 | 3.6455
[18 empty] | 02/18 11:00:00 | 5.4395 | 2.2627 | 2.404 | 5.412 | 1.5915 | 3.4006 | 5.4042 | 1.4982 | 3.6072 | 0.30951 | 0.16256 | 1.9039 | 0.28197 | 0.10174 | 2.7714 | 6.512 | 1.7823 | 3.6538 | 6.5042 | 1.685 | 3.8602 | 6.5286 | 2.2198 | 2.9411 | 3.212 | 0.94616 | 3.3948 | 6.512 | 1.6108 | 4.0427 | 6.5396 | 2.2928 | 2.8522 | 0.83198 | 0.24564 | 3.387 | 0.85952 | 0.37372 | 2.2999 | 7.9506 | 2.1807 | 3.646
[18 empty] | 02/18 12:00:00 | 5.4399 | 2.2628 | 2.404 | 5.4123 | 1.5916 | 3.4006 | 5.4046 | 1.4983 | 3.6072 | 0.30995 | 0.16279 | 1.904 | 0.28231 | 0.10187 | 2.7714 | 6.5123 | 1.7823 | 3.6539 | 6.5045 | 1.685 | 3.8603 | 6.529 | 2.2199 | 2.9412 | 3.2123 | 0.9462 | 3.395 | 6.5123 | 1.6108 | 4.0429 | 6.54 | 2.2928 | 2.8523 | 0.83232 | 0.24549 | 3.3904 | 0.85995 | 0.37364 | 2.3015 | 7.951 | 2.1807 | 3.6461
[18 empty] | 02/18 13:00:00 | 5.4402 | 2.2629 | 2.4041 | 5.4126 | 1.5916 | 3.4006 | 5.4049 | 1.4983 | 3.6073 | 0.31025 | 0.16294 | 1.904 | 0.28256 | 0.10195 | 2.7715 | 6.5126 | 1.7824 | 3.6539 | 6.5049 | 1.6851 | 3.8603 | 6.5293 | 2.22 | 2.9412 | 3.2126 | 0.94627 | 3.395 | 6.5126 | 1.6109 | 4.0428 | 6.5403 | 2.293 | 2.8523 | 0.83257 | 0.24547 | 3.3917 | 0.86025 | 0.37368 | 2.3021 | 7.9512 | 2.1808 | 3.6461
[18 empty] | 02/18 14:00:00 | 5.4409 | 2.2634 | 2.4038 | 5.4131 | 1.5919 | 3.4003 | 5.4055 | 1.4986 | 3.6069 | 0.31086 | 0.16329 | 1.9038 | 0.28309 | 0.10216 | 2.7711 | 6.5131 | 1.7826 | 3.6538 | 6.5055 | 1.6853 | 3.8602 | 6.5299 | 2.2202 | 2.9411 | 3.2131 | 0.9465 | 3.3947 | 6.5131 | 1.6112 | 4.0424 | 6.5409 | 2.2935 | 2.852 | 0.8331 | 0.24575 | 3.39 | 0.86087 | 0.37414 | 2.3009 | 7.9518 | 2.181 | 3.646
[18 empty] | 02/18 15:00:00 | 5.4407 | 2.2638 | 2.4034 | 5.4131 | 1.5922 | 3.3997 | 5.4055 | 1.4989 | 3.6063 | 0.31074 | 0.16327 | 1.9033 | 0.28311 | 0.10219 | 2.7704 | 6.5131 | 1.7828 | 3.6533 | 6.5055 | 1.6855 | 3.8598 | 6.5298 | 2.2205 | 2.9406 | 3.2131 | 0.94664 | 3.3942 | 6.5132 | 1.6114 | 4.042 | 6.5408 | 2.2937 | 2.8516 | 0.83311 | 0.24562 | 3.3919 | 0.86075 | 0.37383 | 2.3025 | 7.9518 | 2.1813 | 3.6455
[18 empty] | 02/18 16:00:00 | 5.4399 | 2.2637 | 2.4031 | 5.4123 | 1.5922 | 3.3994 | 5.4047 | 1.4989 | 3.6059 | 0.30995 | 0.16287 | 1.903 | 0.28233 | 0.10192 | 2.77 | 6.5124 | 1.7828 | 3.6528 | 6.5048 | 1.6855 | 3.8593 | 6.5289 | 2.2205 | 2.9403 | 3.2124 | 0.94648 | 3.394 | 6.5124 | 1.6112 | 4.042 | 6.54 | 2.2936 | 2.8515 | 0.83234 | 0.24501 | 3.3972 | 0.85995 | 0.37305 | 2.3052 | 7.951 | 2.1813 | 3.6451
[18 empty] | 02/18 17:00:00 | 5.4391 | 2.2634 | 2.4031 | 5.4115 | 1.592 | 3.3993 | 5.4041 | 1.4987 | 3.6058 | 0.30909 | 0.16243 | 1.9029 | 0.28154 | 0.10164 | 2.7699 | 6.5116 | 1.7827 | 3.6527 | 6.5041 | 1.6854 | 3.8591 | 6.5281 | 2.2203 | 2.9401 | 3.2116 | 0.94627 | 3.3939 | 6.5116 | 1.6111 | 4.0418 | 6.5392 | 2.2933 | 2.8514 | 0.83155 | 0.24464 | 3.3991 | 0.8591 | 0.3725 | 2.3063 | 7.9503 | 2.1812 | 3.6449
[18 empty] | 02/18 18:00:00 | 5.4381 | 2.2631 | 2.403 | 5.4104 | 1.5917 | 3.3991 | 5.403 | 1.4985 | 3.6057 | 0.30813 | 0.16194 | 1.9028 | 0.28036 | 0.10122 | 2.7698 | 6.5104 | 1.7824 | 3.6526 | 6.503 | 1.6852 | 3.859 | 6.5271 | 2.2201 | 2.9401 | 3.2104 | 0.94591 | 3.394 | 6.5105 | 1.6107 | 4.042 | 6.5382 | 2.2929 | 2.8515 | 0.83037 | 0.24402 | 3.4028 | 0.85814 | 0.37192 | 2.3073 | 7.9491 | 2.1809 | 3.6449
[18 empty] | 02/18 19:00:00 | 5.4365 | 2.2626 | 2.4028 | 5.4088 | 1.5913 | 3.3989 | 5.4014 | 1.4981 | 3.6055 | 0.30651 | 0.1611 | 1.9027 | 0.27883 | 0.10068 | 2.7696 | 6.5089 | 1.7821 | 3.6524 | 6.5015 | 1.6848 | 3.8588 | 6.5255 | 2.2196 | 2.9399 | 3.2089 | 0.94546 | 3.394 | 6.509 | 1.6104 | 4.0419 | 6.5366 | 2.2924 | 2.8515 | 0.82885 | 0.24335 | 3.406 | 0.85652 | 0.37079 | 2.31 | 7.9476 | 2.1806 | 3.6447
[18 empty] | 02/18 20:00:00 | 5.4357 | 2.262 | 2.403 | 5.4082 | 1.591 | 3.3992 | 5.4009 | 1.4978 | 3.6059 | 0.30572 | 0.16066 | 1.9029 | 0.27821 | 0.10044 | 2.77 | 6.5083 | 1.7819 | 3.6525 | 6.5009 | 1.6847 | 3.8588 | 6.5248 | 2.2193 | 2.94 | 3.2083 | 0.94527 | 3.394 | 6.5083 | 1.6102 | 4.0421 | 6.5358 | 2.292 | 2.8516 | 0.82823 | 0.24339 | 3.4029 | 0.85573 | 0.37066 | 2.3086 | 7.9469 | 2.1804 | 3.6448
[18 empty] | 02/18 21:00:00 | 5.4355 | 2.2616 | 2.4034 | 5.408 | 1.5907 | 3.3999 | 5.4007 | 1.4975 | 3.6065 | 0.30554 | 0.16053 | 1.9034 | 0.27798 | 0.10033 | 2.7706 | 6.508 | 1.7816 | 3.653 | 6.5007 | 1.6844 | 3.8593 | 6.5246 | 2.2189 | 2.9404 | 3.208 | 0.94506 | 3.3945 | 6.5081 | 1.6099 | 4.0426 | 6.5356 | 2.2915 | 2.852 | 0.82799 | 0.2435 | 3.4003 | 0.85555 | 0.37088 | 2.3068 | 7.9467 | 2.18 | 3.6452
[18 empty] | 02/18 22:00:00 | 5.4357 | 2.2615 | 2.4036 | 5.408 | 1.5906 | 3.4001 | 5.4006 | 1.4974 | 3.6068 | 0.30573 | 0.16061 | 1.9036 | 0.27802 | 0.10034 | 2.7709 | 6.5081 | 1.7814 | 3.6534 | 6.5007 | 1.6842 | 3.8597 | 6.5247 | 2.2187 | 2.9407 | 3.2081 | 0.94498 | 3.3948 | 6.5081 | 1.6098 | 4.0427 | 6.5358 | 2.2915 | 2.8522 | 0.82804 | 0.24368 | 3.3981 | 0.85574 | 0.3712 | 2.3053 | 7.9468 | 2.1798 | 3.6456
[18 empty] | 02/18 23:00:00 | 5.4357 | 2.2614 | 2.4036 | 5.4079 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30566 | 0.16057 | 1.9035 | 0.27795 | 0.10031 | 2.7709 | 6.508 | 1.7813 | 3.6534 | 6.5006 | 1.6842 | 3.8598 | 6.5247 | 2.2187 | 2.9408 | 3.208 | 0.94493 | 3.3949 | 6.508 | 1.6098 | 4.0428 | 6.5357 | 2.2914 | 2.8523 | 0.82796 | 0.24366 | 3.398 | 0.85566 | 0.3711 | 2.3058 | 7.9467 | 2.1798 | 3.6457
[18 empty] | 02/18 24:00:00 | 5.4356 | 2.2614 | 2.4036 | 5.4079 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6067 | 0.30562 | 0.16055 | 1.9035 | 0.2779 | 0.10029 | 2.7709 | 6.5079 | 1.7813 | 3.6534 | 6.5005 | 1.6842 | 3.8598 | 6.5246 | 2.2187 | 2.9408 | 3.2079 | 0.94492 | 3.3949 | 6.508 | 1.6098 | 4.0427 | 6.5357 | 2.2914 | 2.8522 | 0.82791 | 0.24366 | 3.3978 | 0.85563 | 0.3711 | 2.3056 | 7.9466 | 2.1797 | 3.6457
[18 empty] | 02/19 01:00:00 | 5.4359 | 2.2615 | 2.4036 | 5.408 | 1.5906 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30587 | 0.16068 | 1.9036 | 0.27805 | 0.10034 | 2.7709 | 6.5081 | 1.7814 | 3.6534 | 6.5005 | 1.6842 | 3.8598 | 6.5249 | 2.2187 | 2.9408 | 3.2081 | 0.94498 | 3.3949 | 6.5081 | 1.6098 | 4.0427 | 6.5359 | 2.2915 | 2.8522 | 0.82806 | 0.2438 | 3.3965 | 0.85587 | 0.37137 | 2.3047 | 7.9468 | 2.1798 | 3.6457
[18 empty] | 02/19 02:00:00 | 5.4361 | 2.2619 | 2.4034 | 5.4082 | 1.5908 | 3.3997 | 5.4006 | 1.4975 | 3.6063 | 0.30611 | 0.16083 | 1.9033 | 0.27823 | 0.10043 | 2.7705 | 6.5083 | 1.7815 | 3.6533 | 6.5006 | 1.6842 | 3.8597 | 6.5251 | 2.2189 | 2.9406 | 3.2083 | 0.9451 | 3.3946 | 6.5083 | 1.6101 | 4.0423 | 6.5362 | 2.2919 | 2.8519 | 0.82824 | 0.24393 | 3.3954 | 0.85611 | 0.37157 | 2.304 | 7.947 | 2.1799 | 3.6455
[18 empty] | 02/19 03:00:00 | 5.4364 | 2.2621 | 2.4033 | 5.4085 | 1.591 | 3.3995 | 5.4008 | 1.4977 | 3.6061 | 0.30643 | 0.16101 | 1.9031 | 0.27849 | 0.10053 | 2.7703 | 6.5085 | 1.7817 | 3.653 | 6.5008 | 1.6844 | 3.8594 | 6.5254 | 2.2192 | 2.9404 | 3.2085 | 0.94528 | 3.3943 | 6.5086 | 1.6102 | 4.042 | 6.5365 | 2.2922 | 2.8516 | 0.8285 | 0.24409 | 3.3943 | 0.85644 | 0.37184 | 2.3033 | 7.9473 | 2.1802 | 3.6452
[18 empty] | 02/19 04:00:00 | 5.4369 | 2.2623 | 2.4033 | 5.4089 | 1.5911 | 3.3996 | 5.4011 | 1.4977 | 3.6062 | 0.30694 | 0.16127 | 1.9032 | 0.27889 | 0.10067 | 2.7703 | 6.5089 | 1.7818 | 3.653 | 6.5011 | 1.6845 | 3.8593 | 6.5259 | 2.2194 | 2.9404 | 3.2089 | 0.94541 | 3.3942 | 6.5089 | 1.6103 | 4.0421 | 6.537 | 2.2923 | 2.8517 | 0.8289 | 0.24428 | 3.3932 | 0.85694 | 0.37217 | 2.3026 | 7.9477 | 2.1803 | 3.6452
[18 empty] | 02/19 05:00:00 | 5.4372 | 2.2624 | 2.4033 | 5.4091 | 1.5911 | 3.3996 | 5.4013 | 1.4978 | 3.6062 | 0.30718 | 0.1614 | 1.9032 | 0.27912 | 0.10075 | 2.7703 | 6.5091 | 1.7819 | 3.653 | 6.5013 | 1.6846 | 3.8593 | 6.5261 | 2.2194 | 2.9404 | 3.2091 | 0.94547 | 3.3942 | 6.5092 | 1.6104 | 4.0421 | 6.5372 | 2.2924 | 2.8517 | 0.82913 | 0.24431 | 3.3937 | 0.85719 | 0.3722 | 2.303 | 7.9479 | 2.1804 | 3.6452
[18 empty] | 02/19 06:00:00 | 5.4373 | 2.2624 | 2.4033 | 5.4093 | 1.5911 | 3.3996 | 5.4015 | 1.4978 | 3.6062 | 0.30734 | 0.16148 | 1.9032 | 0.27929 | 0.10081 | 2.7704 | 6.5093 | 1.7819 | 3.653 | 6.5015 | 1.6846 | 3.8594 | 6.5263 | 2.2195 | 2.9404 | 3.2093 | 0.94551 | 3.3943 | 6.5093 | 1.6104 | 4.0422 | 6.5374 | 2.2924 | 2.8518 | 0.8293 | 0.24432 | 3.3943 | 0.85735 | 0.37218 | 2.3036 | 7.9481 | 2.1804 | 3.6453
[18 empty] | 02/19 07:00:00 | 5.4369 | 2.2623 | 2.4033 | 5.409 | 1.5911 | 3.3996 | 5.4014 | 1.4978 | 3.6062 | 0.30691 | 0.16126 | 1.9032 | 0.27904 | 0.10072 | 2.7703 | 6.5091 | 1.7819 | 3.653 | 6.5014 | 1.6846 | 3.8594 | 6.5259 | 2.2194 | 2.9404 | 3.2091 | 0.94541 | 3.3943 | 6.5091 | 1.6103 | 4.0422 | 6.537 | 2.2922 | 2.8518 | 0.82905 | 0.24406 | 3.3968 | 0.85691 | 0.37167 | 2.3056 | 7.9478 | 2.1803 | 3.6452
[18 empty] | 02/19 08:00:00 | 5.4369 | 2.262 | 2.4036 | 5.4091 | 1.5909 | 3.4 | 5.4014 | 1.4976 | 3.6066 | 0.30694 | 0.16125 | 1.9035 | 0.27911 | 0.10073 | 2.7708 | 6.5091 | 1.7818 | 3.6532 | 6.5015 | 1.6845 | 3.8595 | 6.5259 | 2.2193 | 2.9406 | 3.2091 | 0.94539 | 3.3945 | 6.5092 | 1.6102 | 4.0425 | 6.537 | 2.292 | 2.852 | 0.82911 | 0.24414 | 3.3961 | 0.85695 | 0.37181 | 2.3048 | 7.9479 | 2.1802 | 3.6454
[18 empty] | 02/19 09:00:00 | 5.4376 | 2.2621 | 2.4038 | 5.4099 | 1.591 | 3.4003 | 5.4022 | 1.4977 | 3.6069 | 0.30763 | 0.16159 | 1.9037 | 0.2799 | 0.101 | 2.7711 | 6.5099 | 1.7818 | 3.6536 | 6.5022 | 1.6845 | 3.8599 | 6.5266 | 2.2193 | 2.9409 | 3.2099 | 0.94557 | 3.3947 | 6.5099 | 1.6104 | 4.0425 | 6.5377 | 2.2922 | 2.8522 | 0.8299 | 0.24471 | 3.3914 | 0.85763 | 0.37248 | 2.3025 | 7.9486 | 2.1802 | 3.6458
[18 empty] | 02/19 10:00:00 | 5.4384 | 2.2623 | 2.4039 | 5.4107 | 1.5912 | 3.4004 | 5.403 | 1.4979 | 3.607 | 0.30842 | 0.162 | 1.9038 | 0.28068 | 0.10128 | 2.7712 | 6.5107 | 1.7819 | 3.6537 | 6.5029 | 1.6846 | 3.8601 | 6.5274 | 2.2194 | 2.941 | 3.2107 | 0.94576 | 3.3948 | 6.5107 | 1.6105 | 4.0427 | 6.5385 | 2.2924 | 2.8522 | 0.83069 | 0.24504 | 3.39 | 0.85843 | 0.37299 | 2.3015 | 7.9494 | 2.1804 | 3.6459
[18 empty] | 02/19 11:00:00 | 5.4399 | 2.2626 | 2.4043 | 5.4122 | 1.5913 | 3.401 | 5.4044 | 1.4981 | 3.6076 | 0.3099 | 0.16274 | 1.9043 | 0.28216 | 0.1018 | 2.7719 | 6.5122 | 1.7822 | 3.654 | 6.5044 | 1.6849 | 3.8604 | 6.5288 | 2.2197 | 2.9413 | 3.2122 | 0.94616 | 3.3949 | 6.5122 | 1.6108 | 4.0429 | 6.5399 | 2.2928 | 2.8524 | 0.83217 | 0.24582 | 3.3853 | 0.85991 | 0.37408 | 2.2988 | 7.9509 | 2.1806 | 3.6462
[18 empty] | 02/19 12:00:00 | 5.4407 | 2.2629 | 2.4043 | 5.4129 | 1.5916 | 3.4009 | 5.4051 | 1.4983 | 3.6075 | 0.31067 | 0.16315 | 1.9042 | 0.28286 | 0.10205 | 2.7718 | 6.5129 | 1.7823 | 3.6543 | 6.5051 | 1.685 | 3.8607 | 6.5296 | 2.2198 | 2.9415 | 3.2129 | 0.94628 | 3.3953 | 6.5129 | 1.6109 | 4.0431 | 6.5407 | 2.2929 | 2.8525 | 0.83286 | 0.24582 | 3.3881 | 0.86067 | 0.37416 | 2.3003 | 7.9515 | 2.1806 | 3.6464
[18 empty] | 02/19 13:00:00 | 5.4409 | 2.2631 | 2.4041 | 5.4131 | 1.5917 | 3.4007 | 5.4053 | 1.4984 | 3.6073 | 0.31089 | 0.16328 | 1.9041 | 0.28308 | 0.10214 | 2.7715 | 6.5131 | 1.7824 | 3.654 | 6.5053 | 1.6851 | 3.8604 | 6.5299 | 2.2201 | 2.9413 | 3.2131 | 0.9464 | 3.3951 | 6.5131 | 1.611 | 4.0429 | 6.5409 | 2.2931 | 2.8524 | 0.83309 | 0.24568 | 3.3909 | 0.86089 | 0.37399 | 2.3019 | 7.9518 | 2.1808 | 3.6462
[18 empty] | 02/19 14:00:00 | 5.441 | 2.2635 | 2.4039 | 5.4133 | 1.592 | 3.4003 | 5.4055 | 1.4987 | 3.6069 | 0.31105 | 0.16339 | 1.9038 | 0.28327 | 0.10222 | 2.7711 | 6.5133 | 1.7826 | 3.6538 | 6.5056 | 1.6853 | 3.8603 | 6.53 | 2.2203 | 2.9411 | 3.2133 | 0.94653 | 3.3948 | 6.5133 | 1.6112 | 4.0425 | 6.5411 | 2.2935 | 2.852 | 0.83327 | 0.24569 | 3.3916 | 0.86106 | 0.37402 | 2.3022 | 7.952 | 2.181 | 3.646
[18 empty] | 02/19 15:00:00 | 5.4411 | 2.2636 | 2.4037 | 5.4134 | 1.5921 | 3.4001 | 5.4057 | 1.4988 | 3.6067 | 0.31113 | 0.16344 | 1.9036 | 0.28343 | 0.10229 | 2.7709 | 6.5135 | 1.7828 | 3.6535 | 6.5058 | 1.6855 | 3.8599 | 6.5302 | 2.2205 | 2.9408 | 3.2135 | 0.94667 | 3.3945 | 6.5135 | 1.6113 | 4.0423 | 6.5412 | 2.2936 | 2.8519 | 0.83343 | 0.24572 | 3.3918 | 0.86114 | 0.37402 | 2.3024 | 7.9521 | 2.1812 | 3.6457
[18 empty] | 02/19 16:00:00 | 5.4405 | 2.2637 | 2.4034 | 5.4129 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.31048 | 0.16313 | 1.9032 | 0.28292 | 0.10212 | 2.7704 | 6.513 | 1.7828 | 3.6532 | 6.5054 | 1.6855 | 3.8597 | 6.5295 | 2.2205 | 2.9406 | 3.2129 | 0.94656 | 3.3943 | 6.513 | 1.6113 | 4.0422 | 6.5405 | 2.2936 | 2.8517 | 0.83292 | 0.24529 | 3.3957 | 0.86049 | 0.37334 | 2.3048 | 7.9516 | 2.1812 | 3.6455
[18 empty] | 02/19 17:00:00 | 5.439 | 2.2631 | 2.4033 | 5.4116 | 1.5918 | 3.3997 | 5.4042 | 1.4985 | 3.6063 | 0.30904 | 0.16238 | 1.9032 | 0.28159 | 0.10164 | 2.7704 | 6.5116 | 1.7826 | 3.653 | 6.5042 | 1.6853 | 3.8594 | 6.5281 | 2.2202 | 2.9404 | 3.2116 | 0.94617 | 3.3944 | 6.5117 | 1.6108 | 4.0424 | 6.5391 | 2.2929 | 2.8519 | 0.8316 | 0.24444 | 3.402 | 0.85904 | 0.37215 | 2.3083 | 7.9503 | 2.181 | 3.6452
[18 empty] | 02/19 18:00:00 | 5.4384 | 2.2625 | 2.4037 | 5.4107 | 1.5913 | 3.4002 | 5.4033 | 1.4981 | 3.6068 | 0.30838 | 0.16199 | 1.9036 | 0.28075 | 0.10132 | 2.771 | 6.5108 | 1.7822 | 3.6533 | 6.5034 | 1.685 | 3.8597 | 6.5274 | 2.2197 | 2.9407 | 3.2108 | 0.94581 | 3.3948 | 6.5109 | 1.6104 | 4.0429 | 6.5384 | 2.2924 | 2.8523 | 0.83076 | 0.24417 | 3.4023 | 0.85839 | 0.372 | 2.3075 | 7.9496 | 2.1806 | 3.6455
[18 empty] | 02/19 19:00:00 | 5.4372 | 2.262 | 2.4038 | 5.4097 | 1.5909 | 3.4003 | 5.4022 | 1.4977 | 3.607 | 0.30722 | 0.16138 | 1.9037 | 0.27965 | 0.10092 | 2.7711 | 6.5097 | 1.7817 | 3.6536 | 6.5023 | 1.6846 | 3.86 | 6.5263 | 2.2191 | 2.9409 | 3.2097 | 0.94536 | 3.3952 | 6.5098 | 1.61 | 4.0432 | 6.5373 | 2.2917 | 2.8526 | 0.82966 | 0.24367 | 3.4048 | 0.85722 | 0.37115 | 2.3097 | 7.9484 | 2.1801 | 3.6458
[18 empty] | 02/19 20:00:00 | 5.4362 | 2.2616 | 2.4037 | 5.4087 | 1.5907 | 3.4002 | 5.4014 | 1.4975 | 3.6069 | 0.30615 | 0.16083 | 1.9036 | 0.27869 | 0.10057 | 2.771 | 6.5088 | 1.7815 | 3.6535 | 6.5015 | 1.6844 | 3.8599 | 6.5252 | 2.2188 | 2.9409 | 3.2087 | 0.94509 | 3.3952 | 6.5088 | 1.6099 | 4.043 | 6.5362 | 2.2915 | 2.8524 | 0.8287 | 0.24341 | 3.4045 | 0.85616 | 0.37068 | 2.3097 | 7.9474 | 2.1799 | 3.6458
[18 empty] | 02/19 21:00:00 | 5.4357 | 2.2612 | 2.4039 | 5.4082 | 1.5904 | 3.4005 | 5.401 | 1.4973 | 3.6072 | 0.30566 | 0.16055 | 1.9039 | 0.27822 | 0.10039 | 2.7714 | 6.5083 | 1.7813 | 3.6537 | 6.5011 | 1.6842 | 3.86 | 6.5248 | 2.2186 | 2.941 | 3.2083 | 0.94491 | 3.3953 | 6.5083 | 1.6097 | 4.0433 | 6.5357 | 2.2911 | 2.8527 | 0.82823 | 0.24341 | 3.4026 | 0.85567 | 0.37065 | 2.3085 | 7.9469 | 2.1797 | 3.6459
[18 empty] | 02/19 22:00:00 | 5.4354 | 2.2609 | 2.404 | 5.4079 | 1.5902 | 3.4007 | 5.4007 | 1.4971 | 3.6074 | 0.30535 | 0.16037 | 1.904 | 0.27789 | 0.10026 | 2.7716 | 6.5079 | 1.7811 | 3.654 | 6.5008 | 1.684 | 3.8603 | 6.5244 | 2.2183 | 2.9412 | 3.2079 | 0.94474 | 3.3956 | 6.508 | 1.6095 | 4.0435 | 6.5354 | 2.2908 | 2.8529 | 0.8279 | 0.2434 | 3.4015 | 0.85536 | 0.37062 | 2.3079 | 7.9466 | 2.1794 | 3.6462
[18 empty] | 02/19 23:00:00 | 5.4352 | 2.2609 | 2.404 | 5.4077 | 1.5902 | 3.4007 | 5.4004 | 1.497 | 3.6074 | 0.30516 | 0.16027 | 1.904 | 0.27766 | 0.10018 | 2.7716 | 6.5077 | 1.781 | 3.654 | 6.5005 | 1.6839 | 3.8603 | 6.5242 | 2.2182 | 2.9412 | 3.2077 | 0.94466 | 3.3956 | 6.5078 | 1.6095 | 4.0434 | 6.5352 | 2.2908 | 2.8528 | 0.82767 | 0.2434 | 3.4005 | 0.85517 | 0.37064 | 2.3073 | 7.9464 | 2.1794 | 3.6462
[18 empty] | 02/19 24:00:00 | 5.4354 | 2.2612 | 2.4038 | 5.4077 | 1.5904 | 3.4003 | 5.4004 | 1.4972 | 3.607 | 0.30537 | 0.16041 | 1.9037 | 0.27773 | 0.10022 | 2.7711 | 6.5078 | 1.7811 | 3.6538 | 6.5005 | 1.684 | 3.8602 | 6.5244 | 2.2184 | 2.9411 | 3.2078 | 0.94477 | 3.3953 | 6.5078 | 1.6097 | 4.0429 | 6.5354 | 2.2912 | 2.8524 | 0.82774 | 0.24361 | 3.3979 | 0.85538 | 0.37104 | 2.3053 | 7.9465 | 2.1795 | 3.646
[18 empty] | 02/20 01:00:00 | 5.4359 | 2.2615 | 2.4036 | 5.408 | 1.5906 | 3.4001 | 5.4005 | 1.4973 | 3.6067 | 0.30588 | 0.16069 | 1.9036 | 0.27804 | 0.10034 | 2.7709 | 6.5081 | 1.7813 | 3.6535 | 6.5006 | 1.6841 | 3.8599 | 6.5249 | 2.2187 | 2.9408 | 3.2081 | 0.94497 | 3.3949 | 6.5081 | 1.6099 | 4.0427 | 6.5359 | 2.2916 | 2.8522 | 0.82805 | 0.24386 | 3.3955 | 0.85589 | 0.37152 | 2.3037 | 7.9468 | 2.1797 | 3.6457
[18 empty] | 02/20 02:00:00 | 5.4362 | 2.2616 | 2.4037 | 5.4083 | 1.5906 | 3.4001 | 5.4006 | 1.4974 | 3.6068 | 0.30623 | 0.16087 | 1.9036 | 0.27831 | 0.10044 | 2.7709 | 6.5083 | 1.7814 | 3.6535 | 6.5007 | 1.6842 | 3.8598 | 6.5252 | 2.2188 | 2.9408 | 3.2083 | 0.94506 | 3.3949 | 6.5084 | 1.6099 | 4.0427 | 6.5363 | 2.2917 | 2.8522 | 0.82832 | 0.24398 | 3.3951 | 0.85624 | 0.37167 | 2.3038 | 7.9471 | 2.1798 | 3.6457
[18 empty] | 02/20 03:00:00 | 5.4365 | 2.262 | 2.4034 | 5.4085 | 1.5909 | 3.3998 | 5.4008 | 1.4976 | 3.6064 | 0.30646 | 0.16101 | 1.9033 | 0.27852 | 0.10053 | 2.7705 | 6.5085 | 1.7816 | 3.6533 | 6.5008 | 1.6843 | 3.8597 | 6.5254 | 2.219 | 2.9407 | 3.2085 | 0.94518 | 3.3946 | 6.5086 | 1.6101 | 4.0423 | 6.5365 | 2.292 | 2.8519 | 0.82852 | 0.24406 | 3.3947 | 0.85647 | 0.37177 | 2.3038 | 7.9473 | 2.18 | 3.6456
[18 empty] | 02/20 04:00:00 | 5.4365 | 2.2621 | 2.4033 | 5.4086 | 1.591 | 3.3995 | 5.4009 | 1.4977 | 3.6061 | 0.3065 | 0.16105 | 1.9031 | 0.27859 | 0.10056 | 2.7703 | 6.5086 | 1.7817 | 3.653 | 6.5009 | 1.6844 | 3.8594 | 6.5255 | 2.2192 | 2.9404 | 3.2086 | 0.94529 | 3.3943 | 6.5087 | 1.6102 | 4.0421 | 6.5366 | 2.2921 | 2.8517 | 0.8286 | 0.24405 | 3.3952 | 0.85651 | 0.37172 | 2.3042 | 7.9474 | 2.1802 | 3.6453
[18 empty] | 02/20 05:00:00 | 5.4365 | 2.2621 | 2.4033 | 5.4086 | 1.591 | 3.3995 | 5.4009 | 1.4977 | 3.6061 | 0.30647 | 0.16104 | 1.9031 | 0.2786 | 0.10057 | 2.7703 | 6.5086 | 1.7818 | 3.6529 | 6.501 | 1.6845 | 3.8593 | 6.5255 | 2.2193 | 2.9404 | 3.2086 | 0.94531 | 3.3943 | 6.5087 | 1.6102 | 4.0421 | 6.5365 | 2.2921 | 2.8517 | 0.82861 | 0.24401 | 3.3958 | 0.85648 | 0.37165 | 2.3046 | 7.9474 | 2.1802 | 3.6452
[18 empty] | 02/20 06:00:00 | 5.4365 | 2.2619 | 2.4035 | 5.4086 | 1.5908 | 3.3999 | 5.401 | 1.4975 | 3.6066 | 0.3065 | 0.16102 | 1.9034 | 0.27863 | 0.10056 | 2.7707 | 6.5087 | 1.7817 | 3.6531 | 6.501 | 1.6844 | 3.8594 | 6.5255 | 2.2192 | 2.9405 | 3.2087 | 0.94525 | 3.3945 | 6.5087 | 1.61 | 4.0426 | 6.5366 | 2.2919 | 2.8521 | 0.82864 | 0.24398 | 3.3963 | 0.85651 | 0.37161 | 2.3049 | 7.9474 | 2.1801 | 3.6454
[18 empty] | 02/20 07:00:00 | 5.4365 | 2.2617 | 2.4037 | 5.4087 | 1.5907 | 3.4002 | 5.401 | 1.4974 | 3.6068 | 0.30651 | 0.16101 | 1.9036 | 0.27865 | 0.10056 | 2.771 | 6.5087 | 1.7815 | 3.6535 | 6.501 | 1.6843 | 3.8598 | 6.5255 | 2.2189 | 2.9408 | 3.2087 | 0.94516 | 3.3949 | 6.5087 | 1.61 | 4.0428 | 6.5366 | 2.2917 | 2.8523 | 0.82866 | 0.24396 | 3.3967 | 0.85652 | 0.37157 | 2.3051 | 7.9474 | 2.18 | 3.6457
[18 empty] | 02/20 08:00:00 | 5.4369 | 2.2616 | 2.404 | 5.409 | 1.5906 | 3.4006 | 5.4013 | 1.4973 | 3.6073 | 0.30687 | 0.16117 | 1.904 | 0.27897 | 0.10066 | 2.7715 | 6.509 | 1.7815 | 3.6537 | 6.5013 | 1.6843 | 3.86 | 6.5258 | 2.2189 | 2.941 | 3.209 | 0.94518 | 3.3951 | 6.509 | 1.6099 | 4.0431 | 6.5369 | 2.2916 | 2.8525 | 0.82898 | 0.24416 | 3.3952 | 0.85687 | 0.37189 | 2.3041 | 7.9478 | 2.1799 | 3.6459
[18 empty] | 02/20 09:00:00 | 5.4378 | 2.2615 | 2.4045 | 5.4102 | 1.5906 | 3.4014 | 5.4024 | 1.4973 | 3.6081 | 0.30781 | 0.16162 | 1.9045 | 0.28018 | 0.10107 | 2.7723 | 6.5102 | 1.7815 | 3.6543 | 6.5024 | 1.6843 | 3.8607 | 6.5269 | 2.2189 | 2.9416 | 3.2102 | 0.94542 | 3.3955 | 6.5102 | 1.6101 | 4.0434 | 6.5379 | 2.2915 | 2.853 | 0.83019 | 0.24492 | 3.3896 | 0.85782 | 0.3726 | 2.3023 | 7.9489 | 2.1799 | 3.6465
[18 empty] | 02/20 10:00:00 | 5.4393 | 2.2618 | 2.4049 | 5.4117 | 1.5908 | 3.4018 | 5.4038 | 1.4975 | 3.6085 | 0.3093 | 0.16237 | 1.9049 | 0.28167 | 0.10159 | 2.7728 | 6.5117 | 1.7816 | 3.6549 | 6.5038 | 1.6844 | 3.8612 | 6.5284 | 2.219 | 2.942 | 3.2117 | 0.94575 | 3.3959 | 6.5117 | 1.6103 | 4.0437 | 6.5394 | 2.292 | 2.8532 | 0.83168 | 0.24562 | 3.3861 | 0.8593 | 0.37364 | 2.2998 | 7.9503 | 2.18 | 3.647
[18 empty] | 02/20 11:00:00 | 5.4403 | 2.2621 | 2.405 | 5.4126 | 1.5911 | 3.4019 | 5.4048 | 1.4978 | 3.6086 | 0.31029 | 0.16289 | 1.905 | 0.28263 | 0.10193 | 2.7729 | 6.5126 | 1.7818 | 3.6551 | 6.5049 | 1.6846 | 3.8614 | 6.5294 | 2.2192 | 2.9422 | 3.2126 | 0.94596 | 3.3962 | 6.5127 | 1.6104 | 4.044 | 6.5404 | 2.2922 | 2.8534 | 0.83264 | 0.24578 | 3.3877 | 0.8603 | 0.37396 | 2.3005 | 7.9513 | 2.1801 | 3.6472
[18 empty] | 02/20 12:00:00 | 5.4409 | 2.2626 | 2.4047 | 5.4131 | 1.5914 | 3.4016 | 5.4053 | 1.498 | 3.6082 | 0.31088 | 0.16322 | 1.9047 | 0.28311 | 0.10211 | 2.7725 | 6.5131 | 1.782 | 3.6549 | 6.5053 | 1.6847 | 3.8614 | 6.5299 | 2.2195 | 2.942 | 3.2131 | 0.94614 | 3.396 | 6.5131 | 1.6107 | 4.0437 | 6.541 | 2.2926 | 2.8531 | 0.83312 | 0.24575 | 3.39 | 0.86089 | 0.37406 | 2.3015 | 7.9518 | 2.1803 | 3.6471
[18 empty] | 02/20 13:00:00 | 5.4412 | 2.2631 | 2.4043 | 5.4134 | 1.5917 | 3.401 | 5.4056 | 1.4984 | 3.6076 | 0.31116 | 0.1634 | 1.9043 | 0.28339 | 0.10224 | 2.7718 | 6.5134 | 1.7823 | 3.6544 | 6.5057 | 1.685 | 3.8609 | 6.5302 | 2.2199 | 2.9416 | 3.2134 | 0.94637 | 3.3955 | 6.5134 | 1.611 | 4.0431 | 6.5412 | 2.2931 | 2.8526 | 0.8334 | 0.24576 | 3.3911 | 0.86117 | 0.37409 | 2.3021 | 7.9521 | 2.1807 | 3.6466
[18 empty] | 02/20 14:00:00 | 5.4413 | 2.2635 | 2.4039 | 5.4135 | 1.592 | 3.4004 | 5.4058 | 1.4987 | 3.607 | 0.31127 | 0.1635 | 1.9038 | 0.28354 | 0.10232 | 2.7711 | 6.5136 | 1.7826 | 3.6539 | 6.5058 | 1.6853 | 3.8604 | 6.5303 | 2.2203 | 2.9412 | 3.2136 | 0.94659 | 3.3949 | 6.5136 | 1.6113 | 4.0425 | 6.5413 | 2.2935 | 2.8521 | 0.83355 | 0.24576 | 3.3917 | 0.86127 | 0.37409 | 2.3023 | 7.9522 | 2.181 | 3.6461
[18 empty] | 02/20 15:00:00 | 5.4411 | 2.2636 | 2.4037 | 5.4135 | 1.5921 | 3.4001 | 5.4058 | 1.4988 | 3.6067 | 0.31109 | 0.16342 | 1.9036 | 0.28346 | 0.1023 | 2.7709 | 6.5135 | 1.7828 | 3.6535 | 6.5058 | 1.6855 | 3.86 | 6.5302 | 2.2205 | 2.9408 | 3.2135 | 0.94666 | 3.3945 | 6.5135 | 1.6113 | 4.0424 | 6.5411 | 2.2936 | 2.8519 | 0.83347 | 0.24563 | 3.3932 | 0.8611 | 0.37386 | 2.3033 | 7.9521 | 2.1812 | 3.6457
[18 empty] | 02/20 16:00:00 | 5.4406 | 2.2635 | 2.4037 | 5.4131 | 1.5921 | 3.4001 | 5.4055 | 1.4988 | 3.6067 | 0.31065 | 0.16319 | 1.9036 | 0.28311 | 0.10217 | 2.7708 | 6.5131 | 1.7827 | 3.6534 | 6.5056 | 1.6854 | 3.8599 | 6.5297 | 2.2204 | 2.9408 | 3.2131 | 0.94656 | 3.3945 | 6.5132 | 1.6112 | 4.0425 | 6.5407 | 2.2934 | 2.852 | 0.83312 | 0.24536 | 3.3954 | 0.86065 | 0.37346 | 2.3046 | 7.9518 | 2.1812 | 3.6456
[18 empty] | 02/20 17:00:00 | 5.4395 | 2.2631 | 2.4036 | 5.4121 | 1.5918 | 3.4 | 5.4046 | 1.4985 | 3.6066 | 0.30954 | 0.16262 | 1.9034 | 0.28206 | 0.1018 | 2.7707 | 6.5121 | 1.7825 | 3.6533 | 6.5047 | 1.6853 | 3.8598 | 6.5287 | 2.2201 | 2.9407 | 3.2121 | 0.94622 | 3.3947 | 6.5122 | 1.6109 | 4.0426 | 6.5396 | 2.2929 | 2.8521 | 0.83207 | 0.24469 | 3.4005 | 0.85955 | 0.37254 | 2.3073 | 7.9508 | 2.1809 | 3.6456
[18 empty] | 02/20 18:00:00 | 5.4388 | 2.2629 | 2.4035 | 5.4113 | 1.5916 | 3.3999 | 5.4038 | 1.4984 | 3.6065 | 0.30882 | 0.16225 | 1.9034 | 0.28128 | 0.10152 | 2.7706 | 6.5113 | 1.7823 | 3.6532 | 6.5039 | 1.6851 | 3.8597 | 6.5279 | 2.2199 | 2.9406 | 3.2113 | 0.94602 | 3.3946 | 6.5114 | 1.6107 | 4.0425 | 6.5389 | 2.2928 | 2.8519 | 0.83129 | 0.24444 | 3.4008 | 0.85883 | 0.37229 | 2.3069 | 7.95 | 2.1808 | 3.6455
[18 empty] | 02/20 19:00:00 | 5.4383 | 2.2627 | 2.4034 | 5.4105 | 1.5914 | 3.3998 | 5.4031 | 1.4982 | 3.6064 | 0.30829 | 0.16198 | 1.9033 | 0.28054 | 0.10126 | 2.7705 | 6.5106 | 1.7822 | 3.6532 | 6.5032 | 1.6849 | 3.8596 | 6.5273 | 2.2198 | 2.9406 | 3.2106 | 0.94581 | 3.3945 | 6.5106 | 1.6106 | 4.0424 | 6.5384 | 2.2927 | 2.8519 | 0.83055 | 0.24422 | 3.4009 | 0.8583 | 0.37215 | 2.3063 | 7.9493 | 2.1806 | 3.6454
[18 empty] | 02/20 20:00:00 | 5.4381 | 2.2624 | 2.4037 | 5.4103 | 1.5912 | 3.4001 | 5.4028 | 1.498 | 3.6068 | 0.30811 | 0.16185 | 1.9036 | 0.28027 | 0.10115 | 2.7709 | 6.5103 | 1.782 | 3.6533 | 6.5029 | 1.6848 | 3.8597 | 6.5271 | 2.2196 | 2.9407 | 3.2103 | 0.94569 | 3.3947 | 6.5104 | 1.6104 | 4.0427 | 6.5382 | 2.2923 | 2.8522 | 0.83028 | 0.24428 | 3.3989 | 0.85811 | 0.37219 | 2.3056 | 7.949 | 2.1805 | 3.6455
[18 empty] | 02/20 21:00:00 | 5.4378 | 2.2621 | 2.4038 | 5.41 | 1.591 | 3.4003 | 5.4026 | 1.4978 | 3.607 | 0.3078 | 0.16168 | 1.9038 | 0.27998 | 0.10104 | 2.7711 | 6.51 | 1.7818 | 3.6536 | 6.5026 | 1.6846 | 3.86 | 6.5268 | 2.2193 | 2.9409 | 3.21 | 0.94551 | 3.395 | 6.5101 | 1.6102 | 4.0429 | 6.5379 | 2.292 | 2.8524 | 0.82999 | 0.24421 | 3.3987 | 0.85781 | 0.37199 | 2.306 | 7.9488 | 2.1802 | 3.6458
[18 empty] | 02/20 22:00:00 | 5.4375 | 2.2621 | 2.4038 | 5.4097 | 1.591 | 3.4003 | 5.4023 | 1.4977 | 3.607 | 0.30752 | 0.16154 | 1.9037 | 0.27972 | 0.10094 | 2.7711 | 6.5098 | 1.7817 | 3.6536 | 6.5024 | 1.6845 | 3.86 | 6.5265 | 2.2192 | 2.941 | 3.2098 | 0.94543 | 3.395 | 6.5098 | 1.6102 | 4.0429 | 6.5376 | 2.292 | 2.8524 | 0.82973 | 0.24415 | 3.3984 | 0.85753 | 0.37188 | 2.306 | 7.9485 | 2.1801 | 3.6458
[18 empty] | 02/20 23:00:00 | 5.4376 | 2.2621 | 2.4038 | 5.4097 | 1.5909 | 3.4003 | 5.4022 | 1.4977 | 3.607 | 0.30755 | 0.16155 | 1.9037 | 0.27968 | 0.10093 | 2.7711 | 6.5097 | 1.7817 | 3.6536 | 6.5023 | 1.6845 | 3.86 | 6.5265 | 2.2192 | 2.941 | 3.2097 | 0.94543 | 3.395 | 6.5098 | 1.6102 | 4.0428 | 6.5376 | 2.292 | 2.8523 | 0.82969 | 0.24423 | 3.3971 | 0.85756 | 0.37205 | 2.305 | 7.9484 | 2.1801 | 3.6458
[18 empty] | 02/20 24:00:00 | 5.4376 | 2.2621 | 2.4038 | 5.4097 | 1.5909 | 3.4003 | 5.4022 | 1.4977 | 3.6069 | 0.30759 | 0.16157 | 1.9037 | 0.27967 | 0.10092 | 2.7711 | 6.5097 | 1.7817 | 3.6536 | 6.5022 | 1.6845 | 3.86 | 6.5265 | 2.2192 | 2.941 | 3.2097 | 0.94543 | 3.395 | 6.5097 | 1.6102 | 4.0428 | 6.5376 | 2.292 | 2.8523 | 0.82968 | 0.24427 | 3.3966 | 0.8576 | 0.37211 | 2.3047 | 7.9484 | 2.1801 | 3.6458
[18 empty] | 02/21 01:00:00 | 5.4375 | 2.2623 | 2.4035 | 5.4096 | 1.5911 | 3.3999 | 5.4021 | 1.4979 | 3.6065 | 0.30748 | 0.16154 | 1.9034 | 0.27958 | 0.10091 | 2.7707 | 6.5096 | 1.7818 | 3.6534 | 6.5021 | 1.6845 | 3.8599 | 6.5264 | 2.2193 | 2.9408 | 3.2096 | 0.94547 | 3.3947 | 6.5097 | 1.6103 | 4.0424 | 6.5375 | 2.2923 | 2.852 | 0.82959 | 0.24425 | 3.3965 | 0.85749 | 0.37204 | 2.3049 | 7.9484 | 2.1802 | 3.6457
[18 empty] | 02/21 02:00:00 | 5.4371 | 2.2623 | 2.4033 | 5.4093 | 1.5912 | 3.3996 | 5.4018 | 1.4979 | 3.6062 | 0.30711 | 0.16136 | 1.9032 | 0.27931 | 0.10082 | 2.7704 | 6.5094 | 1.7819 | 3.6531 | 6.5019 | 1.6846 | 3.8595 | 6.5261 | 2.2194 | 2.9405 | 3.2093 | 0.94547 | 3.3944 | 6.5094 | 1.6103 | 4.0423 | 6.5372 | 2.2923 | 2.8518 | 0.82932 | 0.2441 | 3.3974 | 0.85712 | 0.37175 | 2.3056 | 7.9481 | 2.1803 | 3.6453
[18 empty] | 02/21 03:00:00 | 5.4367 | 2.2622 | 2.4033 | 5.409 | 1.5911 | 3.3996 | 5.4016 | 1.4979 | 3.6062 | 0.30672 | 0.16116 | 1.9032 | 0.27899 | 0.10071 | 2.7703 | 6.509 | 1.7818 | 3.653 | 6.5016 | 1.6846 | 3.8594 | 6.5258 | 2.2193 | 2.9404 | 3.209 | 0.94539 | 3.3944 | 6.5091 | 1.6103 | 4.0423 | 6.5368 | 2.2921 | 2.8518 | 0.829 | 0.24395 | 3.3982 | 0.85673 | 0.37151 | 2.3061 | 7.9478 | 2.1803 | 3.6452
[18 empty] | 02/21 04:00:00 | 5.4363 | 2.2623 | 2.403 | 5.4087 | 1.5912 | 3.3991 | 5.4013 | 1.498 | 3.6058 | 0.30634 | 0.16099 | 1.9028 | 0.27867 | 0.10061 | 2.7698 | 6.5087 | 1.7819 | 3.6527 | 6.5014 | 1.6846 | 3.8592 | 6.5254 | 2.2194 | 2.9402 | 3.2087 | 0.94538 | 3.3941 | 6.5088 | 1.6104 | 4.0418 | 6.5364 | 2.2923 | 2.8514 | 0.82868 | 0.24387 | 3.3981 | 0.85635 | 0.37138 | 2.3058 | 7.9474 | 2.1803 | 3.645
[18 empty] | 02/21 05:00:00 | 5.4119 | 2.2543 | 2.4007 | 5.3997 | 1.589 | 3.3982 | 5.3908 | 1.4955 | 3.6047 | 0.28185 | 0.1483 | 1.9006 | 0.26974 | 0.097418 | 2.7689 | 6.4999 | 1.7798 | 3.652 | 6.4905 | 1.682 | 3.8588 | 6.5068 | 2.214 | 2.939 | 3.1998 | 0.94219 | 3.3962 | 6.5 | 1.6067 | 4.0455 | 6.5122 | 2.2787 | 2.8578 | 0.81975 | 0.23706 | 3.4581 | 0.83185 | 0.34539 | 2.4084 | 7.9335 | 2.1769 | 3.6444
[18 empty] | 02/21 06:00:00 | 5.42 | 2.2568 | 2.4017 | 5.4024 | 1.5895 | 3.3988 | 5.3939 | 1.4961 | 3.6053 | 0.28998 | 0.15249 | 1.9016 | 0.27237 | 0.098347 | 2.7695 | 6.5024 | 1.7805 | 3.6519 | 6.494 | 1.6831 | 3.8583 | 6.5128 | 2.2162 | 2.9387 | 3.2024 | 0.94395 | 3.3926 | 6.5025 | 1.6104 | 4.0377 | 6.52 | 2.2927 | 2.8438 | 0.82239 | 0.24265 | 3.3893 | 0.84 | 0.36774 | 2.2842 | 7.9376 | 2.1784 | 3.6438
[18 empty] | 02/21 07:00:00 | 5.4363 | 2.2621 | 2.4032 | 5.4091 | 1.5911 | 3.3996 | 5.4002 | 1.4975 | 3.606 | 0.30634 | 0.16096 | 1.9031 | 0.27906 | 0.10073 | 2.7703 | 6.5091 | 1.7819 | 3.6529 | 6.5003 | 1.6846 | 3.8588 | 6.5256 | 2.2194 | 2.9402 | 3.2091 | 0.94571 | 3.3933 | 6.5091 | 1.6102 | 4.0424 | 6.5362 | 2.2919 | 2.8519 | 0.82908 | 0.2465 | 3.3633 | 0.85634 | 0.37911 | 2.2588 | 7.9471 | 2.1803 | 3.6449
[18 empty] | 02/21 08:00:00 | 5.4366 | 2.2619 | 2.4035 | 5.409 | 1.5909 | 3.4 | 5.4006 | 1.4975 | 3.6065 | 0.30661 | 0.16108 | 1.9035 | 0.27903 | 0.10071 | 2.7708 | 6.509 | 1.7818 | 3.6532 | 6.5007 | 1.6844 | 3.8593 | 6.5257 | 2.2192 | 2.9405 | 3.209 | 0.94538 | 3.3944 | 6.509 | 1.6102 | 4.0425 | 6.5366 | 2.292 | 2.852 | 0.82904 | 0.24479 | 3.3867 | 0.85662 | 0.37371 | 2.2922 | 7.9474 | 2.1802 | 3.6453
[18 empty] | 02/21 09:00:00 | 5.4121 | 2.2538 | 2.4013 | 5.3999 | 1.5886 | 3.3991 | 5.3913 | 1.4952 | 3.6057 | 0.28213 | 0.14839 | 1.9013 | 0.26994 | 0.097455 | 2.7699 | 6.5001 | 1.7794 | 3.6529 | 6.491 | 1.6818 | 3.8597 | 6.5071 | 2.2135 | 2.9397 | 3.2001 | 0.94201 | 3.3971 | 6.5002 | 1.6064 | 4.0464 | 6.5124 | 2.2781 | 2.8587 | 0.82003 | 0.2373 | 3.4558 | 0.83213 | 0.34596 | 2.4053 | 7.9337 | 2.1765 | 3.6453
[18 empty] | 02/21 10:00:00 | 5.4217 | 2.2569 | 2.4023 | 5.4044 | 1.5897 | 3.3997 | 5.3956 | 1.4962 | 3.6062 | 0.29172 | 0.15335 | 1.9023 | 0.27441 | 0.099048 | 2.7705 | 6.5045 | 1.7807 | 3.6527 | 6.4956 | 1.6832 | 3.8591 | 6.5146 | 2.2164 | 2.9393 | 3.2044 | 0.94451 | 3.3927 | 6.5044 | 1.6112 | 4.0371 | 6.5217 | 2.2935 | 2.8436 | 0.82445 | 0.24428 | 3.375 | 0.84174 | 0.36972 | 2.2767 | 7.9395 | 2.1785 | 3.6444
[18 empty] | 02/21 11:00:00 | 5.4406 | 2.263 | 2.4041 | 5.4133 | 1.5918 | 3.4007 | 5.4044 | 1.4982 | 3.6072 | 0.31058 | 0.16312 | 1.904 | 0.28333 | 0.10223 | 2.7716 | 6.5133 | 1.7826 | 3.6539 | 6.5046 | 1.6852 | 3.8599 | 6.53 | 2.2203 | 2.9411 | 3.2133 | 0.94683 | 3.3937 | 6.5132 | 1.6109 | 4.0433 | 6.5406 | 2.293 | 2.8525 | 0.83334 | 0.24889 | 3.3482 | 0.86058 | 0.38247 | 2.2501 | 7.9515 | 2.181 | 3.6459
[18 empty] | 02/21 12:00:00 | 5.441 | 2.2632 | 2.4041 | 5.4135 | 1.5918 | 3.4008 | 5.4052 | 1.4984 | 3.6073 | 0.31101 | 0.16334 | 1.9041 | 0.28348 | 0.10228 | 2.7716 | 6.5134 | 1.7825 | 3.654 | 6.5052 | 1.6852 | 3.8603 | 6.5302 | 2.2202 | 2.9413 | 3.2134 | 0.94655 | 3.3949 | 6.5134 | 1.6111 | 4.0428 | 6.5411 | 2.2932 | 2.8523 | 0.83348 | 0.24664 | 3.3793 | 0.86101 | 0.37625 | 2.2884 | 7.9519 | 2.1809 | 3.6461
[18 empty] | 02/21 13:00:00 | 5.4414 | 2.2636 | 2.4039 | 5.4137 | 1.5921 | 3.4004 | 5.4056 | 1.4987 | 3.6069 | 0.31135 | 0.16354 | 1.9038 | 0.28368 | 0.10237 | 2.7712 | 6.5137 | 1.7827 | 3.6538 | 6.5056 | 1.6853 | 3.8602 | 6.5304 | 2.2204 | 2.9411 | 3.2137 | 0.94665 | 3.3948 | 6.5137 | 1.6113 | 4.0425 | 6.5414 | 2.2936 | 2.852 | 0.83368 | 0.2461 | 3.3875 | 0.86135 | 0.37487 | 2.2978 | 7.9522 | 2.1811 | 3.646
[18 empty] | 02/21 14:00:00 | 5.4415 | 2.264 | 2.4035 | 5.4138 | 1.5924 | 3.3998 | 5.4059 | 1.499 | 3.6063 | 0.31147 | 0.16365 | 1.9033 | 0.28376 | 0.10242 | 2.7705 | 6.5138 | 1.783 | 3.6533 | 6.5059 | 1.6856 | 3.8598 | 6.5305 | 2.2207 | 2.9407 | 3.2138 | 0.94683 | 3.3942 | 6.5138 | 1.6116 | 4.0419 | 6.5415 | 2.2941 | 2.8515 | 0.83376 | 0.24593 | 3.3903 | 0.86148 | 0.37446 | 2.3006 | 7.9524 | 2.1814 | 3.6456
[18 empty] | 02/21 15:00:00 | 5.4414 | 2.2642 | 2.4033 | 5.4137 | 1.5925 | 3.3995 | 5.4059 | 1.4991 | 3.6061 | 0.31142 | 0.16364 | 1.9031 | 0.2837 | 0.10241 | 2.7702 | 6.5137 | 1.7831 | 3.653 | 6.506 | 1.6857 | 3.8594 | 6.5305 | 2.221 | 2.9404 | 3.2137 | 0.94692 | 3.3939 | 6.5137 | 1.6116 | 4.0417 | 6.5415 | 2.2942 | 2.8513 | 0.83371 | 0.24579 | 3.3919 | 0.86143 | 0.37424 | 2.3018 | 7.9524 | 2.1816 | 3.6452
[18 empty] | 02/21 16:00:00 | 5.4412 | 2.2641 | 2.4033 | 5.4135 | 1.5924 | 3.3995 | 5.4058 | 1.4991 | 3.606 | 0.31123 | 0.16354 | 1.9031 | 0.28352 | 0.10235 | 2.7702 | 6.5136 | 1.7831 | 3.6529 | 6.5059 | 1.6858 | 3.8593 | 6.5303 | 2.2209 | 2.9403 | 3.2135 | 0.94687 | 3.3939 | 6.5136 | 1.6116 | 4.0418 | 6.5413 | 2.2941 | 2.8514 | 0.83353 | 0.24563 | 3.3934 | 0.86124 | 0.374 | 2.3028 | 7.9522 | 2.1816 | 3.6451
[18 empty] | 02/21 17:00:00 | 5.4405 | 2.2639 | 2.4032 | 5.4128 | 1.5923 | 3.3994 | 5.4053 | 1.499 | 3.606 | 0.31053 | 0.16317 | 1.9031 | 0.2828 | 0.10209 | 2.7701 | 6.5128 | 1.783 | 3.6528 | 6.5053 | 1.6856 | 3.8593 | 6.5295 | 2.2207 | 2.9403 | 3.2128 | 0.94663 | 3.394 | 6.5129 | 1.6113 | 4.042 | 6.5406 | 2.2938 | 2.8515 | 0.83281 | 0.24513 | 3.3974 | 0.86053 | 0.37336 | 2.3049 | 7.9516 | 2.1815 | 3.6451
[18 empty] | 02/21 18:00:00 | 5.4389 | 2.2633 | 2.403 | 5.4112 | 1.5919 | 3.3992 | 5.4037 | 1.4986 | 3.6058 | 0.30888 | 0.16232 | 1.9029 | 0.28121 | 0.10153 | 2.7699 | 6.5113 | 1.7826 | 3.6527 | 6.5038 | 1.6853 | 3.8591 | 6.5279 | 2.2202 | 2.9401 | 3.2113 | 0.94613 | 3.3941 | 6.5113 | 1.6109 | 4.0421 | 6.5389 | 2.293 | 2.8517 | 0.83122 | 0.24419 | 3.404 | 0.85889 | 0.37197 | 2.309 | 7.95 | 2.1811 | 3.645
[18 empty] | 02/21 19:00:00 | 5.4375 | 2.2629 | 2.4029 | 5.4099 | 1.5916 | 3.3991 | 5.4025 | 1.4983 | 3.6057 | 0.30748 | 0.1616 | 1.9028 | 0.27991 | 0.10106 | 2.7697 | 6.51 | 1.7823 | 3.6525 | 6.5026 | 1.6851 | 3.8589 | 6.5265 | 2.2199 | 2.94 | 3.21 | 0.94578 | 3.394 | 6.51 | 1.6107 | 4.0418 | 6.5376 | 2.2928 | 2.8514 | 0.82992 | 0.24377 | 3.4046 | 0.85749 | 0.37134 | 2.3092 | 7.9487 | 2.1808 | 3.6448
[18 empty] | 02/21 20:00:00 | 5.4372 | 2.2625 | 2.4032 | 5.4095 | 1.5913 | 3.3994 | 5.4021 | 1.4981 | 3.606 | 0.30715 | 0.1614 | 1.903 | 0.2795 | 0.1009 | 2.7701 | 6.5096 | 1.7821 | 3.6527 | 6.5022 | 1.6849 | 3.859 | 6.5262 | 2.2197 | 2.9401 | 3.2096 | 0.94564 | 3.394 | 6.5096 | 1.6105 | 4.0421 | 6.5372 | 2.2925 | 2.8516 | 0.82951 | 0.24392 | 3.4007 | 0.85716 | 0.37161 | 2.3066 | 7.9483 | 2.1807 | 3.6449
[18 empty] | 02/21 21:00:00 | 5.4368 | 2.2622 | 2.4033 | 5.4092 | 1.5911 | 3.3996 | 5.4018 | 1.4979 | 3.6062 | 0.30682 | 0.16122 | 1.9032 | 0.27915 | 0.10076 | 2.7703 | 6.5092 | 1.7819 | 3.6529 | 6.5019 | 1.6847 | 3.8593 | 6.5259 | 2.2194 | 2.9404 | 3.2092 | 0.94546 | 3.3943 | 6.5093 | 1.6103 | 4.0422 | 6.5369 | 2.2922 | 2.8518 | 0.82916 | 0.24392 | 3.3994 | 0.85683 | 0.37155 | 2.3061 | 7.9479 | 2.1804 | 3.6452
[18 empty] | 02/21 22:00:00 | 5.4369 | 2.2622 | 2.4033 | 5.4091 | 1.5911 | 3.3996 | 5.4017 | 1.4979 | 3.6062 | 0.30685 | 0.16123 | 1.9032 | 0.27908 | 0.10074 | 2.7703 | 6.5091 | 1.7819 | 3.653 | 6.5017 | 1.6847 | 3.8594 | 6.5259 | 2.2194 | 2.9404 | 3.2091 | 0.94544 | 3.3943 | 6.5092 | 1.6103 | 4.0422 | 6.5369 | 2.2923 | 2.8517 | 0.82909 | 0.24404 | 3.3973 | 0.85686 | 0.37178 | 2.3048 | 7.9479 | 2.1803 | 3.6452
[18 empty] | 02/21 23:00:00 | 5.4371 | 2.2623 | 2.4033 | 5.4092 | 1.5911 | 3.3996 | 5.4017 | 1.4979 | 3.6062 | 0.30706 | 0.16134 | 1.9032 | 0.27917 | 0.10077 | 2.7703 | 6.5092 | 1.7819 | 3.653 | 6.5017 | 1.6847 | 3.8594 | 6.526 | 2.2194 | 2.9404 | 3.2092 | 0.94548 | 3.3943 | 6.5093 | 1.6104 | 4.0421 | 6.5371 | 2.2924 | 2.8517 | 0.82918 | 0.24419 | 3.3957 | 0.85707 | 0.37203 | 2.3038 | 7.948 | 2.1804 | 3.6452
[18 empty] | 02/21 24:00:00 | 5.4372 | 2.2624 | 2.4033 | 5.4093 | 1.5911 | 3.3996 | 5.4017 | 1.4979 | 3.6062 | 0.30725 | 0.16143 | 1.9032 | 0.2793 | 0.10082 | 2.7704 | 6.5093 | 1.7819 | 3.653 | 6.5018 | 1.6847 | 3.8594 | 6.5262 | 2.2195 | 2.9404 | 3.2093 | 0.94551 | 3.3943 | 6.5094 | 1.6104 | 4.0422 | 6.5373 | 2.2924 | 2.8517 | 0.82931 | 0.24427 | 3.3951 | 0.85725 | 0.37212 | 2.3037 | 7.9481 | 2.1804 | 3.6453
[18 empty] | 02/22 01:00:00 | 5.4369 | 2.2625 | 2.403 | 5.4091 | 1.5913 | 3.3992 | 5.4016 | 1.498 | 3.6058 | 0.30693 | 0.1613 | 1.9029 | 0.2791 | 0.10076 | 2.7699 | 6.5091 | 1.782 | 3.6528 | 6.5017 | 1.6847 | 3.8592 | 6.5259 | 2.2195 | 2.9402 | 3.2091 | 0.94551 | 3.3941 | 6.5092 | 1.6105 | 4.0418 | 6.537 | 2.2925 | 2.8515 | 0.82911 | 0.24412 | 3.3963 | 0.85694 | 0.37178 | 2.3049 | 7.9479 | 2.1804 | 3.6451
[18 empty] | 02/22 02:00:00 | 5.4367 | 2.2626 | 2.4028 | 5.4089 | 1.5914 | 3.3989 | 5.4014 | 1.4981 | 3.6055 | 0.30674 | 0.16121 | 1.9027 | 0.27894 | 0.10071 | 2.7696 | 6.509 | 1.7821 | 3.6524 | 6.5015 | 1.6848 | 3.8589 | 6.5257 | 2.2197 | 2.94 | 3.209 | 0.94556 | 3.3937 | 6.509 | 1.6105 | 4.0415 | 6.5368 | 2.2927 | 2.8511 | 0.82895 | 0.24408 | 3.3962 | 0.85675 | 0.37176 | 2.3046 | 7.9477 | 2.1806 | 3.6447
[18 empty] | 02/22 03:00:00 | 5.4371 | 2.263 | 2.4026 | 5.4091 | 1.5916 | 3.3986 | 5.4016 | 1.4983 | 3.6051 | 0.30708 | 0.16141 | 1.9024 | 0.27914 | 0.1008 | 2.7692 | 6.5092 | 1.7823 | 3.6522 | 6.5016 | 1.6849 | 3.8587 | 6.526 | 2.2199 | 2.9398 | 3.2092 | 0.94573 | 3.3933 | 6.5092 | 1.6108 | 4.0411 | 6.5371 | 2.2931 | 2.8508 | 0.82915 | 0.24431 | 3.3938 | 0.85708 | 0.37223 | 2.3026 | 7.9479 | 2.1808 | 3.6445
[18 empty] | 02/22 04:00:00 | 5.4369 | 2.2631 | 2.4024 | 5.4091 | 1.5917 | 3.3983 | 5.4015 | 1.4984 | 3.6049 | 0.30694 | 0.16136 | 1.9022 | 0.27906 | 0.10078 | 2.7689 | 6.5091 | 1.7824 | 3.6519 | 6.5016 | 1.6851 | 3.8583 | 6.5259 | 2.2201 | 2.9395 | 3.2091 | 0.94578 | 3.3931 | 6.5091 | 1.6108 | 4.041 | 6.537 | 2.2931 | 2.8507 | 0.82907 | 0.24422 | 3.3947 | 0.85695 | 0.37201 | 2.3036 | 7.9478 | 2.181 | 3.6442
[18 empty] | 02/22 05:00:00 | 5.4365 | 2.263 | 2.4024 | 5.4088 | 1.5916 | 3.3983 | 5.4013 | 1.4983 | 3.6048 | 0.30653 | 0.16115 | 1.9022 | 0.27877 | 0.10068 | 2.7689 | 6.5088 | 1.7824 | 3.6518 | 6.5014 | 1.6851 | 3.8582 | 6.5255 | 2.22 | 2.9394 | 3.2088 | 0.9457 | 3.393 | 6.5088 | 1.6107 | 4.041 | 6.5366 | 2.293 | 2.8507 | 0.82878 | 0.24403 | 3.3963 | 0.85654 | 0.37165 | 2.3047 | 7.9475 | 2.1809 | 3.6441
[18 empty] | 02/22 06:00:00 | 5.4363 | 2.2629 | 2.4024 | 5.4086 | 1.5916 | 3.3983 | 5.4011 | 1.4983 | 3.6048 | 0.30633 | 0.16104 | 1.9022 | 0.27859 | 0.10062 | 2.7689 | 6.5086 | 1.7823 | 3.6518 | 6.5012 | 1.685 | 3.8582 | 6.5254 | 2.22 | 2.9394 | 3.2086 | 0.94566 | 3.393 | 6.5087 | 1.6107 | 4.0409 | 6.5364 | 2.293 | 2.8506 | 0.8286 | 0.24398 | 3.3962 | 0.85634 | 0.37161 | 2.3044 | 7.9474 | 2.1809 | 3.6441
[18 empty] | 02/22 07:00:00 | 5.4362 | 2.2626 | 2.4026 | 5.4084 | 1.5914 | 3.3986 | 5.401 | 1.4981 | 3.6052 | 0.30616 | 0.16093 | 1.9024 | 0.27845 | 0.10055 | 2.7693 | 6.5085 | 1.7822 | 3.652 | 6.5011 | 1.685 | 3.8583 | 6.5252 | 2.2198 | 2.9395 | 3.2085 | 0.94555 | 3.3932 | 6.5085 | 1.6105 | 4.0413 | 6.5362 | 2.2926 | 2.851 | 0.82846 | 0.24392 | 3.3965 | 0.85617 | 0.3715 | 2.3046 | 7.9472 | 2.1808 | 3.6442
[18 empty] | 02/22 08:00:00 | 5.4364 | 2.2625 | 2.4028 | 5.4087 | 1.5913 | 3.3989 | 5.4011 | 1.498 | 3.6055 | 0.30644 | 0.16106 | 1.9027 | 0.27869 | 0.10063 | 2.7696 | 6.5087 | 1.7821 | 3.6523 | 6.5012 | 1.6848 | 3.8587 | 6.5254 | 2.2197 | 2.9398 | 3.2087 | 0.94555 | 3.3935 | 6.5088 | 1.6105 | 4.0414 | 6.5365 | 2.2927 | 2.851 | 0.8287 | 0.24415 | 3.3942 | 0.85645 | 0.37185 | 2.3032 | 7.9474 | 2.1806 | 3.6446
[18 empty] | 02/22 09:00:00 | 5.4374 | 2.2626 | 2.4032 | 5.4097 | 1.5914 | 3.3994 | 5.4019 | 1.498 | 3.606 | 0.30736 | 0.16151 | 1.903 | 0.2797 | 0.10097 | 2.7701 | 6.5097 | 1.7822 | 3.6526 | 6.5019 | 1.6849 | 3.859 | 6.5264 | 2.2198 | 2.9401 | 3.2097 | 0.9458 | 3.3936 | 6.5097 | 1.6107 | 4.0416 | 6.5374 | 2.2928 | 2.8513 | 0.82971 | 0.24482 | 3.3891 | 0.85737 | 0.37263 | 2.3009 | 7.9484 | 2.1807 | 3.6448
[18 empty] | 02/22 10:00:00 | 5.4391 | 2.263 | 2.4035 | 5.4113 | 1.5916 | 3.3999 | 5.4036 | 1.4983 | 3.6065 | 0.3091 | 0.1624 | 1.9034 | 0.2813 | 0.10153 | 2.7706 | 6.5113 | 1.7824 | 3.6531 | 6.5036 | 1.6851 | 3.8595 | 6.5281 | 2.2201 | 2.9405 | 3.2113 | 0.9462 | 3.3939 | 6.5113 | 1.611 | 4.0418 | 6.5391 | 2.2933 | 2.8514 | 0.8313 | 0.24567 | 3.3839 | 0.85911 | 0.37399 | 2.2971 | 7.95 | 2.1809 | 3.6453
[18 empty] | 02/22 11:00:00 | 5.4405 | 2.2634 | 2.4036 | 5.4125 | 1.5919 | 3.4 | 5.4049 | 1.4986 | 3.6066 | 0.31047 | 0.1631 | 1.9035 | 0.28249 | 0.10195 | 2.7707 | 6.5125 | 1.7826 | 3.6533 | 6.5048 | 1.6853 | 3.8597 | 6.5294 | 2.2204 | 2.9407 | 3.2125 | 0.94649 | 3.3941 | 6.5125 | 1.6112 | 4.0421 | 6.5405 | 2.2936 | 2.8517 | 0.83249 | 0.24598 | 3.3844 | 0.86047 | 0.37452 | 2.2975 | 7.9512 | 2.1811 | 3.6455
[18 empty] | 02/22 12:00:00 | 5.4409 | 2.2638 | 2.4034 | 5.413 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.31093 | 0.16337 | 1.9033 | 0.28302 | 0.10216 | 2.7704 | 6.513 | 1.7828 | 3.6532 | 6.5053 | 1.6855 | 3.8596 | 6.5299 | 2.2206 | 2.9406 | 3.213 | 0.94667 | 3.394 | 6.5131 | 1.6114 | 4.0418 | 6.541 | 2.2939 | 2.8514 | 0.83303 | 0.24593 | 3.3873 | 0.86094 | 0.37437 | 2.2997 | 7.9517 | 2.1813 | 3.6454
[18 empty] | 02/22 13:00:00 | 5.4411 | 2.2643 | 2.403 | 5.4133 | 1.5926 | 3.3991 | 5.4056 | 1.4992 | 3.6056 | 0.31111 | 0.1635 | 1.9028 | 0.28331 | 0.10229 | 2.7697 | 6.5133 | 1.7832 | 3.6527 | 6.5056 | 1.6857 | 3.8592 | 6.5301 | 2.221 | 2.9402 | 3.2133 | 0.94691 | 3.3935 | 6.5134 | 1.6117 | 4.0412 | 6.5412 | 2.2944 | 2.8509 | 0.83332 | 0.24591 | 3.3887 | 0.86111 | 0.3743 | 2.3006 | 7.952 | 2.1816 | 3.645
[18 empty] | 02/22 14:00:00 | 5.4412 | 2.2648 | 2.4026 | 5.4135 | 1.5929 | 3.3985 | 5.4058 | 1.4996 | 3.605 | 0.31122 | 0.1636 | 1.9023 | 0.28352 | 0.10239 | 2.769 | 6.5135 | 1.7835 | 3.6522 | 6.5058 | 1.686 | 3.8587 | 6.5303 | 2.2214 | 2.9397 | 3.2135 | 0.94714 | 3.3929 | 6.5136 | 1.612 | 4.0406 | 6.5413 | 2.2949 | 2.8504 | 0.83353 | 0.24594 | 3.3891 | 0.86123 | 0.37434 | 2.3006 | 7.9522 | 2.182 | 3.6444
[18 empty] | 02/22 15:00:00 | 5.4408 | 2.2648 | 2.4023 | 5.4133 | 1.593 | 3.3982 | 5.4056 | 1.4996 | 3.6047 | 0.31079 | 0.16339 | 1.9021 | 0.28327 | 0.10231 | 2.7687 | 6.5133 | 1.7836 | 3.6518 | 6.5057 | 1.6862 | 3.8582 | 6.5299 | 2.2215 | 2.9394 | 3.2133 | 0.94715 | 3.3926 | 6.5133 | 1.612 | 4.0406 | 6.5409 | 2.2948 | 2.8503 | 0.83327 | 0.24566 | 3.392 | 0.8608 | 0.37387 | 2.3024 | 7.9519 | 2.1822 | 3.644
[18 empty] | 02/22 16:00:00 | 5.4404 | 2.2647 | 2.4023 | 5.4129 | 1.5929 | 3.3982 | 5.4054 | 1.4996 | 3.6047 | 0.31039 | 0.16319 | 1.9021 | 0.28295 | 0.1022 | 2.7687 | 6.513 | 1.7836 | 3.6517 | 6.5054 | 1.6862 | 3.8581 | 6.5295 | 2.2215 | 2.9393 | 3.213 | 0.94707 | 3.3925 | 6.513 | 1.6119 | 4.0405 | 6.5405 | 2.2947 | 2.8502 | 0.83296 | 0.24547 | 3.3933 | 0.8604 | 0.37363 | 2.3028 | 7.9516 | 2.1821 | 3.6439
[18 empty] | 02/22 17:00:00 | 5.4398 | 2.2645 | 2.4022 | 5.4124 | 1.5928 | 3.3981 | 5.4049 | 1.4994 | 3.6046 | 0.30978 | 0.16287 | 1.902 | 0.28238 | 0.10199 | 2.7686 | 6.5124 | 1.7834 | 3.6516 | 6.5049 | 1.6861 | 3.8581 | 6.5289 | 2.2213 | 2.9392 | 3.2124 | 0.94689 | 3.3926 | 6.5125 | 1.6118 | 4.0406 | 6.5398 | 2.2945 | 2.8503 | 0.83239 | 0.24515 | 3.3955 | 0.85979 | 0.37319 | 2.3039 | 7.951 | 2.182 | 3.6439
[18 empty] | 02/22 18:00:00 | 5.4384 | 2.264 | 2.4021 | 5.411 | 1.5924 | 3.3979 | 5.4035 | 1.4991 | 3.6044 | 0.30837 | 0.16214 | 1.9019 | 0.28102 | 0.10151 | 2.7684 | 6.5111 | 1.7831 | 3.6515 | 6.5035 | 1.6858 | 3.8579 | 6.5275 | 2.2209 | 2.9391 | 3.2111 | 0.94645 | 3.3927 | 6.5111 | 1.6113 | 4.0409 | 6.5384 | 2.2938 | 2.8505 | 0.83103 | 0.24431 | 3.4015 | 0.85838 | 0.37203 | 2.3073 | 7.9497 | 2.1817 | 3.6438
[18 empty] | 02/22 19:00:00 | 5.4363 | 2.2633 | 2.4019 | 5.4088 | 1.5919 | 3.3977 | 5.4013 | 1.4986 | 3.6042 | 0.30633 | 0.16109 | 1.9017 | 0.27879 | 0.10071 | 2.7682 | 6.5088 | 1.7826 | 3.6513 | 6.5014 | 1.6853 | 3.8577 | 6.5255 | 2.2203 | 2.9389 | 3.2088 | 0.94575 | 3.3928 | 6.5088 | 1.6108 | 4.0408 | 6.5364 | 2.2932 | 2.8504 | 0.82881 | 0.24315 | 3.4086 | 0.85634 | 0.37065 | 2.3104 | 7.9475 | 2.1812 | 3.6436
[18 empty] | 02/22 20:00:00 | 5.4354 | 2.2628 | 2.4021 | 5.408 | 1.5915 | 3.398 | 5.4006 | 1.4983 | 3.6045 | 0.30545 | 0.1606 | 1.9019 | 0.278 | 0.10042 | 2.7685 | 6.508 | 1.7824 | 3.6513 | 6.5008 | 1.6852 | 3.8577 | 6.5246 | 2.22 | 2.939 | 3.208 | 0.94554 | 3.3927 | 6.5081 | 1.6106 | 4.0408 | 6.5355 | 2.2928 | 2.8505 | 0.82802 | 0.24327 | 3.4036 | 0.85545 | 0.3706 | 2.3083 | 7.9465 | 2.1809 | 3.6436
[18 empty] | 02/22 21:00:00 | 5.4349 | 2.2622 | 2.4025 | 5.4075 | 1.5911 | 3.3985 | 5.4003 | 1.4979 | 3.6051 | 0.30493 | 0.1603 | 1.9023 | 0.27753 | 0.10022 | 2.7692 | 6.5075 | 1.782 | 3.6518 | 6.5005 | 1.6849 | 3.8581 | 6.5241 | 2.2195 | 2.9394 | 3.2075 | 0.94527 | 3.3932 | 6.5076 | 1.6103 | 4.0414 | 6.535 | 2.2922 | 2.851 | 0.82754 | 0.24331 | 3.4012 | 0.85494 | 0.37056 | 2.3071 | 7.9461 | 2.1806 | 3.6441
[18 empty] | 02/22 22:00:00 | 5.4347 | 2.262 | 2.4026 | 5.4072 | 1.591 | 3.3987 | 5.4001 | 1.4978 | 3.6054 | 0.30469 | 0.16016 | 1.9025 | 0.27725 | 0.10011 | 2.7694 | 6.5073 | 1.7818 | 3.6521 | 6.5002 | 1.6847 | 3.8585 | 6.5238 | 2.2192 | 2.9397 | 3.2073 | 0.9451 | 3.3936 | 6.5073 | 1.6101 | 4.0415 | 6.5348 | 2.292 | 2.8511 | 0.82726 | 0.24335 | 3.3995 | 0.8547 | 0.37062 | 2.3061 | 7.9459 | 2.1803 | 3.6444
[18 empty] | 02/22 23:00:00 | 5.4347 | 2.262 | 2.4026 | 5.4071 | 1.5909 | 3.3987 | 5.4 | 1.4978 | 3.6054 | 0.30467 | 0.16014 | 1.9025 | 0.27715 | 0.10008 | 2.7694 | 6.5072 | 1.7817 | 3.6522 | 6.5001 | 1.6846 | 3.8586 | 6.5237 | 2.2192 | 2.9397 | 3.2072 | 0.94507 | 3.3936 | 6.5072 | 1.6101 | 4.0414 | 6.5347 | 2.292 | 2.8511 | 0.82716 | 0.24344 | 3.3978 | 0.85467 | 0.37078 | 2.3051 | 7.9458 | 2.1802 | 3.6445
[18 empty] | 02/22 24:00:00 | 5.4349 | 2.262 | 2.4027 | 5.4073 | 1.591 | 3.3987 | 5.4 | 1.4978 | 3.6054 | 0.30493 | 0.16028 | 1.9025 | 0.27728 | 0.10012 | 2.7694 | 6.5073 | 1.7818 | 3.6522 | 6.5001 | 1.6846 | 3.8585 | 6.524 | 2.2192 | 2.9397 | 3.2073 | 0.94512 | 3.3935 | 6.5074 | 1.6102 | 4.0414 | 6.535 | 2.2921 | 2.851 | 0.82729 | 0.24362 | 3.3959 | 0.85494 | 0.3711 | 2.3038 | 7.946 | 2.1803 | 3.6445
[18 empty] | 02/23 01:00:00 | 5.4353 | 2.2624 | 2.4024 | 5.4075 | 1.5912 | 3.3984 | 5.4 | 1.4979 | 3.6049 | 0.30531 | 0.1605 | 1.9022 | 0.27754 | 0.10023 | 2.769 | 6.5076 | 1.7819 | 3.652 | 6.5001 | 1.6847 | 3.8584 | 6.5243 | 2.2195 | 2.9396 | 3.2076 | 0.94528 | 3.3932 | 6.5076 | 1.6104 | 4.041 | 6.5354 | 2.2926 | 2.8507 | 0.82755 | 0.24383 | 3.394 | 0.85532 | 0.37144 | 2.3027 | 7.9463 | 2.1804 | 3.6444
[18 empty] | 02/23 02:00:00 | 5.4356 | 2.2627 | 2.4023 | 5.4078 | 1.5914 | 3.3982 | 5.4001 | 1.4981 | 3.6047 | 0.30559 | 0.16066 | 1.9021 | 0.27778 | 0.10033 | 2.7688 | 6.5078 | 1.7821 | 3.6517 | 6.5002 | 1.6848 | 3.8581 | 6.5246 | 2.2197 | 2.9393 | 3.2078 | 0.94544 | 3.3929 | 6.5078 | 1.6105 | 4.0408 | 6.5356 | 2.2928 | 2.8505 | 0.82779 | 0.24394 | 3.3934 | 0.85559 | 0.37159 | 2.3025 | 7.9465 | 2.1807 | 3.6441
[18 empty] | 02/23 03:00:00 | 5.4359 | 2.2628 | 2.4023 | 5.408 | 1.5914 | 3.3982 | 5.4002 | 1.4981 | 3.6047 | 0.30586 | 0.1608 | 1.9021 | 0.278 | 0.1004 | 2.7688 | 6.508 | 1.7822 | 3.6517 | 6.5003 | 1.6849 | 3.8581 | 6.5248 | 2.2198 | 2.9393 | 3.208 | 0.94552 | 3.3929 | 6.5081 | 1.6106 | 4.0408 | 6.5359 | 2.2929 | 2.8505 | 0.82801 | 0.24402 | 3.3932 | 0.85586 | 0.37172 | 2.3024 | 7.9467 | 2.1808 | 3.644
[18 empty] | 02/23 04:00:00 | 5.4361 | 2.2631 | 2.4021 | 5.4082 | 1.5917 | 3.3978 | 5.4004 | 1.4983 | 3.6043 | 0.3061 | 0.16095 | 1.9018 | 0.27821 | 0.1005 | 2.7684 | 6.5082 | 1.7823 | 3.6515 | 6.5004 | 1.6849 | 3.8579 | 6.5251 | 2.22 | 2.9392 | 3.2082 | 0.94565 | 3.3926 | 6.5083 | 1.6108 | 4.0404 | 6.5361 | 2.2932 | 2.8502 | 0.82822 | 0.24411 | 3.3928 | 0.8561 | 0.37187 | 2.3022 | 7.947 | 2.1809 | 3.6439
[18 empty] | 02/23 05:00:00 | 5.4361 | 2.2633 | 2.4019 | 5.4083 | 1.5918 | 3.3976 | 5.4005 | 1.4984 | 3.6041 | 0.30613 | 0.16098 | 1.9016 | 0.27828 | 0.10053 | 2.7681 | 6.5083 | 1.7825 | 3.6512 | 6.5005 | 1.6851 | 3.8576 | 6.5251 | 2.2203 | 2.9389 | 3.2083 | 0.94576 | 3.3923 | 6.5083 | 1.6109 | 4.0402 | 6.5362 | 2.2934 | 2.85 | 0.82829 | 0.2441 | 3.3932 | 0.85614 | 0.37182 | 2.3025 | 7.947 | 2.1811 | 3.6436
[18 empty] | 02/23 06:00:00 | 5.4361 | 2.2633 | 2.4019 | 5.4083 | 1.5918 | 3.3976 | 5.4006 | 1.4985 | 3.6041 | 0.30612 | 0.16098 | 1.9016 | 0.27831 | 0.10054 | 2.7681 | 6.5083 | 1.7825 | 3.6512 | 6.5006 | 1.6852 | 3.8575 | 6.5251 | 2.2203 | 2.9389 | 3.2083 | 0.94578 | 3.3923 | 6.5084 | 1.6109 | 4.0402 | 6.5362 | 2.2934 | 2.85 | 0.82832 | 0.24407 | 3.3937 | 0.85613 | 0.37176 | 2.3029 | 7.9471 | 2.1812 | 3.6435
[18 empty] | 02/23 07:00:00 | 5.4359 | 2.2629 | 2.4021 | 5.4082 | 1.5916 | 3.398 | 5.4005 | 1.4983 | 3.6045 | 0.30592 | 0.16085 | 1.9019 | 0.27821 | 0.10049 | 2.7685 | 6.5082 | 1.7824 | 3.6514 | 6.5006 | 1.6851 | 3.8577 | 6.525 | 2.2201 | 2.939 | 3.2082 | 0.94567 | 3.3926 | 6.5083 | 1.6107 | 4.0407 | 6.536 | 2.293 | 2.8504 | 0.82822 | 0.24394 | 3.3951 | 0.85593 | 0.3715 | 2.304 | 7.9469 | 2.181 | 3.6437
[18 empty] | 02/23 08:00:00 | 5.4361 | 2.2628 | 2.4023 | 5.4084 | 1.5915 | 3.3982 | 5.4007 | 1.4982 | 3.6048 | 0.30608 | 0.16092 | 1.9021 | 0.27837 | 0.10054 | 2.7688 | 6.5084 | 1.7823 | 3.6517 | 6.5007 | 1.685 | 3.858 | 6.5251 | 2.22 | 2.9393 | 3.2084 | 0.94564 | 3.3928 | 6.5084 | 1.6107 | 4.0408 | 6.5361 | 2.293 | 2.8505 | 0.82838 | 0.24407 | 3.394 | 0.85609 | 0.37172 | 2.3031 | 7.9471 | 2.1809 | 3.644
[18 empty] | 02/23 09:00:00 | 5.4373 | 2.2632 | 2.4025 | 5.4095 | 1.5918 | 3.3984 | 5.4018 | 1.4985 | 3.6049 | 0.30733 | 0.16156 | 1.9023 | 0.27947 | 0.10093 | 2.769 | 6.5095 | 1.7825 | 3.6518 | 6.5018 | 1.6852 | 3.8582 | 6.5263 | 2.2203 | 2.9394 | 3.2095 | 0.946 | 3.3927 | 6.5095 | 1.6111 | 4.0405 | 6.5374 | 2.2936 | 2.8502 | 0.82948 | 0.24487 | 3.3874 | 0.85734 | 0.37296 | 2.2988 | 7.9482 | 2.1811 | 3.6441
[18 empty] | 02/23 10:00:00 | 5.439 | 2.2638 | 2.4026 | 5.4111 | 1.5922 | 3.3986 | 5.4034 | 1.4988 | 3.6051 | 0.30895 | 0.1624 | 1.9024 | 0.28114 | 0.10152 | 2.7692 | 6.5111 | 1.7829 | 3.652 | 6.5033 | 1.6855 | 3.8584 | 6.5279 | 2.2207 | 2.9396 | 3.2111 | 0.9465 | 3.3926 | 6.5112 | 1.6115 | 4.0405 | 6.539 | 2.2941 | 2.8504 | 0.83114 | 0.24575 | 3.382 | 0.85896 | 0.37403 | 2.2965 | 7.9498 | 2.1815 | 3.6443
[18 empty] | 02/23 11:00:00 | 5.4398 | 2.2638 | 2.403 | 5.4122 | 1.5922 | 3.3991 | 5.4044 | 1.4989 | 3.6056 | 0.3098 | 0.16281 | 1.9028 | 0.28215 | 0.10187 | 2.7697 | 6.5122 | 1.783 | 3.6523 | 6.5045 | 1.6857 | 3.8587 | 6.5288 | 2.2208 | 2.9398 | 3.2122 | 0.94668 | 3.3931 | 6.5122 | 1.6114 | 4.0413 | 6.5398 | 2.294 | 2.8509 | 0.83216 | 0.24588 | 3.3844 | 0.85981 | 0.37409 | 2.2984 | 7.9508 | 2.1816 | 3.6445
[18 empty] | 02/23 12:00:00 | 5.4404 | 2.2638 | 2.4032 | 5.4127 | 1.5922 | 3.3994 | 5.4049 | 1.4989 | 3.6059 | 0.31037 | 0.16309 | 1.903 | 0.28267 | 0.10205 | 2.7701 | 6.5127 | 1.783 | 3.6527 | 6.505 | 1.6856 | 3.8591 | 6.5294 | 2.2208 | 2.9402 | 3.2127 | 0.9467 | 3.3936 | 6.5127 | 1.6114 | 4.0415 | 6.5404 | 2.2939 | 2.8512 | 0.83268 | 0.24581 | 3.3875 | 0.86038 | 0.37413 | 2.2997 | 7.9513 | 2.1815 | 3.6449
[18 empty] | 02/23 13:00:00 | 5.4408 | 2.2642 | 2.403 | 5.4131 | 1.5925 | 3.3991 | 5.4053 | 1.4992 | 3.6056 | 0.31084 | 0.16336 | 1.9028 | 0.2831 | 0.10221 | 2.7697 | 6.5131 | 1.7831 | 3.6526 | 6.5054 | 1.6857 | 3.8591 | 6.5298 | 2.221 | 2.9401 | 3.2131 | 0.94687 | 3.3934 | 6.5131 | 1.6117 | 4.0412 | 6.5409 | 2.2944 | 2.8508 | 0.83311 | 0.24588 | 3.3882 | 0.86085 | 0.37431 | 2.2998 | 7.9518 | 2.1816 | 3.6449
[18 empty] | 02/23 14:00:00 | 5.4411 | 2.2645 | 2.4028 | 5.4133 | 1.5927 | 3.3988 | 5.4056 | 1.4993 | 3.6054 | 0.31112 | 0.16352 | 1.9026 | 0.28334 | 0.10231 | 2.7694 | 6.5134 | 1.7833 | 3.6523 | 6.5056 | 1.6859 | 3.8588 | 6.5301 | 2.2212 | 2.9398 | 3.2134 | 0.94702 | 3.3931 | 6.5134 | 1.6118 | 4.0411 | 6.5412 | 2.2946 | 2.8507 | 0.83335 | 0.24587 | 3.3894 | 0.86113 | 0.37436 | 2.3003 | 7.952 | 2.1819 | 3.6446
[18 empty] | 02/23 15:00:00 | 5.4409 | 2.2647 | 2.4025 | 5.4131 | 1.5928 | 3.3984 | 5.4054 | 1.4995 | 3.6049 | 0.31087 | 0.16342 | 1.9023 | 0.28308 | 0.10223 | 2.769 | 6.5131 | 1.7834 | 3.6521 | 6.5055 | 1.686 | 3.8586 | 6.5299 | 2.2213 | 2.9396 | 3.2131 | 0.947 | 3.3929 | 6.5131 | 1.6119 | 4.0407 | 6.5409 | 2.2947 | 2.8504 | 0.83309 | 0.24559 | 3.3922 | 0.86088 | 0.374 | 2.3018 | 7.9518 | 2.182 | 3.6444
[18 empty] | 02/23 16:00:00 | 5.4409 | 2.2648 | 2.4024 | 5.413 | 1.5929 | 3.3982 | 5.4054 | 1.4996 | 3.6047 | 0.31094 | 0.16347 | 1.9021 | 0.28303 | 0.10223 | 2.7687 | 6.5131 | 1.7836 | 3.6517 | 6.5055 | 1.6861 | 3.8582 | 6.5299 | 2.2216 | 2.9393 | 3.2131 | 0.9471 | 3.3925 | 6.5131 | 1.612 | 4.0404 | 6.541 | 2.295 | 2.8501 | 0.83304 | 0.24562 | 3.3917 | 0.86095 | 0.37417 | 2.301 | 7.9518 | 2.1822 | 3.644
[18 empty] | 02/23 17:00:00 | 5.4406 | 2.2647 | 2.4023 | 5.4127 | 1.5928 | 3.3981 | 5.4051 | 1.4995 | 3.6046 | 0.3106 | 0.1633 | 1.9021 | 0.28269 | 0.1021 | 2.7686 | 6.5127 | 1.7835 | 3.6517 | 6.5052 | 1.6861 | 3.8581 | 6.5296 | 2.2215 | 2.9393 | 3.2127 | 0.94699 | 3.3925 | 6.5128 | 1.6118 | 4.0406 | 6.5407 | 2.2948 | 2.8503 | 0.8327 | 0.24537 | 3.3937 | 0.86061 | 0.37379 | 2.3024 | 7.9515 | 2.1821 | 3.6439
[18 empty] | 02/23 18:00:00 | 5.4399 | 2.2645 | 2.4023 | 5.412 | 1.5927 | 3.3981 | 5.4045 | 1.4994 | 3.6046 | 0.30987 | 0.16292 | 1.902 | 0.28201 | 0.10186 | 2.7686 | 6.5121 | 1.7834 | 3.6516 | 6.5046 | 1.686 | 3.858 | 6.5288 | 2.2213 | 2.9392 | 3.2121 | 0.94678 | 3.3926 | 6.5121 | 1.6117 | 4.0406 | 6.5399 | 2.2945 | 2.8503 | 0.83202 | 0.24498 | 3.3963 | 0.85988 | 0.37319 | 2.3041 | 7.9508 | 2.182 | 3.6439
[18 empty] | 02/23 19:00:00 | 5.439 | 2.2639 | 2.4024 | 5.4112 | 1.5923 | 3.3984 | 5.4037 | 1.499 | 3.6049 | 0.309 | 0.16244 | 1.9022 | 0.28123 | 0.10157 | 2.7689 | 6.5113 | 1.7831 | 3.6517 | 6.5038 | 1.6858 | 3.8581 | 6.528 | 2.2209 | 2.9393 | 3.2113 | 0.94648 | 3.3928 | 6.5112 | 1.6113 | 4.041 | 6.5391 | 2.2939 | 2.8506 | 0.83124 | 0.24459 | 3.3985 | 0.85901 | 0.37258 | 2.3055 | 7.95 | 2.1817 | 3.644
[18 empty] | 02/23 20:00:00 | 5.438 | 2.2635 | 2.4025 | 5.4101 | 1.5919 | 3.3985 | 5.4027 | 1.4987 | 3.605 | 0.30798 | 0.1619 | 1.9023 | 0.28009 | 0.10115 | 2.769 | 6.5101 | 1.7827 | 3.6519 | 6.5028 | 1.6854 | 3.8583 | 6.527 | 2.2204 | 2.9395 | 3.2101 | 0.94603 | 3.3933 | 6.5102 | 1.6109 | 4.0413 | 6.538 | 2.2933 | 2.8509 | 0.8301 | 0.244 | 3.4021 | 0.85799 | 0.3719 | 2.3071 | 7.9489 | 2.1812 | 3.6442
[18 empty] | 02/23 21:00:00 | 5.4371 | 2.2629 | 2.4027 | 5.4093 | 1.5916 | 3.3988 | 5.4019 | 1.4983 | 3.6053 | 0.30708 | 0.1614 | 1.9025 | 0.27931 | 0.10086 | 2.7694 | 6.5094 | 1.7824 | 3.6521 | 6.502 | 1.6851 | 3.8584 | 6.5261 | 2.22 | 2.9396 | 3.2094 | 0.94576 | 3.3934 | 6.5094 | 1.6107 | 4.0414 | 6.5371 | 2.2929 | 2.851 | 0.82932 | 0.24383 | 3.4012 | 0.85708 | 0.3715 | 2.3071 | 7.9481 | 2.181 | 3.6443
[18 empty] | 02/23 22:00:00 | 5.4363 | 2.2625 | 2.4028 | 5.4085 | 1.5913 | 3.3989 | 5.401 | 1.498 | 3.6055 | 0.30626 | 0.16097 | 1.9026 | 0.27852 | 0.10057 | 2.7695 | 6.5085 | 1.782 | 3.6523 | 6.5011 | 1.6848 | 3.8587 | 6.5253 | 2.2196 | 2.9399 | 3.2086 | 0.94541 | 3.3938 | 6.5086 | 1.6102 | 4.0421 | 6.5363 | 2.2922 | 2.8516 | 0.82853 | 0.24348 | 3.4028 | 0.85627 | 0.37095 | 2.3083 | 7.9472 | 2.1805 | 3.6446
[18 empty] | 02/23 23:00:00 | 5.434 | 2.2618 | 2.4026 | 5.4064 | 1.5908 | 3.3986 | 5.3992 | 1.4976 | 3.6053 | 0.30404 | 0.15982 | 1.9024 | 0.27642 | 0.099815 | 2.7693 | 6.5065 | 1.7815 | 3.6521 | 6.4994 | 1.6844 | 3.8585 | 6.523 | 2.2189 | 2.9397 | 3.2065 | 0.94477 | 3.3939 | 6.5066 | 1.6099 | 4.0417 | 6.5341 | 2.2916 | 2.8513 | 0.82644 | 0.24237 | 3.4098 | 0.85404 | 0.36932 | 2.3125 | 7.9451 | 2.1801 | 3.6445
[18 empty] | 02/23 24:00:00 | 5.4342 | 2.2618 | 2.4026 | 5.4065 | 1.5908 | 3.3986 | 5.3992 | 1.4976 | 3.6053 | 0.30421 | 0.15991 | 1.9024 | 0.27647 | 0.099836 | 2.7693 | 6.5065 | 1.7816 | 3.6521 | 6.4993 | 1.6844 | 3.8586 | 6.5232 | 2.219 | 2.9397 | 3.2065 | 0.94489 | 3.3935 | 6.5066 | 1.61 | 4.0413 | 6.5343 | 2.292 | 2.851 | 0.82649 | 0.24307 | 3.4002 | 0.85422 | 0.37042 | 2.3061 | 7.9452 | 2.1801 | 3.6444
[18 empty] | 02/24 01:00:00 | 5.4347 | 2.2622 | 2.4024 | 5.4069 | 1.5911 | 3.3983 | 5.3993 | 1.4978 | 3.6049 | 0.30472 | 0.1602 | 1.9022 | 0.27686 | 0.09999 | 2.7689 | 6.5069 | 1.7818 | 3.652 | 6.4994 | 1.6845 | 3.8584 | 6.5237 | 2.2193 | 2.9395 | 3.2069 | 0.94509 | 3.3932 | 6.5069 | 1.6103 | 4.0409 | 6.5348 | 2.2924 | 2.8507 | 0.82687 | 0.24355 | 3.3951 | 0.85473 | 0.37112 | 2.3031 | 7.9456 | 2.1803 | 3.6443
[18 empty] | 02/24 02:00:00 | 5.4357 | 2.2627 | 2.4023 | 5.4077 | 1.5914 | 3.3982 | 5.3999 | 1.498 | 3.6047 | 0.30566 | 0.1607 | 1.9021 | 0.27767 | 0.10029 | 2.7687 | 6.5077 | 1.7821 | 3.6517 | 6.5 | 1.6848 | 3.858 | 6.5246 | 2.2198 | 2.9393 | 3.2077 | 0.94547 | 3.3927 | 6.5078 | 1.6107 | 4.0404 | 6.5357 | 2.2931 | 2.8502 | 0.82768 | 0.24415 | 3.39 | 0.85567 | 0.37203 | 2.3 | 7.9465 | 2.1807 | 3.644
[18 empty] | 02/24 03:00:00 | 5.4368 | 2.2633 | 2.4021 | 5.4086 | 1.5918 | 3.3979 | 5.401 | 1.4984 | 3.6044 | 0.30677 | 0.1613 | 1.9019 | 0.27856 | 0.10062 | 2.7684 | 6.5087 | 1.7824 | 3.6516 | 6.5009 | 1.685 | 3.858 | 6.5257 | 2.2202 | 2.9392 | 3.2087 | 0.94582 | 3.3925 | 6.5087 | 1.6109 | 4.0404 | 6.5368 | 2.2935 | 2.8502 | 0.82856 | 0.24454 | 3.3883 | 0.85678 | 0.37267 | 2.2991 | 7.9475 | 2.181 | 3.6439
[18 empty] | 02/24 04:00:00 | 5.4119 | 2.2554 | 2.3995 | 5.3997 | 1.5898 | 3.3965 | 5.3908 | 1.4962 | 3.6029 | 0.28186 | 0.1484 | 1.8993 | 0.26968 | 0.097459 | 2.7671 | 6.4998 | 1.7804 | 3.6507 | 6.4906 | 1.6826 | 3.8576 | 6.5068 | 2.2149 | 2.9378 | 3.1998 | 0.94262 | 3.3946 | 6.4999 | 1.6074 | 4.0438 | 6.5122 | 2.2799 | 2.8564 | 0.81968 | 0.23738 | 3.4531 | 0.83186 | 0.34566 | 2.4066 | 7.9335 | 2.1776 | 3.6431
[18 empty] | 02/24 05:00:00 | 5.4198 | 2.258 | 2.4003 | 5.4022 | 1.5903 | 3.3969 | 5.3939 | 1.4969 | 3.6033 | 0.28982 | 0.15252 | 1.9001 | 0.27216 | 0.098346 | 2.7674 | 6.5022 | 1.7813 | 3.6502 | 6.4941 | 1.6838 | 3.8567 | 6.5127 | 2.2173 | 2.9373 | 3.2022 | 0.94441 | 3.3907 | 6.5022 | 1.6111 | 4.0359 | 6.5199 | 2.294 | 2.8421 | 0.82218 | 0.24273 | 3.3872 | 0.83984 | 0.36788 | 2.2829 | 7.9374 | 2.1793 | 3.6422
[18 empty] | 02/24 06:00:00 | 5.4362 | 2.263 | 2.4022 | 5.4087 | 1.5917 | 3.398 | 5.4 | 1.4982 | 3.6044 | 0.30622 | 0.161 | 1.902 | 0.27874 | 0.10068 | 2.7686 | 6.5087 | 1.7826 | 3.6513 | 6.5002 | 1.6852 | 3.8572 | 6.5255 | 2.2203 | 2.9389 | 3.2087 | 0.9461 | 3.3915 | 6.5087 | 1.6107 | 4.0409 | 6.5361 | 2.2929 | 2.8505 | 0.82875 | 0.24649 | 3.3622 | 0.85622 | 0.37929 | 2.2574 | 7.9469 | 2.1812 | 3.6434
[18 empty] | 02/24 07:00:00 | 5.4364 | 2.2629 | 2.4024 | 5.4087 | 1.5916 | 3.3983 | 5.4002 | 1.4981 | 3.6047 | 0.30638 | 0.16107 | 1.9022 | 0.2787 | 0.10065 | 2.7689 | 6.5087 | 1.7824 | 3.6517 | 6.5004 | 1.685 | 3.8579 | 6.5255 | 2.2201 | 2.9393 | 3.2087 | 0.94574 | 3.3928 | 6.5087 | 1.6107 | 4.0408 | 6.5363 | 2.2931 | 2.8505 | 0.8287 | 0.24479 | 3.3853 | 0.85638 | 0.37377 | 2.2912 | 7.9471 | 2.1809 | 3.644
[18 empty] | 02/24 08:00:00 | 5.4368 | 2.2631 | 2.4024 | 5.409 | 1.5917 | 3.3983 | 5.4008 | 1.4982 | 3.6048 | 0.30684 | 0.16131 | 1.9022 | 0.279 | 0.10076 | 2.7689 | 6.509 | 1.7824 | 3.6518 | 6.5009 | 1.685 | 3.8581 | 6.5259 | 2.2201 | 2.9394 | 3.209 | 0.94581 | 3.3929 | 6.509 | 1.6108 | 4.0408 | 6.5369 | 2.2933 | 2.8505 | 0.82901 | 0.24457 | 3.3896 | 0.85685 | 0.37281 | 2.2983 | 7.9477 | 2.181 | 3.6441
[18 empty] | 02/24 09:00:00 | 5.4377 | 2.2631 | 2.4028 | 5.4101 | 1.5917 | 3.3988 | 5.4022 | 1.4984 | 3.6054 | 0.3077 | 0.16173 | 1.9026 | 0.28006 | 0.10112 | 2.7695 | 6.5101 | 1.7826 | 3.6521 | 6.5022 | 1.6852 | 3.8585 | 6.5269 | 2.2203 | 2.9396 | 3.2101 | 0.94609 | 3.393 | 6.5101 | 1.611 | 4.0409 | 6.5378 | 2.2934 | 2.8507 | 0.83007 | 0.2451 | 3.3866 | 0.8577 | 0.37306 | 2.2991 | 7.9487 | 2.1811 | 3.6443
[18 empty] | 02/24 10:00:00 | 5.4395 | 2.2635 | 2.4031 | 5.4116 | 1.592 | 3.3993 | 5.4039 | 1.4987 | 3.6058 | 0.30947 | 0.16263 | 1.903 | 0.28163 | 0.10167 | 2.7699 | 6.5116 | 1.7828 | 3.6526 | 6.5038 | 1.6854 | 3.859 | 6.5286 | 2.2206 | 2.9401 | 3.2116 | 0.94647 | 3.3933 | 6.5116 | 1.6113 | 4.0412 | 6.5395 | 2.2939 | 2.8509 | 0.83163 | 0.24585 | 3.3827 | 0.85948 | 0.37431 | 2.2962 | 7.9503 | 2.1813 | 3.6448
[18 empty] | 02/24 11:00:00 | 5.4406 | 2.2636 | 2.4035 | 5.4127 | 1.5921 | 3.3998 | 5.4049 | 1.4987 | 3.6064 | 0.31057 | 0.16317 | 1.9034 | 0.28267 | 0.10203 | 2.7705 | 6.5127 | 1.7829 | 3.6529 | 6.5048 | 1.6855 | 3.8593 | 6.5296 | 2.2207 | 2.9404 | 3.2127 | 0.94664 | 3.3938 | 6.5127 | 1.6113 | 4.0419 | 6.5406 | 2.2937 | 2.8515 | 0.83267 | 0.246 | 3.3848 | 0.86058 | 0.37449 | 2.298 | 7.9513 | 2.1813 | 3.6451
[18 empty] | 02/24 12:00:00 | 5.4408 | 2.2638 | 2.4034 | 5.413 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.3108 | 0.1633 | 1.9033 | 0.28303 | 0.10216 | 2.7704 | 6.513 | 1.7829 | 3.6531 | 6.5052 | 1.6855 | 3.8596 | 6.5298 | 2.2206 | 2.9405 | 3.213 | 0.94668 | 3.394 | 6.5131 | 1.6114 | 4.0418 | 6.5408 | 2.2939 | 2.8515 | 0.83303 | 0.24585 | 3.3884 | 0.86081 | 0.37417 | 2.3006 | 7.9517 | 2.1813 | 3.6454
[18 empty] | 02/24 13:00:00 | 5.4409 | 2.2643 | 2.403 | 5.4133 | 1.5926 | 3.3991 | 5.4055 | 1.4992 | 3.6056 | 0.31094 | 0.16341 | 1.9028 | 0.28326 | 0.10227 | 2.7697 | 6.5133 | 1.7831 | 3.6527 | 6.5055 | 1.6857 | 3.8592 | 6.53 | 2.221 | 2.9402 | 3.2133 | 0.94689 | 3.3935 | 6.5133 | 1.6117 | 4.0412 | 6.541 | 2.2943 | 2.8509 | 0.83327 | 0.24584 | 3.3894 | 0.86094 | 0.37416 | 2.301 | 7.9519 | 2.1816 | 3.645
[18 empty] | 02/24 14:00:00 | 5.4409 | 2.2647 | 2.4025 | 5.4134 | 1.5929 | 3.3985 | 5.4057 | 1.4995 | 3.6049 | 0.31092 | 0.16345 | 1.9023 | 0.28335 | 0.10233 | 2.769 | 6.5134 | 1.7834 | 3.6521 | 6.5057 | 1.686 | 3.8586 | 6.53 | 2.2213 | 2.9397 | 3.2134 | 0.94709 | 3.3929 | 6.5134 | 1.612 | 4.0406 | 6.541 | 2.2948 | 2.8504 | 0.83336 | 0.24583 | 3.39 | 0.86093 | 0.37412 | 2.3012 | 7.952 | 2.182 | 3.6444
[18 empty] | 02/24 15:00:00 | 5.4407 | 2.2647 | 2.4023 | 5.4132 | 1.593 | 3.3982 | 5.4056 | 1.4996 | 3.6047 | 0.31066 | 0.16333 | 1.9021 | 0.28321 | 0.10229 | 2.7687 | 6.5132 | 1.7836 | 3.6518 | 6.5056 | 1.6862 | 3.8582 | 6.5298 | 2.2215 | 2.9393 | 3.2132 | 0.94714 | 3.3926 | 6.5133 | 1.612 | 4.0405 | 6.5407 | 2.2948 | 2.8502 | 0.83322 | 0.24567 | 3.3916 | 0.86067 | 0.37387 | 2.302 | 7.9519 | 2.1822 | 3.644
[18 empty] | 02/24 16:00:00 | 5.4403 | 2.2646 | 2.4023 | 5.4129 | 1.5929 | 3.3982 | 5.4053 | 1.4995 | 3.6047 | 0.3103 | 0.16314 | 1.9021 | 0.2829 | 0.10218 | 2.7687 | 6.5129 | 1.7836 | 3.6517 | 6.5054 | 1.6862 | 3.8581 | 6.5294 | 2.2215 | 2.9393 | 3.2129 | 0.94706 | 3.3925 | 6.513 | 1.6119 | 4.0405 | 6.5404 | 2.2947 | 2.8502 | 0.83291 | 0.24546 | 3.3932 | 0.8603 | 0.37361 | 2.3027 | 7.9515 | 2.1821 | 3.6439
[18 empty] | 02/24 17:00:00 | 5.4398 | 2.2645 | 2.4022 | 5.4124 | 1.5928 | 3.3981 | 5.4048 | 1.4994 | 3.6046 | 0.30977 | 0.16286 | 1.902 | 0.28236 | 0.10199 | 2.7686 | 6.5124 | 1.7834 | 3.6516 | 6.5048 | 1.686 | 3.8581 | 6.5289 | 2.2213 | 2.9392 | 3.2124 | 0.94689 | 3.3926 | 6.5124 | 1.6117 | 4.0406 | 6.5398 | 2.2945 | 2.8503 | 0.83237 | 0.24515 | 3.3954 | 0.85977 | 0.37323 | 2.3036 | 7.951 | 2.182 | 3.6439
[18 empty] | 02/24 18:00:00 | 5.4382 | 2.2639 | 2.4021 | 5.4108 | 1.5924 | 3.3979 | 5.4032 | 1.4991 | 3.6044 | 0.30819 | 0.16205 | 1.9019 | 0.28075 | 0.10141 | 2.7684 | 6.5108 | 1.7831 | 3.6515 | 6.5033 | 1.6857 | 3.8579 | 6.5274 | 2.2209 | 2.9391 | 3.2108 | 0.94636 | 3.3928 | 6.5109 | 1.6112 | 4.0409 | 6.5383 | 2.2937 | 2.8505 | 0.83076 | 0.24413 | 3.4029 | 0.8582 | 0.37186 | 2.3078 | 7.9494 | 2.1816 | 3.6438
[18 empty] | 02/24 19:00:00 | 5.4361 | 2.2632 | 2.4019 | 5.4085 | 1.5919 | 3.3976 | 5.4011 | 1.4986 | 3.6042 | 0.30605 | 0.16094 | 1.9016 | 0.27851 | 0.10061 | 2.7681 | 6.5086 | 1.7826 | 3.6513 | 6.5013 | 1.6853 | 3.8576 | 6.5251 | 2.2202 | 2.9389 | 3.2086 | 0.9457 | 3.3928 | 6.5087 | 1.6107 | 4.0408 | 6.5361 | 2.2931 | 2.8504 | 0.82853 | 0.24303 | 3.4092 | 0.85606 | 0.37045 | 2.3109 | 7.9472 | 2.1812 | 3.6436
[18 empty] | 02/24 20:00:00 | 5.4353 | 2.263 | 2.4018 | 5.4078 | 1.5917 | 3.3975 | 5.4005 | 1.4984 | 3.6041 | 0.30526 | 0.16053 | 1.9016 | 0.27781 | 0.10036 | 2.768 | 6.5079 | 1.7824 | 3.6511 | 6.5006 | 1.6852 | 3.8575 | 6.5243 | 2.2201 | 2.9388 | 3.2079 | 0.94559 | 3.3925 | 6.5079 | 1.6107 | 4.0403 | 6.5353 | 2.293 | 2.8501 | 0.82782 | 0.24327 | 3.4029 | 0.85527 | 0.37061 | 2.3077 | 7.9465 | 2.181 | 3.6435
[18 empty] | 02/24 21:00:00 | 5.4351 | 2.2629 | 2.4018 | 5.4076 | 1.5916 | 3.3975 | 5.4003 | 1.4984 | 3.6041 | 0.30508 | 0.16044 | 1.9015 | 0.27758 | 0.10028 | 2.768 | 6.5076 | 1.7824 | 3.6511 | 6.5004 | 1.6852 | 3.8575 | 6.5241 | 2.22 | 2.9388 | 3.2076 | 0.94556 | 3.3923 | 6.5077 | 1.6107 | 4.0402 | 6.5351 | 2.2931 | 2.85 | 0.8276 | 0.24353 | 3.3984 | 0.85509 | 0.37098 | 2.305 | 7.9463 | 2.181 | 3.6434
[18 empty] | 02/24 22:00:00 | 5.4353 | 2.263 | 2.4018 | 5.4077 | 1.5917 | 3.3975 | 5.4003 | 1.4984 | 3.6041 | 0.30532 | 0.16056 | 1.9016 | 0.27768 | 0.10032 | 2.768 | 6.5077 | 1.7824 | 3.6511 | 6.5004 | 1.6851 | 3.8575 | 6.5243 | 2.2201 | 2.9388 | 3.2077 | 0.94561 | 3.3922 | 6.5078 | 1.6108 | 4.0402 | 6.5354 | 2.2932 | 2.8499 | 0.82769 | 0.24379 | 3.3951 | 0.85532 | 0.37141 | 2.3029 | 7.9464 | 2.181 | 3.6434
[18 empty] | 02/24 23:00:00 | 5.4355 | 2.2631 | 2.4018 | 5.4078 | 1.5917 | 3.3975 | 5.4003 | 1.4984 | 3.6041 | 0.30546 | 0.16064 | 1.9016 | 0.27776 | 0.10035 | 2.768 | 6.5078 | 1.7824 | 3.6511 | 6.5004 | 1.6851 | 3.8575 | 6.5245 | 2.2201 | 2.9388 | 3.2078 | 0.94563 | 3.3922 | 6.5078 | 1.6108 | 4.0402 | 6.5355 | 2.2932 | 2.85 | 0.82777 | 0.24387 | 3.3943 | 0.85547 | 0.3715 | 2.3027 | 7.9465 | 2.181 | 3.6434
[18 empty] | 02/24 24:00:00 | 5.4353 | 2.2633 | 2.4015 | 5.4077 | 1.5918 | 3.3971 | 5.4002 | 1.4985 | 3.6036 | 0.30534 | 0.1606 | 1.9013 | 0.27768 | 0.10033 | 2.7676 | 6.5077 | 1.7825 | 3.6509 | 6.5003 | 1.6852 | 3.8573 | 6.5244 | 2.2202 | 2.9386 | 3.2077 | 0.94567 | 3.392 | 6.5078 | 1.6109 | 4.0398 | 6.5354 | 2.2934 | 2.8496 | 0.82769 | 0.24384 | 3.3944 | 0.85535 | 0.37139 | 2.3031 | 7.9464 | 2.1811 | 3.6433
[18 empty] | 02/25 01:00:00 | 5.4355 | 2.2635 | 2.4014 | 5.4078 | 1.592 | 3.3969 | 5.4002 | 1.4987 | 3.6034 | 0.3055 | 0.1607 | 1.9011 | 0.27778 | 0.10038 | 2.7673 | 6.5078 | 1.7827 | 3.6506 | 6.5003 | 1.6853 | 3.857 | 6.5245 | 2.2205 | 2.9384 | 3.2078 | 0.9458 | 3.3916 | 6.5079 | 1.611 | 4.0395 | 6.5356 | 2.2937 | 2.8494 | 0.82779 | 0.24396 | 3.3932 | 0.85551 | 0.37163 | 2.3021 | 7.9465 | 2.1813 | 3.6429
[18 empty] | 02/25 02:00:00 | 5.4358 | 2.2639 | 2.4011 | 5.408 | 1.5922 | 3.3965 | 5.4003 | 1.4989 | 3.603 | 0.30582 | 0.16089 | 1.9008 | 0.278 | 0.10047 | 2.7669 | 6.508 | 1.7829 | 3.6504 | 6.5004 | 1.6854 | 3.8568 | 6.5248 | 2.2207 | 2.9382 | 3.208 | 0.94596 | 3.3913 | 6.5081 | 1.6113 | 4.0391 | 6.5359 | 2.2941 | 2.849 | 0.82801 | 0.24413 | 3.3917 | 0.85583 | 0.37195 | 2.3009 | 7.9467 | 2.1815 | 3.6427
[18 empty] | 02/25 03:00:00 | 5.4361 | 2.2641 | 2.401 | 5.4082 | 1.5924 | 3.3963 | 5.4005 | 1.499 | 3.6027 | 0.30609 | 0.16105 | 1.9007 | 0.2782 | 0.10055 | 2.7667 | 6.5082 | 1.7831 | 3.65 | 6.5005 | 1.6856 | 3.8565 | 6.5251 | 2.221 | 2.9379 | 3.2082 | 0.94611 | 3.391 | 6.5083 | 1.6114 | 4.0389 | 6.5361 | 2.2943 | 2.8488 | 0.82821 | 0.24423 | 3.3912 | 0.8561 | 0.37212 | 2.3006 | 7.947 | 2.1818 | 3.6424
[18 empty] | 02/25 04:00:00 | 5.4366 | 2.2643 | 2.401 | 5.4086 | 1.5925 | 3.3964 | 5.4008 | 1.4991 | 3.6028 | 0.30659 | 0.1613 | 1.9007 | 0.27858 | 0.10069 | 2.7667 | 6.5086 | 1.7832 | 3.65 | 6.5008 | 1.6857 | 3.8564 | 6.5255 | 2.2212 | 2.9379 | 3.2086 | 0.94625 | 3.3909 | 6.5086 | 1.6115 | 4.0388 | 6.5366 | 2.2946 | 2.8487 | 0.82859 | 0.24444 | 3.3897 | 0.8566 | 0.37252 | 2.2995 | 7.9474 | 2.1819 | 3.6424
[18 empty] | 02/25 05:00:00 | 5.4375 | 2.2648 | 2.4009 | 5.4093 | 1.5928 | 3.3961 | 5.4015 | 1.4994 | 3.6024 | 0.30751 | 0.16181 | 1.9005 | 0.27931 | 0.10097 | 2.7664 | 6.5093 | 1.7834 | 3.6499 | 6.5015 | 1.6859 | 3.8564 | 6.5264 | 2.2215 | 2.9378 | 3.2093 | 0.94655 | 3.3906 | 6.5094 | 1.6119 | 4.0384 | 6.5376 | 2.2952 | 2.8484 | 0.82932 | 0.24487 | 3.3868 | 0.85752 | 0.37323 | 2.2976 | 7.9481 | 2.1822 | 3.6423
[18 empty] | 02/25 06:00:00 | 5.438 | 2.2651 | 2.4007 | 5.4097 | 1.593 | 3.3959 | 5.4019 | 1.4996 | 3.6022 | 0.30797 | 0.16206 | 1.9004 | 0.27973 | 0.10113 | 2.7662 | 6.5098 | 1.7837 | 3.6496 | 6.5018 | 1.6861 | 3.8561 | 6.5269 | 2.2219 | 2.9376 | 3.2098 | 0.94675 | 3.3903 | 6.5098 | 1.612 | 4.0383 | 6.538 | 2.2955 | 2.8482 | 0.82974 | 0.24496 | 3.3873 | 0.85798 | 0.37334 | 2.2981 | 7.9486 | 2.1825 | 3.642
[18 empty] | 02/25 07:00:00 | 5.4385 | 2.2653 | 2.4008 | 5.4102 | 1.5931 | 3.3959 | 5.4023 | 1.4997 | 3.6023 | 0.30846 | 0.16231 | 1.9004 | 0.28018 | 0.10129 | 2.7662 | 6.5102 | 1.7838 | 3.6496 | 6.5023 | 1.6863 | 3.856 | 6.5273 | 2.222 | 2.9376 | 3.2102 | 0.94689 | 3.3902 | 6.5102 | 1.6121 | 4.0383 | 6.5385 | 2.2956 | 2.8483 | 0.83019 | 0.2451 | 3.3871 | 0.85847 | 0.37356 | 2.2981 | 7.949 | 2.1826 | 3.642
[18 empty] | 02/25 08:00:00 | 5.439 | 2.2652 | 2.4011 | 5.4107 | 1.5931 | 3.3964 | 5.4028 | 1.4996 | 3.6028 | 0.30899 | 0.16256 | 1.9008 | 0.28073 | 0.10147 | 2.7667 | 6.5108 | 1.7838 | 3.6499 | 6.5028 | 1.6863 | 3.8562 | 6.5278 | 2.222 | 2.9378 | 3.2107 | 0.94698 | 3.3905 | 6.5108 | 1.6121 | 4.0387 | 6.539 | 2.2955 | 2.8486 | 0.83073 | 0.24528 | 3.3868 | 0.85899 | 0.37377 | 2.2982 | 7.9496 | 2.1826 | 3.6422
[18 empty] | 02/25 09:00:00 | 5.4396 | 2.2652 | 2.4013 | 5.4113 | 1.5931 | 3.3967 | 5.4034 | 1.4997 | 3.6031 | 0.30963 | 0.16288 | 1.901 | 0.28133 | 0.10167 | 2.7671 | 6.5113 | 1.7838 | 3.6503 | 6.5034 | 1.6863 | 3.8566 | 6.5285 | 2.222 | 2.9381 | 3.2113 | 0.94706 | 3.3908 | 6.5114 | 1.6122 | 4.0389 | 6.5397 | 2.2956 | 2.8488 | 0.83133 | 0.2455 | 3.3863 | 0.85964 | 0.37412 | 2.2978 | 7.9502 | 2.1826 | 3.6426
[18 empty] | 02/25 10:00:00 | 5.4401 | 2.2654 | 2.4014 | 5.4118 | 1.5932 | 3.3968 | 5.4039 | 1.4998 | 3.6031 | 0.31006 | 0.1631 | 1.9011 | 0.28178 | 0.10183 | 2.7671 | 6.5118 | 1.7839 | 3.6504 | 6.5039 | 1.6864 | 3.8568 | 6.5289 | 2.2221 | 2.9382 | 3.2118 | 0.94717 | 3.391 | 6.5118 | 1.6122 | 4.039 | 6.5401 | 2.2956 | 2.8489 | 0.83179 | 0.2456 | 3.3868 | 0.86007 | 0.37422 | 2.2983 | 7.9507 | 2.1826 | 3.6427
[18 empty] | 02/25 11:00:00 | 5.4405 | 2.2655 | 2.4014 | 5.4124 | 1.5934 | 3.3968 | 5.4045 | 1.4999 | 3.6032 | 0.31051 | 0.16333 | 1.9011 | 0.28237 | 0.10204 | 2.7672 | 6.5124 | 1.784 | 3.6504 | 6.5045 | 1.6865 | 3.8568 | 6.5294 | 2.2222 | 2.9382 | 3.2124 | 0.94735 | 3.3909 | 6.5124 | 1.6124 | 4.0389 | 6.5406 | 2.2958 | 2.8489 | 0.83237 | 0.24585 | 3.3857 | 0.86051 | 0.37445 | 2.2981 | 7.9512 | 2.1828 | 3.6428
[18 empty] | 02/25 12:00:00 | 5.4413 | 2.266 | 2.4012 | 5.4134 | 1.5938 | 3.3966 | 5.4056 | 1.5003 | 3.6029 | 0.31128 | 0.16375 | 1.9009 | 0.28342 | 0.10243 | 2.7669 | 6.5134 | 1.7843 | 3.6503 | 6.5056 | 1.6868 | 3.8568 | 6.5301 | 2.2226 | 2.9381 | 3.2134 | 0.94774 | 3.3906 | 6.5135 | 1.6128 | 4.0385 | 6.5413 | 2.2964 | 2.8485 | 0.83343 | 0.24641 | 3.3822 | 0.86128 | 0.37503 | 2.2966 | 7.9521 | 2.183 | 3.6427
[18 empty] | 02/25 13:00:00 | 5.4415 | 2.2666 | 2.4008 | 5.4137 | 1.5942 | 3.396 | 5.406 | 1.5007 | 3.6023 | 0.31155 | 0.16394 | 1.9004 | 0.28372 | 0.10257 | 2.7662 | 6.5137 | 1.7847 | 3.6499 | 6.506 | 1.6871 | 3.8564 | 6.5305 | 2.223 | 2.9377 | 3.2137 | 0.94795 | 3.3902 | 6.5138 | 1.6131 | 4.0381 | 6.5416 | 2.2969 | 2.8481 | 0.83373 | 0.24633 | 3.3845 | 0.86156 | 0.37504 | 2.2972 | 7.9524 | 2.1834 | 3.6422
[18 empty] | 02/25 14:00:00 | 5.4415 | 2.267 | 2.4004 | 5.4138 | 1.5945 | 3.3953 | 5.4061 | 1.501 | 3.6016 | 0.31154 | 0.16398 | 1.8999 | 0.28377 | 0.10261 | 2.7655 | 6.5138 | 1.7849 | 3.6493 | 6.5061 | 1.6873 | 3.8558 | 6.5305 | 2.2233 | 2.9373 | 3.2138 | 0.94813 | 3.3896 | 6.5138 | 1.6133 | 4.0375 | 6.5416 | 2.2973 | 2.8476 | 0.83378 | 0.24624 | 3.3861 | 0.86155 | 0.37494 | 2.2978 | 7.9525 | 2.1837 | 3.6417
[18 empty] | 02/25 15:00:00 | 5.413 | 2.2579 | 2.3974 | 5.401 | 1.5915 | 3.3935 | 5.3925 | 1.498 | 3.5998 | 0.28304 | 0.1492 | 1.897 | 0.27095 | 0.09804 | 2.7637 | 6.5011 | 1.7821 | 3.6481 | 6.4925 | 1.6842 | 3.8549 | 6.508 | 2.2169 | 2.9356 | 3.2011 | 0.94361 | 3.3924 | 6.5012 | 1.6083 | 4.0422 | 6.5134 | 2.2817 | 2.8546 | 0.82096 | 0.23634 | 3.4737 | 0.83304 | 0.34473 | 2.4165 | 7.9348 | 2.1795 | 3.6407
[18 empty] | 02/25 16:00:00 | 5.4215 | 2.2604 | 2.3985 | 5.4041 | 1.5921 | 3.3943 | 5.3952 | 1.4985 | 3.6005 | 0.29153 | 0.15358 | 1.8982 | 0.27413 | 0.09916 | 2.7645 | 6.5042 | 1.7831 | 3.6476 | 6.4953 | 1.6853 | 3.8541 | 6.5144 | 2.2195 | 2.9351 | 3.2041 | 0.94595 | 3.3872 | 6.5042 | 1.6132 | 4.0319 | 6.5215 | 2.2972 | 2.8389 | 0.82415 | 0.24365 | 3.3825 | 0.84155 | 0.36932 | 2.2786 | 7.9392 | 2.1813 | 3.6396
[18 empty] | 02/25 17:00:00 | 5.44 | 2.2662 | 2.4005 | 5.4126 | 1.594 | 3.3956 | 5.4034 | 1.5002 | 3.6017 | 0.31002 | 0.16316 | 1.9001 | 0.28262 | 0.10219 | 2.7658 | 6.5126 | 1.7847 | 3.6491 | 6.5035 | 1.687 | 3.8552 | 6.5294 | 2.2231 | 2.9371 | 3.2126 | 0.9481 | 3.3885 | 6.5124 | 1.6127 | 4.0383 | 6.5401 | 2.2964 | 2.848 | 0.83263 | 0.24861 | 3.3491 | 0.86002 | 0.38244 | 2.2488 | 7.9507 | 2.1835 | 3.6413
[18 empty] | 02/25 18:00:00 | 5.4395 | 2.2658 | 2.4007 | 5.412 | 1.5937 | 3.3959 | 5.4035 | 1.5001 | 3.6022 | 0.30955 | 0.16289 | 1.9003 | 0.28195 | 0.10193 | 2.7662 | 6.5119 | 1.7844 | 3.6494 | 6.5036 | 1.6867 | 3.8557 | 6.5287 | 2.2226 | 2.9374 | 3.2119 | 0.94747 | 3.39 | 6.5118 | 1.6125 | 4.0384 | 6.5396 | 2.296 | 2.8483 | 0.83195 | 0.24604 | 3.3813 | 0.85955 | 0.37563 | 2.2883 | 7.9503 | 2.1831 | 3.6417
[18 empty] | 02/25 19:00:00 | 5.4393 | 2.2656 | 2.4009 | 5.4115 | 1.5934 | 3.3961 | 5.4034 | 1.4999 | 3.6024 | 0.30928 | 0.16274 | 1.9005 | 0.28148 | 0.10175 | 2.7664 | 6.5115 | 1.7841 | 3.6497 | 6.5035 | 1.6866 | 3.8561 | 6.5283 | 2.2223 | 2.9376 | 3.2115 | 0.94722 | 3.3904 | 6.5114 | 1.6123 | 4.0386 | 6.5393 | 2.2958 | 2.8484 | 0.83148 | 0.24529 | 3.3898 | 0.85928 | 0.37401 | 2.2975 | 7.9501 | 2.1829 | 3.6421
[18 empty] | 02/25 20:00:00 | 5.4386 | 2.2651 | 2.4011 | 5.4108 | 1.5931 | 3.3964 | 5.403 | 1.4997 | 3.6028 | 0.30856 | 0.16234 | 1.9007 | 0.28077 | 0.10148 | 2.7667 | 6.5108 | 1.7838 | 3.6499 | 6.5031 | 1.6864 | 3.8563 | 6.5276 | 2.2219 | 2.9378 | 3.2108 | 0.94691 | 3.3908 | 6.5108 | 1.6119 | 4.0392 | 6.5386 | 2.2951 | 2.849 | 0.83078 | 0.24471 | 3.395 | 0.85857 | 0.3729 | 2.3024 | 7.9495 | 2.1826 | 3.6423
[18 empty] | 02/25 21:00:00 | 5.4373 | 2.2642 | 2.4014 | 5.4097 | 1.5925 | 3.3969 | 5.4021 | 1.4992 | 3.6034 | 0.3073 | 0.16165 | 1.9011 | 0.27969 | 0.10107 | 2.7673 | 6.5097 | 1.7833 | 3.6503 | 6.5022 | 1.686 | 3.8567 | 6.5263 | 2.2213 | 2.9381 | 3.2097 | 0.94642 | 3.3914 | 6.5098 | 1.6115 | 4.0397 | 6.5374 | 2.2943 | 2.8495 | 0.8297 | 0.24408 | 3.3992 | 0.85731 | 0.37181 | 2.3058 | 7.9485 | 2.1821 | 3.6427
[18 empty] | 02/25 22:00:00 | 5.4364 | 2.2635 | 2.4017 | 5.4089 | 1.592 | 3.3974 | 5.4014 | 1.4987 | 3.6039 | 0.30637 | 0.16112 | 1.9015 | 0.27887 | 0.10075 | 2.7679 | 6.5089 | 1.7829 | 3.6508 | 6.5014 | 1.6856 | 3.8571 | 6.5254 | 2.2206 | 2.9385 | 3.2089 | 0.94601 | 3.3921 | 6.509 | 1.611 | 4.0404 | 6.5364 | 2.2934 | 2.8501 | 0.82888 | 0.24375 | 3.4005 | 0.85638 | 0.37125 | 2.3068 | 7.9476 | 2.1815 | 3.6431
[18 empty] | 02/25 23:00:00 | 5.4353 | 2.263 | 2.4018 | 5.408 | 1.5917 | 3.3976 | 5.4007 | 1.4985 | 3.6041 | 0.30533 | 0.16057 | 1.9016 | 0.27796 | 0.10042 | 2.7681 | 6.508 | 1.7825 | 3.6511 | 6.5007 | 1.6853 | 3.8574 | 6.5244 | 2.2201 | 2.9388 | 3.208 | 0.94565 | 3.3924 | 6.5081 | 1.6108 | 4.0404 | 6.5354 | 2.293 | 2.8501 | 0.82797 | 0.24343 | 3.4013 | 0.85534 | 0.3707 | 2.3074 | 7.9467 | 2.1811 | 3.6434
[18 empty] | 02/25 24:00:00 | 5.4351 | 2.2627 | 2.4021 | 5.4077 | 1.5915 | 3.3979 | 5.4004 | 1.4982 | 3.6045 | 0.3051 | 0.16042 | 1.9019 | 0.27766 | 0.10029 | 2.7685 | 6.5077 | 1.7823 | 3.6513 | 6.5005 | 1.6851 | 3.8576 | 6.5242 | 2.2199 | 2.9389 | 3.2077 | 0.9455 | 3.3926 | 6.5078 | 1.6106 | 4.0407 | 6.5352 | 2.2928 | 2.8504 | 0.82767 | 0.24352 | 3.3987 | 0.85511 | 0.37092 | 2.3054 | 7.9464 | 2.1809 | 3.6436
[18 empty] | 02/26 01:00:00 | 5.4351 | 2.2625 | 2.4022 | 5.4076 | 1.5913 | 3.3981 | 5.4003 | 1.4981 | 3.6047 | 0.30511 | 0.16041 | 1.902 | 0.27757 | 0.10025 | 2.7687 | 6.5076 | 1.7821 | 3.6516 | 6.5004 | 1.6849 | 3.8579 | 6.5242 | 2.2197 | 2.9392 | 3.2076 | 0.9454 | 3.3929 | 6.5077 | 1.6105 | 4.0409 | 6.5352 | 2.2926 | 2.8505 | 0.82759 | 0.24362 | 3.397 | 0.85512 | 0.37108 | 2.3044 | 7.9463 | 2.1807 | 3.6439
[18 empty] | 02/26 02:00:00 | 5.4349 | 2.2625 | 2.4022 | 5.4074 | 1.5913 | 3.3981 | 5.4001 | 1.4981 | 3.6047 | 0.30491 | 0.16031 | 1.902 | 0.27738 | 0.10018 | 2.7687 | 6.5074 | 1.7821 | 3.6516 | 6.5002 | 1.6849 | 3.858 | 6.524 | 2.2196 | 2.9393 | 3.2074 | 0.94532 | 3.393 | 6.5075 | 1.6104 | 4.0409 | 6.535 | 2.2925 | 2.8506 | 0.82739 | 0.24356 | 3.3971 | 0.85491 | 0.37093 | 2.3048 | 7.9461 | 2.1806 | 3.644
[18 empty] | 02/26 03:00:00 | 5.4346 | 2.2626 | 2.4019 | 5.4071 | 1.5914 | 3.3977 | 5.4 | 1.4982 | 3.6043 | 0.30465 | 0.1602 | 1.9017 | 0.27714 | 0.10011 | 2.7682 | 6.5072 | 1.7821 | 3.6514 | 6.5 | 1.6849 | 3.8578 | 6.5237 | 2.2197 | 2.9391 | 3.2072 | 0.94532 | 3.3927 | 6.5072 | 1.6105 | 4.0404 | 6.5347 | 2.2927 | 2.8502 | 0.82715 | 0.2435 | 3.3969 | 0.85466 | 0.37083 | 2.3047 | 7.9458 | 2.1807 | 3.6438
[18 empty] | 02/26 04:00:00 | 5.4346 | 2.2625 | 2.402 | 5.4071 | 1.5913 | 3.3978 | 5.3999 | 1.4981 | 3.6044 | 0.3046 | 0.16016 | 1.9018 | 0.27705 | 0.10008 | 2.7684 | 6.5071 | 1.7821 | 3.6513 | 6.4999 | 1.685 | 3.8576 | 6.5237 | 2.2197 | 2.939 | 3.2071 | 0.94532 | 3.3926 | 6.5071 | 1.6104 | 4.0406 | 6.5347 | 2.2926 | 2.8503 | 0.82706 | 0.24351 | 3.3964 | 0.85461 | 0.37088 | 2.3042 | 7.9458 | 2.1807 | 3.6436
[18 empty] | 02/26 05:00:00 | 5.4347 | 2.2624 | 2.4022 | 5.4071 | 1.5912 | 3.3981 | 5.3998 | 1.498 | 3.6047 | 0.30468 | 0.16019 | 1.902 | 0.27708 | 0.10008 | 2.7687 | 6.5071 | 1.782 | 3.6516 | 6.4999 | 1.6848 | 3.8579 | 6.5237 | 2.2196 | 2.9392 | 3.2071 | 0.94526 | 3.3928 | 6.5072 | 1.6104 | 4.0408 | 6.5347 | 2.2925 | 2.8505 | 0.82709 | 0.24356 | 3.3958 | 0.85469 | 0.37098 | 2.3039 | 7.9458 | 2.1806 | 3.6439
[18 empty] | 02/26 06:00:00 | 5.4347 | 2.2621 | 2.4025 | 5.4071 | 1.591 | 3.3985 | 5.3997 | 1.4978 | 3.6051 | 0.30467 | 0.16016 | 1.9023 | 0.27706 | 0.10005 | 2.7691 | 6.5071 | 1.7819 | 3.6518 | 6.4998 | 1.6847 | 3.8581 | 6.5237 | 2.2194 | 2.9394 | 3.2071 | 0.94516 | 3.3932 | 6.5071 | 1.6102 | 4.0413 | 6.5347 | 2.2922 | 2.8509 | 0.82707 | 0.24352 | 3.3963 | 0.85468 | 0.37087 | 2.3045 | 7.9458 | 2.1805 | 3.6441
[18 empty] | 02/26 07:00:00 | 5.4345 | 2.2617 | 2.4029 | 5.407 | 1.5907 | 3.3991 | 5.3996 | 1.4975 | 3.6057 | 0.30453 | 0.16005 | 1.9028 | 0.27695 | 0.09999 | 2.7698 | 6.507 | 1.7816 | 3.6523 | 6.4997 | 1.6844 | 3.8586 | 6.5236 | 2.219 | 2.9398 | 3.207 | 0.94496 | 3.3938 | 6.507 | 1.6099 | 4.0419 | 6.5346 | 2.2917 | 2.8515 | 0.82696 | 0.2434 | 3.3975 | 0.85454 | 0.37066 | 2.3055 | 7.9457 | 2.1801 | 3.6446
[18 empty] | 02/26 08:00:00 | 5.4358 | 2.2616 | 2.4035 | 5.4081 | 1.5907 | 3.3999 | 5.4004 | 1.4974 | 3.6065 | 0.30579 | 0.16066 | 1.9034 | 0.27809 | 0.10037 | 2.7706 | 6.5081 | 1.7816 | 3.653 | 6.5004 | 1.6844 | 3.8592 | 6.5248 | 2.219 | 2.9404 | 3.2081 | 0.9452 | 3.3941 | 6.5081 | 1.6101 | 4.042 | 6.5358 | 2.2919 | 2.8517 | 0.8281 | 0.24426 | 3.3902 | 0.8558 | 0.37193 | 2.301 | 7.9468 | 2.1801 | 3.6452
[18 empty] | 02/26 09:00:00 | 5.4378 | 2.2621 | 2.4038 | 5.4101 | 1.591 | 3.4003 | 5.4024 | 1.4978 | 3.607 | 0.30778 | 0.16167 | 1.9038 | 0.28006 | 0.10106 | 2.7712 | 6.5101 | 1.7818 | 3.6535 | 6.5023 | 1.6845 | 3.86 | 6.5268 | 2.2193 | 2.9409 | 3.2101 | 0.94568 | 3.3945 | 6.5101 | 1.6105 | 4.0423 | 6.5378 | 2.2924 | 2.852 | 0.83006 | 0.24534 | 3.3834 | 0.85778 | 0.37335 | 2.2975 | 7.9487 | 2.1803 | 3.6457
[18 empty] | 02/26 10:00:00 | 5.4389 | 2.2622 | 2.4042 | 5.4115 | 1.5912 | 3.4009 | 5.4037 | 1.4979 | 3.6075 | 0.30891 | 0.16223 | 1.9042 | 0.28146 | 0.10155 | 2.7718 | 6.5115 | 1.782 | 3.654 | 6.5037 | 1.6847 | 3.8603 | 6.528 | 2.2195 | 2.9412 | 3.2115 | 0.94596 | 3.3949 | 6.5115 | 1.6106 | 4.043 | 6.5389 | 2.2923 | 2.8525 | 0.83146 | 0.24568 | 3.3843 | 0.85891 | 0.37354 | 2.2994 | 7.9501 | 2.1804 | 3.6461
[18 empty] | 02/26 11:00:00 | 5.4397 | 2.2623 | 2.4045 | 5.4122 | 1.5912 | 3.4012 | 5.4045 | 1.498 | 3.6079 | 0.30972 | 0.16263 | 1.9044 | 0.28219 | 0.1018 | 2.7721 | 6.5122 | 1.782 | 3.6544 | 6.5045 | 1.6848 | 3.8608 | 6.5288 | 2.2195 | 2.9416 | 3.2122 | 0.94603 | 3.3955 | 6.5122 | 1.6106 | 4.0434 | 6.5398 | 2.2924 | 2.8528 | 0.8322 | 0.24563 | 3.388 | 0.85973 | 0.37368 | 2.3007 | 7.9508 | 2.1804 | 3.6465
[18 empty] | 02/26 12:00:00 | 5.4401 | 2.2627 | 2.4042 | 5.4127 | 1.5915 | 3.4009 | 5.4049 | 1.4982 | 3.6075 | 0.31014 | 0.16287 | 1.9042 | 0.28265 | 0.10198 | 2.7717 | 6.5127 | 1.7822 | 3.6543 | 6.5049 | 1.6849 | 3.8607 | 6.5292 | 2.2197 | 2.9415 | 3.2127 | 0.94619 | 3.3954 | 6.5127 | 1.6108 | 4.043 | 6.5402 | 2.2927 | 2.8526 | 0.83266 | 0.24562 | 3.39 | 0.86015 | 0.37368 | 2.3018 | 7.9513 | 2.1805 | 3.6465
[18 empty] | 02/26 13:00:00 | 5.4402 | 2.2629 | 2.4041 | 5.4128 | 1.5917 | 3.4007 | 5.4051 | 1.4984 | 3.6073 | 0.31018 | 0.16291 | 1.904 | 0.28282 | 0.10205 | 2.7715 | 6.5128 | 1.7824 | 3.654 | 6.5051 | 1.6851 | 3.8604 | 6.5293 | 2.2199 | 2.9413 | 3.2128 | 0.94631 | 3.3951 | 6.5129 | 1.6109 | 4.0429 | 6.5402 | 2.2929 | 2.8524 | 0.83282 | 0.24553 | 3.392 | 0.86019 | 0.37349 | 2.3031 | 7.9514 | 2.1807 | 3.6462
[18 empty] | 02/26 14:00:00 | 5.4402 | 2.2632 | 2.4038 | 5.4129 | 1.5919 | 3.4003 | 5.4053 | 1.4986 | 3.6069 | 0.31022 | 0.16296 | 1.9037 | 0.28295 | 0.10211 | 2.7711 | 6.513 | 1.7825 | 3.6538 | 6.5053 | 1.6852 | 3.8602 | 6.5294 | 2.2201 | 2.941 | 3.213 | 0.94644 | 3.3948 | 6.513 | 1.6111 | 4.0425 | 6.5403 | 2.2932 | 2.852 | 0.83296 | 0.24554 | 3.3923 | 0.86023 | 0.37351 | 2.3031 | 7.9515 | 2.1809 | 3.646
[18 empty] | 02/26 15:00:00 | 5.4402 | 2.2636 | 2.4033 | 5.413 | 1.5922 | 3.3997 | 5.4053 | 1.4989 | 3.6062 | 0.31017 | 0.16297 | 1.9032 | 0.28298 | 0.10215 | 2.7704 | 6.513 | 1.7828 | 3.6533 | 6.5054 | 1.6854 | 3.8597 | 6.5294 | 2.2204 | 2.9406 | 3.213 | 0.94661 | 3.3942 | 6.513 | 1.6114 | 4.0419 | 6.5402 | 2.2936 | 2.8515 | 0.83299 | 0.24554 | 3.3924 | 0.86018 | 0.37351 | 2.303 | 7.9515 | 2.1812 | 3.6455
[18 empty] | 02/26 16:00:00 | 5.4398 | 2.2636 | 2.4031 | 5.4127 | 1.5922 | 3.3994 | 5.4051 | 1.4989 | 3.606 | 0.30983 | 0.16281 | 1.903 | 0.28267 | 0.10204 | 2.7701 | 6.5127 | 1.7829 | 3.6529 | 6.5051 | 1.6856 | 3.8593 | 6.529 | 2.2206 | 2.9403 | 3.2127 | 0.9466 | 3.3939 | 6.5127 | 1.6113 | 4.0418 | 6.5399 | 2.2936 | 2.8514 | 0.83268 | 0.24529 | 3.3946 | 0.85984 | 0.37321 | 2.3039 | 7.9512 | 2.1814 | 3.6451
[18 empty] | 02/26 17:00:00 | 5.4391 | 2.2631 | 2.4033 | 5.4118 | 1.5919 | 3.3997 | 5.4042 | 1.4985 | 3.6063 | 0.30911 | 0.16241 | 1.9032 | 0.2818 | 0.10172 | 2.7704 | 6.5119 | 1.7826 | 3.6529 | 6.5042 | 1.6853 | 3.8593 | 6.5283 | 2.2203 | 2.9403 | 3.2118 | 0.94627 | 3.3942 | 6.5119 | 1.6109 | 4.0424 | 6.5392 | 2.293 | 2.8518 | 0.83181 | 0.24469 | 3.3994 | 0.85911 | 0.37256 | 2.306 | 7.9504 | 2.1811 | 3.6451
[18 empty] | 02/26 18:00:00 | 5.4379 | 2.2626 | 2.4034 | 5.4103 | 1.5914 | 3.3997 | 5.4029 | 1.4981 | 3.6064 | 0.30786 | 0.16175 | 1.9033 | 0.2803 | 0.10117 | 2.7705 | 6.5104 | 1.7821 | 3.6531 | 6.5029 | 1.6849 | 3.8595 | 6.5269 | 2.2197 | 2.9405 | 3.2104 | 0.94571 | 3.3947 | 6.5104 | 1.6104 | 4.0427 | 6.5379 | 2.2923 | 2.8521 | 0.83031 | 0.24384 | 3.4052 | 0.85787 | 0.37156 | 2.3088 | 7.9489 | 2.1806 | 3.6453
[18 empty] | 02/26 19:00:00 | 5.4358 | 2.2619 | 2.4032 | 5.4084 | 1.5909 | 3.3995 | 5.401 | 1.4977 | 3.6061 | 0.30582 | 0.1607 | 1.9031 | 0.27839 | 0.10049 | 2.7702 | 6.5085 | 1.7817 | 3.653 | 6.5011 | 1.6845 | 3.8593 | 6.525 | 2.2191 | 2.9404 | 3.2084 | 0.94513 | 3.3947 | 6.5085 | 1.61 | 4.0426 | 6.5359 | 2.2916 | 2.8521 | 0.8284 | 0.24295 | 3.4097 | 0.85583 | 0.37012 | 2.3123 | 7.9471 | 2.1801 | 3.6452
[18 empty] | 02/26 20:00:00 | 5.4352 | 2.2614 | 2.4034 | 5.4078 | 1.5906 | 3.3998 | 5.4005 | 1.4974 | 3.6065 | 0.30516 | 0.16033 | 1.9033 | 0.27777 | 0.10026 | 2.7706 | 6.5078 | 1.7815 | 3.6531 | 6.5007 | 1.6844 | 3.8594 | 6.5243 | 2.2188 | 2.9405 | 3.2078 | 0.94496 | 3.3947 | 6.5079 | 1.6098 | 4.0427 | 6.5352 | 2.2913 | 2.8522 | 0.82779 | 0.24313 | 3.4047 | 0.85516 | 0.37029 | 2.3095 | 7.9465 | 2.1799 | 3.6453
[18 empty] | 02/26 21:00:00 | 5.4347 | 2.2611 | 2.4035 | 5.4073 | 1.5904 | 3.4 | 5.4002 | 1.4973 | 3.6067 | 0.30473 | 0.16009 | 1.9035 | 0.27734 | 0.10009 | 2.7708 | 6.5074 | 1.7812 | 3.6533 | 6.5004 | 1.6842 | 3.8596 | 6.5238 | 2.2185 | 2.9407 | 3.2074 | 0.94476 | 3.3949 | 6.5075 | 1.6096 | 4.0428 | 6.5348 | 2.2911 | 2.8523 | 0.82736 | 0.24317 | 3.4024 | 0.85474 | 0.3703 | 2.3082 | 7.946 | 2.1797 | 3.6456
[18 empty] | 02/26 22:00:00 | 5.4345 | 2.2608 | 2.4038 | 5.4071 | 1.5901 | 3.4004 | 5.4 | 1.497 | 3.6071 | 0.30452 | 0.15996 | 1.9037 | 0.27708 | 0.099986 | 2.7712 | 6.5071 | 1.7811 | 3.6535 | 6.5001 | 1.684 | 3.8598 | 6.5236 | 2.2183 | 2.9409 | 3.2071 | 0.94461 | 3.3952 | 6.5072 | 1.6094 | 4.0432 | 6.5346 | 2.2907 | 2.8526 | 0.8271 | 0.24318 | 3.4012 | 0.85453 | 0.37031 | 2.3076 | 7.9458 | 2.1795 | 3.6458
[18 empty] | 02/26 23:00:00 | 5.4344 | 2.2606 | 2.4039 | 5.4069 | 1.59 | 3.4006 | 5.3998 | 1.4969 | 3.6073 | 0.30441 | 0.15989 | 1.9039 | 0.27692 | 0.099919 | 2.7715 | 6.507 | 1.7809 | 3.6538 | 6.5 | 1.6839 | 3.8601 | 6.5235 | 2.218 | 2.9411 | 3.207 | 0.94447 | 3.3955 | 6.507 | 1.6093 | 4.0434 | 6.5345 | 2.2905 | 2.8528 | 0.82693 | 0.24318 | 3.4005 | 0.85441 | 0.37031 | 2.3073 | 7.9456 | 2.1792 | 3.6461
[18 empty] | 02/26 24:00:00 | 5.4343 | 2.2606 | 2.4039 | 5.4068 | 1.59 | 3.4006 | 5.3997 | 1.4969 | 3.6073 | 0.30427 | 0.15982 | 1.9039 | 0.27677 | 0.099864 | 2.7715 | 6.5068 | 1.7808 | 3.6539 | 6.4998 | 1.6838 | 3.8602 | 6.5233 | 2.2179 | 2.9412 | 3.2068 | 0.94441 | 3.3956 | 6.5069 | 1.6093 | 4.0434 | 6.5343 | 2.2905 | 2.8528 | 0.82678 | 0.24316 | 3.4002 | 0.85428 | 0.37026 | 2.3073 | 7.9455 | 2.1792 | 3.6461
[18 empty] | 02/27 01:00:00 | 5.4341 | 2.2608 | 2.4036 | 5.4066 | 1.5901 | 3.4002 | 5.3995 | 1.497 | 3.6069 | 0.30414 | 0.15977 | 1.9036 | 0.27662 | 0.099827 | 2.771 | 6.5067 | 1.7809 | 3.6537 | 6.4995 | 1.6838 | 3.8602 | 6.5232 | 2.218 | 2.941 | 3.2067 | 0.94444 | 3.3953 | 6.5067 | 1.6094 | 4.0429 | 6.5342 | 2.2907 | 2.8524 | 0.82663 | 0.24316 | 3.3995 | 0.85414 | 0.37026 | 2.3069 | 7.9453 | 2.1792 | 3.6459
[18 empty] | 02/27 02:00:00 | 5.4341 | 2.2609 | 2.4035 | 5.4066 | 1.5902 | 3.3999 | 5.3993 | 1.4971 | 3.6066 | 0.30411 | 0.15977 | 1.9034 | 0.27656 | 0.099816 | 2.7707 | 6.5066 | 1.781 | 3.6533 | 6.4994 | 1.6839 | 3.8598 | 6.5232 | 2.2182 | 2.9407 | 3.2066 | 0.94452 | 3.3949 | 6.5067 | 1.6095 | 4.0427 | 6.5342 | 2.2909 | 2.8522 | 0.82657 | 0.2432 | 3.3988 | 0.85412 | 0.37033 | 2.3064 | 7.9453 | 2.1794 | 3.6456
[18 empty] | 02/27 03:00:00 | 5.4343 | 2.261 | 2.4035 | 5.4067 | 1.5902 | 3.3999 | 5.3993 | 1.4971 | 3.6066 | 0.30432 | 0.15988 | 1.9034 | 0.27666 | 0.099851 | 2.7707 | 6.5067 | 1.7811 | 3.6533 | 6.4994 | 1.6839 | 3.8597 | 6.5233 | 2.2183 | 2.9407 | 3.2067 | 0.94458 | 3.3948 | 6.5067 | 1.6095 | 4.0426 | 6.5344 | 2.2911 | 2.8521 | 0.82667 | 0.24331 | 3.3976 | 0.85432 | 0.37059 | 2.3053 | 7.9454 | 2.1795 | 3.6455
[18 empty] | 02/27 04:00:00 | 5.435 | 2.2615 | 2.4033 | 5.4071 | 1.5905 | 3.3996 | 5.3995 | 1.4973 | 3.6062 | 0.30499 | 0.16025 | 1.9032 | 0.27711 | 0.10003 | 2.7703 | 6.5071 | 1.7813 | 3.6531 | 6.4996 | 1.684 | 3.8595 | 6.524 | 2.2186 | 2.9405 | 3.2071 | 0.9448 | 3.3945 | 6.5072 | 1.6098 | 4.0422 | 6.535 | 2.2916 | 2.8518 | 0.82712 | 0.24366 | 3.3946 | 0.855 | 0.37124 | 2.3031 | 7.9459 | 2.1797 | 3.6454
[18 empty] | 02/27 05:00:00 | 5.4353 | 2.2617 | 2.4031 | 5.4074 | 1.5907 | 3.3994 | 5.3997 | 1.4974 | 3.606 | 0.30531 | 0.16043 | 1.903 | 0.27738 | 0.10013 | 2.7701 | 6.5074 | 1.7815 | 3.6528 | 6.4998 | 1.6842 | 3.8592 | 6.5243 | 2.2189 | 2.9403 | 3.2074 | 0.94496 | 3.3942 | 6.5074 | 1.6099 | 4.042 | 6.5354 | 2.2918 | 2.8516 | 0.82739 | 0.24374 | 3.3946 | 0.85531 | 0.37131 | 2.3035 | 7.9461 | 2.1799 | 3.6451
[18 empty] | 02/27 06:00:00 | 5.4353 | 2.2615 | 2.4034 | 5.4075 | 1.5905 | 3.3998 | 5.3998 | 1.4973 | 3.6064 | 0.30534 | 0.16042 | 1.9033 | 0.27747 | 0.10015 | 2.7706 | 6.5075 | 1.7814 | 3.653 | 6.4998 | 1.6842 | 3.8592 | 6.5243 | 2.2188 | 2.9404 | 3.2075 | 0.94491 | 3.3945 | 6.5075 | 1.6098 | 4.0425 | 6.5354 | 2.2915 | 2.8521 | 0.82748 | 0.24365 | 3.3962 | 0.85534 | 0.37109 | 2.305 | 7.9462 | 2.1799 | 3.6453
[18 empty] | 02/27 07:00:00 | 5.4352 | 2.261 | 2.4039 | 5.4074 | 1.5902 | 3.4004 | 5.3998 | 1.497 | 3.6071 | 0.30523 | 0.16032 | 1.9038 | 0.27745 | 0.10012 | 2.7713 | 6.5075 | 1.7812 | 3.6535 | 6.4998 | 1.684 | 3.8597 | 6.5242 | 2.2185 | 2.9409 | 3.2075 | 0.94474 | 3.3951 | 6.5075 | 1.6095 | 4.0431 | 6.5353 | 2.291 | 2.8526 | 0.82745 | 0.24353 | 3.3978 | 0.85523 | 0.37084 | 2.3062 | 7.9462 | 2.1796 | 3.6457
[18 empty] | 02/27 08:00:00 | 5.436 | 2.2611 | 2.4041 | 5.4081 | 1.5903 | 3.4007 | 5.4004 | 1.497 | 3.6074 | 0.306 | 0.16071 | 1.9041 | 0.27811 | 0.10034 | 2.7716 | 6.5081 | 1.7811 | 3.6539 | 6.5004 | 1.6839 | 3.8602 | 6.525 | 2.2185 | 2.9412 | 3.2081 | 0.94487 | 3.3953 | 6.5082 | 1.6097 | 4.043 | 6.536 | 2.2913 | 2.8526 | 0.82812 | 0.24402 | 3.3937 | 0.856 | 0.37165 | 2.3032 | 7.9469 | 2.1795 | 3.6461
[18 empty] | 02/27 09:00:00 | 5.4376 | 2.2614 | 2.4045 | 5.4099 | 1.5905 | 3.4014 | 5.4022 | 1.4973 | 3.608 | 0.30765 | 0.16153 | 1.9045 | 0.27992 | 0.10097 | 2.7723 | 6.5099 | 1.7814 | 3.6544 | 6.5021 | 1.6841 | 3.8608 | 6.5266 | 2.2187 | 2.9416 | 3.2099 | 0.94536 | 3.3955 | 6.5099 | 1.61 | 4.0434 | 6.5377 | 2.2916 | 2.8529 | 0.82992 | 0.2451 | 3.3861 | 0.85766 | 0.37292 | 2.2999 | 7.9485 | 2.1798 | 3.6465
[18 empty] | 02/27 10:00:00 | 5.4394 | 2.2618 | 2.4049 | 5.4116 | 1.5908 | 3.4018 | 5.4038 | 1.4975 | 3.6085 | 0.30936 | 0.1624 | 1.9049 | 0.28155 | 0.10154 | 2.7727 | 6.5116 | 1.7816 | 3.6549 | 6.5037 | 1.6844 | 3.8613 | 6.5283 | 2.219 | 2.942 | 3.2116 | 0.94572 | 3.3959 | 6.5116 | 1.6103 | 4.0437 | 6.5394 | 2.2919 | 2.8532 | 0.83156 | 0.24572 | 3.3842 | 0.85937 | 0.37387 | 2.2986 | 7.9502 | 2.1799 | 3.647
[18 empty] | 02/27 11:00:00 | 5.4402 | 2.2621 | 2.4049 | 5.4126 | 1.591 | 3.4019 | 5.4047 | 1.4977 | 3.6086 | 0.31023 | 0.16285 | 1.905 | 0.28256 | 0.1019 | 2.7729 | 6.5126 | 1.7818 | 3.655 | 6.5047 | 1.6845 | 3.8614 | 6.5293 | 2.2192 | 2.9421 | 3.2126 | 0.94595 | 3.3961 | 6.5126 | 1.6104 | 4.044 | 6.5403 | 2.2921 | 2.8534 | 0.83257 | 0.24582 | 3.3869 | 0.86024 | 0.37391 | 2.3006 | 7.9512 | 2.1801 | 3.6472
[18 empty] | 02/27 12:00:00 | 5.4408 | 2.2625 | 2.4047 | 5.4131 | 1.5913 | 3.4016 | 5.4052 | 1.498 | 3.6082 | 0.31076 | 0.16315 | 1.9047 | 0.28307 | 0.1021 | 2.7725 | 6.5131 | 1.782 | 3.6549 | 6.5052 | 1.6847 | 3.8613 | 6.5298 | 2.2195 | 2.942 | 3.2131 | 0.94613 | 3.396 | 6.5131 | 1.6107 | 4.0436 | 6.5408 | 2.2925 | 2.8531 | 0.83307 | 0.24577 | 3.3896 | 0.86077 | 0.37398 | 2.3016 | 7.9517 | 2.1803 | 3.6471
[18 empty] | 02/27 13:00:00 | 5.4411 | 2.2628 | 2.4046 | 5.4135 | 1.5915 | 3.4014 | 5.4057 | 1.4982 | 3.608 | 0.31114 | 0.16337 | 1.9046 | 0.28346 | 0.10225 | 2.7723 | 6.5135 | 1.7823 | 3.6546 | 6.5056 | 1.6849 | 3.8611 | 6.5302 | 2.2198 | 2.9418 | 3.2135 | 0.94633 | 3.3957 | 6.5135 | 1.6109 | 4.0435 | 6.5412 | 2.2928 | 2.8529 | 0.83347 | 0.2458 | 3.3908 | 0.86115 | 0.37406 | 2.3022 | 7.9521 | 2.1806 | 3.6468
[18 empty] | 02/27 14:00:00 | 5.4414 | 2.2631 | 2.4043 | 5.4137 | 1.5918 | 3.401 | 5.406 | 1.4985 | 3.6076 | 0.31137 | 0.16351 | 1.9043 | 0.28375 | 0.10237 | 2.7719 | 6.5138 | 1.7824 | 3.6544 | 6.506 | 1.6851 | 3.8609 | 6.5304 | 2.22 | 2.9416 | 3.2138 | 0.94649 | 3.3955 | 6.5138 | 1.6111 | 4.0431 | 6.5414 | 2.2931 | 2.8526 | 0.83375 | 0.24585 | 3.3913 | 0.86137 | 0.37411 | 2.3025 | 7.9524 | 2.1808 | 3.6466
[18 empty] | 02/27 15:00:00 | 5.441 | 2.2634 | 2.4039 | 5.4136 | 1.5921 | 3.4004 | 5.4059 | 1.4987 | 3.607 | 0.311 | 0.16336 | 1.9038 | 0.2836 | 0.10234 | 2.7711 | 6.5136 | 1.7826 | 3.6539 | 6.5059 | 1.6853 | 3.8604 | 6.5301 | 2.2202 | 2.9412 | 3.2136 | 0.94659 | 3.395 | 6.5137 | 1.6112 | 4.0427 | 6.5411 | 2.2933 | 2.8522 | 0.83361 | 0.24565 | 3.3935 | 0.861 | 0.37367 | 2.3042 | 7.9522 | 2.181 | 3.6461
[18 empty] | 02/27 16:00:00 | 5.4401 | 2.2633 | 2.4036 | 5.4128 | 1.592 | 3.4 | 5.4052 | 1.4987 | 3.6066 | 0.31005 | 0.16289 | 1.9035 | 0.28282 | 0.10207 | 2.7708 | 6.5129 | 1.7827 | 3.6535 | 6.5053 | 1.6854 | 3.8599 | 6.5292 | 2.2202 | 2.9408 | 3.2129 | 0.94644 | 3.3947 | 6.5129 | 1.6111 | 4.0426 | 6.5401 | 2.2932 | 2.852 | 0.83283 | 0.24511 | 3.3978 | 0.86006 | 0.37292 | 2.3063 | 7.9515 | 2.1811 | 3.6457
[18 empty] | 02/27 17:00:00 | 5.4396 | 2.2631 | 2.4036 | 5.4119 | 1.5918 | 3.3999 | 5.4044 | 1.4985 | 3.6065 | 0.30958 | 0.16264 | 1.9034 | 0.28193 | 0.10176 | 2.7707 | 6.512 | 1.7825 | 3.6533 | 6.5046 | 1.6852 | 3.8598 | 6.5287 | 2.2201 | 2.9407 | 3.212 | 0.94619 | 3.3946 | 6.512 | 1.6109 | 4.0425 | 6.5396 | 2.2931 | 2.8519 | 0.83194 | 0.24467 | 3.4003 | 0.85959 | 0.37282 | 2.3056 | 7.9506 | 2.1809 | 3.6455
[18 empty] | 02/27 18:00:00 | 5.4394 | 2.2631 | 2.4035 | 5.4116 | 1.5917 | 3.3999 | 5.4041 | 1.4984 | 3.6065 | 0.30945 | 0.16257 | 1.9034 | 0.28158 | 0.10163 | 2.7706 | 6.5116 | 1.7824 | 3.6533 | 6.5042 | 1.6852 | 3.8597 | 6.5284 | 2.2201 | 2.9406 | 3.2116 | 0.94613 | 3.3945 | 6.5117 | 1.6109 | 4.0423 | 6.5395 | 2.2931 | 2.8518 | 0.83159 | 0.24472 | 3.3981 | 0.85946 | 0.37296 | 2.3045 | 7.9504 | 2.1809 | 3.6455
[18 empty] | 02/27 19:00:00 | 5.4392 | 2.2628 | 2.4038 | 5.4113 | 1.5914 | 3.4003 | 5.4038 | 1.4982 | 3.6069 | 0.30923 | 0.16243 | 1.9037 | 0.28126 | 0.1015 | 2.771 | 6.5113 | 1.7823 | 3.6534 | 6.5039 | 1.685 | 3.8598 | 6.5282 | 2.2199 | 2.9408 | 3.2113 | 0.94597 | 3.3947 | 6.5114 | 1.6106 | 4.0428 | 6.5393 | 2.2927 | 2.8522 | 0.83128 | 0.24464 | 3.398 | 0.85923 | 0.37279 | 2.3049 | 7.9501 | 2.1807 | 3.6456
[18 empty] | 02/27 20:00:00 | 5.4389 | 2.2625 | 2.4039 | 5.4109 | 1.5912 | 3.4004 | 5.4035 | 1.498 | 3.6071 | 0.30889 | 0.16224 | 1.9039 | 0.28092 | 0.10137 | 2.7713 | 6.511 | 1.782 | 3.6537 | 6.5035 | 1.6848 | 3.8601 | 6.5278 | 2.2196 | 2.941 | 3.211 | 0.94578 | 3.395 | 6.511 | 1.6104 | 4.043 | 6.539 | 2.2924 | 2.8525 | 0.83093 | 0.24451 | 3.3983 | 0.8589 | 0.37252 | 2.3056 | 7.9498 | 2.1805 | 3.6459
[18 empty] | 02/27 21:00:00 | 5.4384 | 2.2623 | 2.4039 | 5.4105 | 1.5911 | 3.4004 | 5.4031 | 1.4979 | 3.6071 | 0.30844 | 0.16201 | 1.9038 | 0.28053 | 0.10123 | 2.7712 | 6.5106 | 1.7819 | 3.6537 | 6.5032 | 1.6847 | 3.8601 | 6.5274 | 2.2194 | 2.941 | 3.2106 | 0.94565 | 3.3951 | 6.5106 | 1.6104 | 4.043 | 6.5385 | 2.2922 | 2.8524 | 0.83054 | 0.24437 | 3.3987 | 0.85844 | 0.37223 | 2.3062 | 7.9494 | 2.1803 | 3.6459
[18 empty] | 02/27 22:00:00 | 5.4377 | 2.2618 | 2.4041 | 5.4099 | 1.5908 | 3.4007 | 5.4024 | 1.4976 | 3.6074 | 0.30768 | 0.16159 | 1.9041 | 0.27991 | 0.10099 | 2.7716 | 6.51 | 1.7817 | 3.6539 | 6.5025 | 1.6845 | 3.8602 | 6.5267 | 2.2191 | 2.9412 | 3.21 | 0.94537 | 3.3954 | 6.51 | 1.61 | 4.0436 | 6.5377 | 2.2916 | 2.853 | 0.82992 | 0.244 | 3.4013 | 0.85769 | 0.37158 | 2.3082 | 7.9487 | 2.1801 | 3.6461
[18 empty] | 02/27 23:00:00 | 5.4367 | 2.2614 | 2.4042 | 5.409 | 1.5905 | 3.4009 | 5.4015 | 1.4973 | 3.6075 | 0.30668 | 0.16106 | 1.9041 | 0.27905 | 0.10068 | 2.7717 | 6.5091 | 1.7813 | 3.6541 | 6.5016 | 1.6842 | 3.8604 | 6.5257 | 2.2186 | 2.9413 | 3.2091 | 0.94504 | 3.3957 | 6.5092 | 1.6098 | 4.0435 | 6.5367 | 2.2912 | 2.853 | 0.82906 | 0.24361 | 3.4032 | 0.85669 | 0.37097 | 2.3093 | 7.9478 | 2.1797 | 3.6463
[18 empty] | 02/27 24:00:00 | 5.4367 | 2.2616 | 2.4039 | 5.409 | 1.5907 | 3.4004 | 5.4014 | 1.4974 | 3.6071 | 0.3067 | 0.16109 | 1.9038 | 0.27895 | 0.10066 | 2.7713 | 6.509 | 1.7814 | 3.6539 | 6.5015 | 1.6842 | 3.8603 | 6.5257 | 2.2187 | 2.9412 | 3.209 | 0.94511 | 3.3954 | 6.509 | 1.6099 | 4.043 | 6.5368 | 2.2916 | 2.8525 | 0.82896 | 0.24386 | 3.3993 | 0.85671 | 0.37147 | 2.3063 | 7.9477 | 2.1798 | 3.6462
[18 empty] | 02/28 01:00:00 | 5.4365 | 2.2617 | 2.4037 | 5.4087 | 1.5907 | 3.4002 | 5.4013 | 1.4975 | 3.6068 | 0.30646 | 0.16099 | 1.9036 | 0.27874 | 0.10059 | 2.771 | 6.5088 | 1.7815 | 3.6536 | 6.5014 | 1.6843 | 3.86 | 6.5255 | 2.2189 | 2.9409 | 3.2088 | 0.94513 | 3.3951 | 6.5088 | 1.61 | 4.0429 | 6.5365 | 2.2916 | 2.8524 | 0.82875 | 0.24384 | 3.3988 | 0.85647 | 0.37136 | 2.3063 | 7.9475 | 2.1799 | 3.6458
[18 empty] | 02/28 02:00:00 | 5.436 | 2.2616 | 2.4037 | 5.4084 | 1.5906 | 3.4001 | 5.401 | 1.4974 | 3.6068 | 0.30601 | 0.16076 | 1.9036 | 0.27838 | 0.10046 | 2.7709 | 6.5084 | 1.7814 | 3.6535 | 6.5011 | 1.6843 | 3.8599 | 6.5251 | 2.2188 | 2.9408 | 3.2084 | 0.94504 | 3.395 | 6.5085 | 1.6099 | 4.0429 | 6.5361 | 2.2915 | 2.8524 | 0.82839 | 0.24367 | 3.3996 | 0.85602 | 0.37104 | 2.3071 | 7.9471 | 2.1798 | 3.6457
[18 empty] | 02/28 03:00:00 | 5.4357 | 2.2617 | 2.4033 | 5.4081 | 1.5907 | 3.3997 | 5.4007 | 1.4976 | 3.6064 | 0.30566 | 0.1606 | 1.9032 | 0.27807 | 0.10037 | 2.7705 | 6.5081 | 1.7815 | 3.6533 | 6.5008 | 1.6843 | 3.8597 | 6.5247 | 2.2188 | 2.9406 | 3.2081 | 0.94503 | 3.3947 | 6.5082 | 1.61 | 4.0424 | 6.5357 | 2.2916 | 2.852 | 0.82808 | 0.24361 | 3.3992 | 0.85566 | 0.37094 | 2.3067 | 7.9468 | 2.1799 | 3.6455
[18 empty] | 02/28 04:00:00 | 5.4352 | 2.2617 | 2.4031 | 5.4077 | 1.5908 | 3.3994 | 5.4005 | 1.4976 | 3.6061 | 0.30518 | 0.16037 | 1.903 | 0.27769 | 0.10024 | 2.7702 | 6.5077 | 1.7815 | 3.6529 | 6.5006 | 1.6844 | 3.8593 | 6.5243 | 2.2189 | 2.9403 | 3.2077 | 0.945 | 3.3944 | 6.5078 | 1.61 | 4.0422 | 6.5352 | 2.2916 | 2.8518 | 0.8277 | 0.24347 | 3.3996 | 0.85519 | 0.37069 | 2.307 | 7.9464 | 2.18 | 3.6452
[18 empty] | 02/28 05:00:00 | 5.4348 | 2.2616 | 2.4031 | 5.4073 | 1.5907 | 3.3994 | 5.4002 | 1.4975 | 3.606 | 0.30478 | 0.16016 | 1.903 | 0.27732 | 0.10011 | 2.7701 | 6.5074 | 1.7815 | 3.6528 | 6.5003 | 1.6844 | 3.8591 | 6.5239 | 2.2188 | 2.9402 | 3.2074 | 0.94492 | 3.3943 | 6.5074 | 1.6099 | 4.0421 | 6.5348 | 2.2915 | 2.8517 | 0.82733 | 0.24335 | 3.3998 | 0.85479 | 0.37053 | 2.3069 | 7.946 | 2.1799 | 3.6451
[18 empty] | 02/28 06:00:00 | 5.4347 | 2.2613 | 2.4034 | 5.4072 | 1.5905 | 3.3998 | 5.4 | 1.4973 | 3.6064 | 0.30474 | 0.16011 | 1.9033 | 0.27722 | 0.10006 | 2.7705 | 6.5073 | 1.7814 | 3.653 | 6.5001 | 1.6843 | 3.8593 | 6.5238 | 2.2187 | 2.9404 | 3.2073 | 0.94483 | 3.3945 | 6.5073 | 1.6097 | 4.0425 | 6.5348 | 2.2913 | 2.852 | 0.82723 | 0.24338 | 3.3989 | 0.85475 | 0.37063 | 2.3062 | 7.9459 | 2.1798 | 3.6452
[18 empty] | 02/28 07:00:00 | 5.4348 | 2.2612 | 2.4035 | 5.4072 | 1.5904 | 3.4 | 5.4 | 1.4972 | 3.6067 | 0.3048 | 0.16013 | 1.9035 | 0.2772 | 0.10004 | 2.7708 | 6.5072 | 1.7812 | 3.6533 | 6.5001 | 1.6841 | 3.8596 | 6.5238 | 2.2185 | 2.9407 | 3.2072 | 0.94475 | 3.3948 | 6.5073 | 1.6097 | 4.0427 | 6.5349 | 2.2912 | 2.8522 | 0.82721 | 0.24343 | 3.3982 | 0.8548 | 0.37074 | 2.3057 | 7.9459 | 2.1796 | 3.6455
[18 empty] | 02/28 08:00:00 | 5.4357 | 2.2615 | 2.4036 | 5.408 | 1.5905 | 3.4001 | 5.4003 | 1.4973 | 3.6067 | 0.30569 | 0.16059 | 1.9036 | 0.27798 | 0.10032 | 2.7709 | 6.508 | 1.7814 | 3.6534 | 6.5003 | 1.6841 | 3.8597 | 6.5247 | 2.2187 | 2.9408 | 3.208 | 0.945 | 3.3947 | 6.508 | 1.6099 | 4.0424 | 6.5357 | 2.2916 | 2.8521 | 0.82799 | 0.24404 | 3.3928 | 0.8557 | 0.37162 | 2.3026 | 7.9466 | 2.1798 | 3.6456
[18 empty] | 02/28 09:00:00 | 5.4368 | 2.2616 | 2.404 | 5.4093 | 1.5907 | 3.4007 | 5.4015 | 1.4974 | 3.6073 | 0.30681 | 0.16114 | 1.904 | 0.27934 | 0.10079 | 2.7715 | 6.5094 | 1.7816 | 3.6537 | 6.5015 | 1.6843 | 3.8601 | 6.5259 | 2.2189 | 2.941 | 3.2094 | 0.94535 | 3.3949 | 6.5094 | 1.6101 | 4.0428 | 6.5369 | 2.2917 | 2.8524 | 0.82935 | 0.24479 | 3.388 | 0.85682 | 0.37236 | 2.3011 | 7.9479 | 2.1799 | 3.6459
[18 empty] | 02/28 10:00:00 | 5.4384 | 2.2619 | 2.4043 | 5.4107 | 1.5909 | 3.4011 | 5.403 | 1.4976 | 3.6077 | 0.30842 | 0.16196 | 1.9043 | 0.28075 | 0.10128 | 2.7719 | 6.5108 | 1.7817 | 3.6542 | 6.503 | 1.6844 | 3.8606 | 6.5275 | 2.2191 | 2.9414 | 3.2108 | 0.94566 | 3.3952 | 6.5108 | 1.6104 | 4.043 | 6.5385 | 2.2922 | 2.8525 | 0.83075 | 0.24537 | 3.3858 | 0.85843 | 0.37343 | 2.2988 | 7.9494 | 2.1801 | 3.6464
[18 empty] | 02/28 11:00:00 | 5.4396 | 2.2623 | 2.4044 | 5.4119 | 1.5912 | 3.4012 | 5.4043 | 1.4979 | 3.6079 | 0.3096 | 0.16257 | 1.9044 | 0.28186 | 0.10168 | 2.7721 | 6.512 | 1.782 | 3.6544 | 6.5042 | 1.6847 | 3.8608 | 6.5286 | 2.2194 | 2.9416 | 3.212 | 0.94598 | 3.3954 | 6.512 | 1.6106 | 4.0433 | 6.5396 | 2.2924 | 2.8528 | 0.83199 | 0.24573 | 3.3859 | 0.85961 | 0.37381 | 2.2996 | 7.9505 | 2.1803 | 3.6466
[18 empty] | 02/28 12:00:00 | 5.4402 | 2.2625 | 2.4045 | 5.4125 | 1.5913 | 3.4013 | 5.4048 | 1.498 | 3.6079 | 0.31017 | 0.16286 | 1.9045 | 0.28247 | 0.1019 | 2.7722 | 6.5126 | 1.7821 | 3.6545 | 6.5048 | 1.6848 | 3.8609 | 6.5292 | 2.2196 | 2.9417 | 3.2126 | 0.9461 | 3.3956 | 6.5126 | 1.6107 | 4.0434 | 6.5402 | 2.2925 | 2.8529 | 0.83255 | 0.24565 | 3.3892 | 0.86017 | 0.37377 | 2.3014 | 7.9511 | 2.1804 | 3.6466
[18 empty] | 02/28 13:00:00 | 5.4405 | 2.2628 | 2.4043 | 5.4128 | 1.5916 | 3.4009 | 5.4051 | 1.4983 | 3.6075 | 0.31046 | 0.16304 | 1.9042 | 0.28283 | 0.10204 | 2.7718 | 6.5129 | 1.7822 | 3.6543 | 6.5051 | 1.6849 | 3.8608 | 6.5295 | 2.2198 | 2.9415 | 3.2129 | 0.94625 | 3.3954 | 6.5129 | 1.6109 | 4.0431 | 6.5405 | 2.2928 | 2.8526 | 0.83288 | 0.24562 | 3.3909 | 0.86047 | 0.37375 | 2.3022 | 7.9515 | 2.1806 | 3.6465
[18 empty] | 02/28 14:00:00 | 5.4407 | 2.2633 | 2.4038 | 5.4131 | 1.5919 | 3.4003 | 5.4054 | 1.4986 | 3.6069 | 0.3107 | 0.16321 | 1.9037 | 0.28311 | 0.10217 | 2.7711 | 6.5132 | 1.7826 | 3.6538 | 6.5054 | 1.6852 | 3.8603 | 6.5298 | 2.2202 | 2.9411 | 3.2132 | 0.94648 | 3.3948 | 6.5132 | 1.6112 | 4.0425 | 6.5408 | 2.2934 | 2.852 | 0.83314 | 0.24568 | 3.3911 | 0.86071 | 0.37389 | 2.302 | 7.9518 | 2.1809 | 3.646
[18 empty] | 02/28 15:00:00 | 5.4408 | 2.2638 | 2.4034 | 5.4132 | 1.5923 | 3.3997 | 5.4056 | 1.4989 | 3.6063 | 0.31079 | 0.1633 | 1.9033 | 0.28325 | 0.10224 | 2.7704 | 6.5133 | 1.7829 | 3.6533 | 6.5056 | 1.6855 | 3.8598 | 6.5299 | 2.2206 | 2.9406 | 3.2133 | 0.94669 | 3.3942 | 6.5133 | 1.6114 | 4.0419 | 6.5408 | 2.2938 | 2.8515 | 0.83327 | 0.2457 | 3.3914 | 0.8608 | 0.37392 | 2.3021 | 7.9519 | 2.1813 | 3.6455
[18 empty] | 02/28 16:00:00 | 5.4404 | 2.2638 | 2.4032 | 5.413 | 1.5923 | 3.3994 | 5.4054 | 1.499 | 3.606 | 0.31044 | 0.16313 | 1.903 | 0.283 | 0.10216 | 2.7701 | 6.513 | 1.783 | 3.6529 | 6.5054 | 1.6856 | 3.8593 | 6.5296 | 2.2207 | 2.9403 | 3.213 | 0.94671 | 3.3939 | 6.5131 | 1.6114 | 4.0418 | 6.5405 | 2.2938 | 2.8514 | 0.83302 | 0.24545 | 3.3938 | 0.86045 | 0.37353 | 2.3035 | 7.9516 | 2.1814 | 3.6451
[18 empty] | 02/28 17:00:00 | 5.4395 | 2.2633 | 2.4034 | 5.4121 | 1.5919 | 3.3997 | 5.4044 | 1.4986 | 3.6063 | 0.30945 | 0.16259 | 1.9033 | 0.28205 | 0.10181 | 2.7704 | 6.5121 | 1.7827 | 3.653 | 6.5045 | 1.6854 | 3.8593 | 6.5286 | 2.2203 | 2.9404 | 3.2121 | 0.94633 | 3.3943 | 6.5121 | 1.6109 | 4.0425 | 6.5395 | 2.293 | 2.8519 | 0.83206 | 0.24474 | 3.3997 | 0.85946 | 0.37257 | 2.3068 | 7.9507 | 2.1812 | 3.6452
[18 empty] | 02/28 18:00:00 | 5.4378 | 2.2626 | 2.4034 | 5.4103 | 1.5914 | 3.3997 | 5.4029 | 1.4982 | 3.6064 | 0.30784 | 0.16174 | 1.9033 | 0.28034 | 0.10119 | 2.7705 | 6.5104 | 1.7821 | 3.6531 | 6.503 | 1.6849 | 3.8595 | 6.5269 | 2.2197 | 2.9405 | 3.2104 | 0.94571 | 3.3947 | 6.5105 | 1.6104 | 4.0427 | 6.5379 | 2.2923 | 2.8521 | 0.83036 | 0.24377 | 3.4063 | 0.85785 | 0.37136 | 2.31 | 7.949 | 2.1806 | 3.6453
[18 empty] | 02/28 19:00:00 | 5.4364 | 2.2618 | 2.4035 | 5.409 | 1.5909 | 3.4 | 5.4015 | 1.4977 | 3.6066 | 0.30639 | 0.16097 | 1.9034 | 0.27899 | 0.10069 | 2.7708 | 6.5091 | 1.7817 | 3.6532 | 6.5016 | 1.6846 | 3.8595 | 6.5255 | 2.2191 | 2.9406 | 3.209 | 0.94526 | 3.3949 | 6.5091 | 1.61 | 4.0429 | 6.5365 | 2.2916 | 2.8523 | 0.829 | 0.24332 | 3.407 | 0.8564 | 0.37059 | 2.3109 | 7.9477 | 2.1802 | 3.6454
[18 empty] | 02/28 20:00:00 | 5.4358 | 2.2615 | 2.4036 | 5.4084 | 1.5906 | 3.4001 | 5.401 | 1.4974 | 3.6068 | 0.30583 | 0.16066 | 1.9036 | 0.2784 | 0.10047 | 2.7709 | 6.5085 | 1.7815 | 3.6534 | 6.5011 | 1.6843 | 3.8598 | 6.5249 | 2.2188 | 2.9408 | 3.2085 | 0.94504 | 3.395 | 6.5085 | 1.6098 | 4.0429 | 6.5359 | 2.2914 | 2.8524 | 0.82842 | 0.24339 | 3.4036 | 0.85584 | 0.37069 | 2.3088 | 7.9471 | 2.1799 | 3.6457
[18 empty] | 02/28 21:00:00 | 5.4352 | 2.2613 | 2.4036 | 5.4078 | 1.5905 | 3.4001 | 5.4005 | 1.4973 | 3.6068 | 0.30516 | 0.16031 | 1.9035 | 0.27779 | 0.10025 | 2.7709 | 6.5079 | 1.7813 | 3.6534 | 6.5006 | 1.6842 | 3.8598 | 6.5243 | 2.2186 | 2.9408 | 3.2078 | 0.94486 | 3.3951 | 6.5079 | 1.6097 | 4.0429 | 6.5352 | 2.2911 | 2.8524 | 0.8278 | 0.24327 | 3.4029 | 0.85516 | 0.37041 | 2.3087 | 7.9465 | 2.1797 | 3.6457
[18 empty] | 02/28 22:00:00 | 5.4348 | 2.2614 | 2.4033 | 5.4074 | 1.5906 | 3.3996 | 5.4002 | 1.4974 | 3.6063 | 0.30475 | 0.16013 | 1.9032 | 0.27737 | 0.10012 | 2.7704 | 6.5074 | 1.7813 | 3.6532 | 6.5003 | 1.6842 | 3.8596 | 6.5239 | 2.2186 | 2.9406 | 3.2074 | 0.94482 | 3.3947 | 6.5075 | 1.6098 | 4.0424 | 6.5348 | 2.2914 | 2.8519 | 0.82738 | 0.24327 | 3.4011 | 0.85476 | 0.37043 | 2.3075 | 7.9461 | 2.1797 | 3.6455
[18 empty] | 02/28 23:00:00 | 5.4346 | 2.2615 | 2.4031 | 5.4071 | 1.5906 | 3.3994 | 5.4 | 1.4975 | 3.606 | 0.30457 | 0.16005 | 1.903 | 0.27713 | 0.10004 | 2.7701 | 6.5072 | 1.7814 | 3.6528 | 6.5001 | 1.6843 | 3.8592 | 6.5237 | 2.2187 | 2.9403 | 3.2072 | 0.94486 | 3.3943 | 6.5072 | 1.6099 | 4.0421 | 6.5346 | 2.2915 | 2.8517 | 0.82714 | 0.24331 | 3.3996 | 0.85458 | 0.37052 | 2.3064 | 7.9458 | 2.1799 | 3.6451
[12 empty] | Analytical | E+ vs Anal |  |  |  |  | 02/28 24:00:00 | 5.4346 | 2.2615 | 2.4031 | 5.4071 | 1.5906 | 3.3993 | 5.3999 | 1.4975 | 3.606 | 0.30461 | 0.16007 | 1.903 | 0.27707 | 0.10002 | 2.7701 | 6.5071 | 1.7814 | 3.6528 | 6.5 | 1.6843 | 3.8591 | 6.5237 | 2.2188 | 2.9402 | 3.2071 | 0.94487 | 3.3942 | 6.5072 | 1.6099 | 4.0421 | 6.5347 | 2.2916 | 2.8516 | 0.82708 | 0.24339 | 3.3981 | 0.85462 | 0.37071 | 2.3054 | 7.9458 | 2.1799 | 3.645
[12 empty] | Average | Diff (%)
[12 empty] | 2.3896 | 0.5625% |  |  |  |  | Min |  |  | 2.3974 |  |  | 3.3935 |  |  | 3.5998 |  |  | 1.897 |  |  | 2.7637 |  |  | 3.6428 |  |  | 3.8476 |  |  | 2.9309 |  |  | 3.3792 |  |  | 4.0206 |  |  | 2.8341 |  |  | 3.3365 |  |  | 2.2341 |  |  | 3.6334
[12 empty] | 3.3798 | 0.5793% |  |  |  |  | Max |  |  | 2.4051 |  |  | 3.4022 |  |  | 3.609 |  |  | 1.9053 |  |  | 2.7735 |  |  | 3.6619 |  |  | 3.8696 |  |  | 2.9486 |  |  | 3.4067 |  |  | 4.062 |  |  | 2.8674 |  |  | 3.4737 |  |  | 2.4165 |  |  | 3.6553
[12 empty] | 3.5888 | 0.4783%
[12 empty] | 1.9032 | 0.01012%
[12 empty] | 2.7634 | 0.2438%
[12 empty] | 3.6291 | 0.645%
[12 empty] | 3.8376 | 0.5539%
[12 empty] | 2.9298 | 0.3445%
[12 empty] | 3.3824 | 0.3353%
[12 empty] | 4.0408 | 0.02065%
[12 empty] | 2.8486 | 0.09057%
[12 empty] | 3.4022 | 0.2101%
[12 empty] | 2.3048 | 0.03036%
[12 empty] | 3.6202 | 0.6777%
[12 empty] | Max | 0.6777%

## Coil Load Data
IEA HVAC BESTEST
Results taken from File i221000a.WK3, Sheet Q, Cells BF77:BU146
Coil Loads: Total, Sensible, and Latent
Coil Load, Total (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 3800 | 3792 | 3841.47 | 3793.9625 | 3804.2 | 3799.7366 | 3797.9491 | 3792 | 3841.47 | 3804.1883 | 1.3% | 3800.3599 | 3800.4 | 3800.4 | 3796.6945 | 3800.3866 | 0.09715%
CE110 | 3765 | 3776 | 3803.58 | 3755.5686 | 3764.7 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 3770.3851 | 1.273% | 3765.2438 | 3765 | 3765.3 | 3762.6846 | 3765.1813 | 0.06631%
CE120 | 3749 | 3751 | 3763.48 | 3739.1559 | 3739.5 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 3748.1966 | 0.649% | 3748.902 | 3748.8 | 3748.5 | 3746.3788 | 3748.734 | 0.06283%
CE130 | 219 | 219 | 215.778 | 215.1231 | 217.7 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 217.908 | 2.132% | 219.3541 | 219.3 | 219.2 | 215.9611 | 219.2847 | 1.516%
CE140 | 198 | 198 | 195.53 | 194.6073 | 196.7 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 197.0109 | 2.009% | 197.9671 | 197.9 | 197.3 | 195.8173 | 197.7224 | 0.9635%
CE150 | 4517 | 4519 | 4542.78 | 4527.5498 | 4526.6 | 4516.9958 | 4515.0285 | 4515.0285 | 4542.78 | 4523.5649 | 0.6135% | 4517.5274 | 4517.4 | 4518.3 | 4508.3212 | 4517.7425 | 0.2085%
CE160 | 4501 | 4502 | 4516.378 | 4508.4994 | 4505.5 | 4500.0682 | 4498.8816 | 4498.8816 | 4516.378 | 4504.6182 | 0.3884% | 4500.5449 | 4500.3 | 4499.9 | 4490.5145 | 4500.2483 | 0.2163%
CE165 | 4538 | 4539 | 4567.458 | 4548.9449 | 4555.7 | 4537.0685 | 4535.1008 | 4535.1008 | 4567.458 | 4545.896 | 0.7118% | 4536.998 | 4537.3 | 4537.9 | 4527.873 | 4537.3993 | 0.21%
CE170 | 2233 | 2232 | 2226.057 | 2236.5182 | 2230.4 | 2231.6851 | 2231.6345 | 2226.057 | 2236.5182 | 2231.6135 | 0.4688% | 2232.3427 | 2231.9 | 2232.5 | 2224.4208 | 2232.2476 | 0.3506%
CE180 | 4495 | 4496 | 4509.984 | 4534.5838 | 4506.8 | 4494.6115 | 4494.0999 | 4494.0999 | 4534.5838 | 4504.4399 | 0.8988% | 4495.2651 | 4494.9 | 4493.8 | 4480.7708 | 4494.655 | 0.3089%
CE185 | 4507 | 4537 | 4564.894 | 4582.6495 | 4611 | 4534.5283 | 4533.9432 | 4507 | 4611 | 4553.0021 | 2.284% | 4535.1231 | 4534.9 | 4533.9 | 4521.5036 | 4534.641 | 0.2897%
CE190 | 578 | 578 | 572.607 | 578.5463 | 576.3 | 577.1889 | 577.6703 | 572.607 | 578.5463 | 576.9018 | 1.03% | 577.5279 | 577.3 | 577.7 | 573.8077 | 577.5093 | 0.641%
CE195 | 602 | 602 | 595.24 | 601.6999 | 606.8 | 600.9508 | 601.339 | 595.24 | 606.8 | 601.4328 | 1.922% | 601.3744 | 601.2 | 601.2 | 596.6464 | 601.2581 | 0.767%
CE200 | 5498 | 5438 | 5534.2 | 5521.9812 | 5522 | 5497.5648 | 5497.5648 | 5438 | 5534.2 | 5501.3301 | 1.749% | 5497.8008 | 5497.8 | 5497.8 | 5483.8906 | 5497.8003 | 0.253%
Coil Load, Sensible (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.516%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 3800 | 3792 | 3841.47 | 3793.9625 | 3804.2 | 3799.7366 | 3797.9491 | 3792 | 3841.47 | 3804.1883 | 1.3% | 3800.3599 | 3800.4 | 3800.4 | 3796.6945 | 3800.3866 | 0.09715%
CE110 | 3765 | 3776 | 3803.58 | 3755.5686 | 3764.7 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 3770.3851 | 1.273% | 3765.2438 | 3765 | 3765.3 | 3762.6846 | 3765.1813 | 0.06631%
CE120 | 3749 | 3751 | 3763.48 | 3739.1559 | 3739.5 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 3748.1966 | 0.649% | 3748.902 | 3748.8 | 3748.5 | 3746.3788 | 3748.734 | 0.06283%
CE130 | 219 | 219 | 215.778 | 215.1231 | 217.7 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 217.908 | 2.132% | 219.3541 | 219.3 | 219.2 | 215.9611 | 219.2847 | 1.516%
CE140 | 198 | 198 | 195.53 | 194.6073 | 196.7 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 197.0109 | 2.009% | 197.9671 | 197.9 | 197.3 | 195.8173 | 197.7224 | 0.9635%
CE150 | 3778 | 3780 | 3803.58 | 3786.0492 | 3787.8 | 3777.7958 | 3775.8216 | 3775.8216 | 3803.58 | 3784.1495 | 0.7335% | 3778.3318 | 3778.2 | 3779 | 3769.124 | 3778.5106 | 0.2484%
CE160 | 3761 | 3763 | 3777.178 | 3769.0504 | 3766.4 | 3760.8682 | 3759.6868 | 3759.6868 | 3777.178 | 3765.3119 | 0.4645% | 3761.3053 | 3761.1 | 3760.8 | 3751.3173 | 3761.0684 | 0.2593%
CE165 | 3798 | 3800 | 3828.258 | 3808.6166 | 3816.8 | 3797.8685 | 3795.9117 | 3795.9117 | 3828.258 | 3806.4935 | 0.8498% | 3797.7525 | 3798.1 | 3798.6 | 3788.6753 | 3798.1508 | 0.2495%
CE170 | 1493 | 1493 | 1486.857 | 1497.6553 | 1492.6 | 1492.4851 | 1492.423 | 1486.857 | 1497.6553 | 1492.5744 | 0.7235% | 1493.027 | 1492.7 | 1493.1 | 1485.2201 | 1492.9423 | 0.5173%
CE180 | 1537 | 1539 | 1553.184 | 1606.6823 | 1563.4 | 1537.8115 | 1537.3001 | 1537 | 1606.6823 | 1553.4826 | 4.486% | 1537.7939 | 1538.1 | 1537.7 | 1523.978 | 1537.8646 | 0.903%
CE185 | 1548 | 1580 | 1608.094 | 1652.6964 | 1664.6 | 1577.7283 | 1577.1233 | 1548 | 1664.6 | 1601.1774 | 7.282% | 1577.6007 | 1578.1 | 1577.7 | 1564.7043 | 1577.8002 | 0.83%
CE190 | 208 | 208 | 203.007 | 212.1923 | 208.4 | 207.5889 | 208.0235 | 203.007 | 212.1923 | 207.8874 | 4.418% | 207.8123 | 207.7 | 207.9 | 204.2038 | 207.8041 | 1.733%
CE195 | 232 | 232 | 225.64 | 235.0528 | 238.5 | 231.3508 | 231.7335 | 225.64 | 238.5 | 232.3253 | 5.535% | 231.645 | 231.6 | 231.6 | 227.0242 | 231.615 | 1.982%
CE200 | 4276 | 4217 | 4313.176 | 4302.755 | 4299.6 | 4276.5408 | 4276.5408 | 4217 | 4313.176 | 4280.2304 | 2.247% | 4276.6945 | 4276.8 | 4276.8 | 4262.9069 | 4276.7648 | 0.324%
Coil Load, Latent (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.982%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 3.3138e-14 | 4.734e-15 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 2.6912e-15 | 3.8445e-16 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 3.8103e-15 | 5.4433e-16 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 3.1415e-14 | 4.4878e-15 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | -2.7533e-16 | 0 | -3.9334e-17 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE150 | 739 | 739 | 739.2 | 741.5006 | 738.7 | 739.2 | 739.2069 | 738.7 | 741.5006 | 739.4011 | 0.3788% | 739.1956 | 739.2 | 739.4 | 739.1972 | 739.2652 | 0.009196%
CE160 | 740 | 739 | 739.2 | 739.449 | 739.1 | 739.2 | 739.1947 | 739 | 740 | 739.3062 | 0.1353% | 739.2396 | 739.2 | 739.1 | 739.1972 | 739.1799 | 0.002344%
CE165 | 740 | 739 | 739.2 | 740.3283 | 739 | 739.2 | 739.1892 | 739 | 740.3283 | 739.4168 | 0.1796% | 739.2454 | 739.2 | 739.3 | 739.1977 | 739.2485 | 0.006864%
CE170 | 740 | 739 | 739.2 | 738.8628 | 737.8 | 739.2 | 739.2115 | 737.8 | 740 | 739.0392 | 0.2977% | 739.3157 | 739.2 | 739.4 | 739.2008 | 739.3052 | 0.01413%
CE180 | 2958 | 2957 | 2956.8 | 2927.9015 | 2943.4 | 2956.8 | 2956.7992 | 2927.9015 | 2958 | 2950.9573 | 1.02% | 2957.4713 | 2956.8 | 2956.1 | 2956.7927 | 2956.7904 | 7.847e-05%
CE185 | 2959 | 2957 | 2956.8 | 2929.9531 | 2946.4 | 2956.8 | 2956.8195 | 2929.9531 | 2959 | 2951.8247 | 0.984% | 2957.5224 | 2956.8 | 2956.2 | 2956.7993 | 2956.8408 | 0.001404%
CE190 | 370 | 370 | 369.6 | 366.354 | 368 | 369.6 | 369.6468 | 366.354 | 370 | 369.0287 | 0.988% | 369.7156 | 369.6 | 369.8 | 369.6039 | 369.7052 | 0.0274%
CE195 | 370 | 370 | 369.6 | 366.6471 | 368.4 | 369.6 | 369.6055 | 366.6471 | 370 | 369.1218 | 0.9083% | 369.7294 | 369.6 | 369.6 | 369.6221 | 369.6431 | 0.005683%
CE200 | 1222 | 1221 | 1221 | 1219.2263 | 1222.4 | 1221.024 | 1221.024 | 1219.2263 | 1222.4 | 1221.0963 | 0.2599% | 1221.1063 | 1221 | 1221 | 1220.9837 | 1221.0354 | 0.004238%
|  | i221000a.wk3 q:be77..bs146; 10/23/00 | [13 empty] | Max | 0.0274%
Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 144 | 136 | 187.05 | 138.6284 | 147.6 | 143.6534 | 142.3632 | 136 | 187.05 | 148.4707 | 34.38% | 144.0536 | 144.1 | 144.1 | 143.5848 | 144.0845 | 0.3469%
CE110 | 128 | 139 | 167.979 | 118.9918 | 127.3 | 127.6867 | 126.6828 | 118.9918 | 167.979 | 133.6629 | 36.65% | 128.1309 | 127.9 | 128.2 | 127.5927 | 128.077 | 0.3781%
CE120 | 117 | 119 | 133.008 | 107.5615 | 107.2 | 116.6726 | 115.4889 | 107.2 | 133.008 | 116.5616 | 22.14% | 116.9127 | 116.9 | 116.6 | 116.438 | 116.8042 | 0.3136%
CE130 | 10 | 10 | 8.434 | 7.6202 | 8.4 | 10.2601 | 10.3985 | 7.6202 | 10.3985 | 9.3018 | 29.87% | 10.4079 | 10.3 | 10.2 | 10.2115 | 10.3026 | 0.8844%
CE140 | 8 | 8 | 7.027 | 6.1547 | 6.6 | 8.1097 | 8.2063 | 6.1547 | 8.2063 | 7.4425 | 27.57% | 8.2142 | 8.2 | 7.6 | 8.0856 | 8.0047 | 1.01%
CE150 | 141 | 143 | 167.979 | 149.4725 | 137.9 | 140.8714 | 139.4441 | 137.9 | 167.979 | 145.6667 | 20.65% | 141.2189 | 141.1 | 141.9 | 140.3497 | 141.4063 | 0.7472%
CE160 | 129 | 131 | 146.726 | 137.456 | 124.9 | 129.1114 | 128.2687 | 124.9 | 146.726 | 132.3517 | 16.49% | 129.316 | 129.2 | 128.9 | 128.3806 | 129.1387 | 0.587%
CE165 | 149 | 151 | 181.387 | 160.6096 | 147.1 | 149.3587 | 147.9512 | 147.1 | 181.387 | 155.2009 | 22.09% | 149.1144 | 149.4 | 149.9 | 148.616 | 149.4715 | 0.5723%
CE170 | 73 | 74 | 68.706 | 79.1325 | 61.1 | 73.1606 | 73.002 | 61.1 | 79.1325 | 71.7287 | 25.14% | 73.5141 | 73.2 | 73.6 | 73.0391 | 73.438 | 0.5432%
CE180 | 117 | 120 | 135.132 | 188.1594 | 106.3 | 118.487 | 118.1294 | 106.3 | 188.1594 | 129.0297 | 63.44% | 118.281 | 118.6 | 118.2 | 118.4636 | 118.3603 | 0.08726%
CE185 | 109 | 161 | 171.245 | 215.4162 | 133.8 | 139.2451 | 138.8308 | 109 | 215.4162 | 152.6482 | 69.71% | 138.8945 | 139.4 | 139 | 139.139 | 139.0982 | 0.02936%
CE190 | 18 | 18 | 14.517 | 23.7397 | 13.6 | 18.0237 | 18.1676 | 13.6 | 23.7397 | 17.7212 | 57.22% | 18.0594 | 18 | 18.2 | 18.0123 | 18.0865 | 0.4099%
CE195 | 23 | 23 | 18.314 | 27.5498 | 17.6 | 22.6256 | 22.7915 | 17.6 | 27.5498 | 22.1258 | 44.97% | 22.6987 | 22.6 | 22.6 | 22.6112 | 22.6329 | 0.0959%
CE200 | 154 | 155 | 192.674 | 181.1254 | 155.1 | 154.56 | 154.56 | 154 | 192.674 | 163.8599 | 23.6% | 154.4636 | 154.6 | 154.6 | 153.4905 | 154.5545 | 0.6884%
[16 empty] | Max | 1.01%

## Zone Load Data
IEA HVAC BESTEST
Results taken from File i221000a.WK3, Sheet Q, Cells BV77:CK146
Zone Loads: Total, Sensible, and Latent
Zone Load, Total (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3656.6 | 3656.0832 | 3655.5859 | 3654.42 | 3656.6 | 3655.7176 | 0.05963% | 3656.3062 | 3656.3 | 3656.3 | 3653.1097 | 3656.3021 | 0.08731%
CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3637.4 | 3636.9245 | 3636.5534 | 3635.601 | 3637.4 | 3636.7222 | 0.04947% | 3637.1129 | 3637.1 | 3637.1 | 3635.0919 | 3637.1043 | 0.05533%
CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3632.3 | 3631.7568 | 3631.3216 | 3630.472 | 3632.3 | 3631.635 | 0.05034% | 3631.9893 | 3631.9 | 3631.9 | 3629.9408 | 3631.9298 | 0.05476%
CE130 | 209 | 209 | 207.344 | 207.5029 | 209.3 | 208.7252 | 209.371 | 207.344 | 209.371 | 208.6062 | 0.9717% | 208.9462 | 209 | 209 | 205.7496 | 208.9821 | 1.547%
CE140 | 190 | 190 | 188.503 | 188.4525 | 190.1 | 189.5652 | 190.358 | 188.4525 | 190.358 | 189.5684 | 1.005% | 189.7529 | 189.7 | 189.7 | 187.7318 | 189.7176 | 1.047%
CE150 | 4376 | 4376 | 4374.801 | 4376.0258 | 4388.6 | 4376.1245 | 4375.5775 | 4374.801 | 4388.6 | 4377.5898 | 0.3152% | 4376.3129 | 4376.3 | 4376.3 | 4374.3181 | 4376.3043 | 0.04539%
CE160 | 4371 | 4371 | 4369.652 | 4371.0434 | 4380.7 | 4370.9568 | 4370.6181 | 4369.652 | 4380.7 | 4372.1386 | 0.2527% | 4371.1893 | 4371.1 | 4371.1 | 4369.1704 | 4371.1298 | 0.04482%
CE165 | 4388 | 4388 | 4386.071 | 4387.456 | 4408.6 | 4387.7098 | 4387.1605 | 4386.071 | 4408.6 | 4390.4282 | 0.5131% | 4387.8381 | 4387.9 | 4387.9 | 4385.1599 | 4387.8794 | 0.06198%
CE170 | 2159 | 2158 | 2157.351 | 2157.9719 | 2169.3 | 2158.5245 | 2158.621 | 2157.351 | 2169.3 | 2159.8241 | 0.5532% | 2158.7129 | 2158.7 | 2158.7 | 2156.7137 | 2158.7043 | 0.09221%
CE180 | 4376 | 4376 | 4374.852 | 4376.0258 | 4400.5 | 4376.1245 | 4375.9707 | 4374.852 | 4400.5 | 4379.3533 | 0.5857% | 4376.3129 | 4376.3 | 4376.3 | 4374.3398 | 4376.3043 | 0.04489%
CE185 | 4396 | 4396 | 4393.649 | 4394.7831 | 4477.2 | 4395.2832 | 4395.0925 | 4393.649 | 4477.2 | 4406.8583 | 1.896% | 4395.5062 | 4395.5 | 4395.5 | 4392.349 | 4395.5021 | 0.07173%
CE190 | 557 | 560 | 558.09 | 558.0305 | 562.8 | 559.1652 | 559.4558 | 557 | 562.8 | 559.2202 | 1.037% | 559.3529 | 559.3 | 559.3 | 557.3382 | 559.3176 | 0.3539%
CE195 | 576 | 579 | 576.926 | 577.0809 | 589.2 | 578.3252 | 578.542 | 576 | 589.2 | 579.2963 | 2.279% | 578.5462 | 578.6 | 578.6 | 575.3548 | 578.5821 | 0.5578%
CE200 | 5343 | 5283 | 5341.526 | 5342.9074 | 5366.9 | 5343.0048 | 5343.0048 | 5283 | 5366.9 | 5337.6204 | 1.572% | 5343.2549 | 5343.2 | 5343.2 | 5340.9046 | 5343.2183 | 0.0433%
Zone Load, Sensible (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.547%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3656.6 | 3656.0832 | 3655.5859 | 3654.42 | 3656.6 | 3655.7176 | 0.05963% | 3656.3062 | 3656.3 | 3656.3 | 3653.1097 | 3656.3021 | 0.08731%
CE110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3637.4 | 3636.9245 | 3636.5534 | 3635.601 | 3637.4 | 3636.7222 | 0.04947% | 3637.1129 | 3637.1 | 3637.1 | 3635.0919 | 3637.1043 | 0.05533%
CE120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3632.3 | 3631.7568 | 3631.3216 | 3630.472 | 3632.3 | 3631.635 | 0.05034% | 3631.9893 | 3631.9 | 3631.9 | 3629.9408 | 3631.9298 | 0.05476%
CE130 | 209 | 209 | 207.344 | 207.5029 | 209.3 | 208.7252 | 209.371 | 207.344 | 209.371 | 208.6062 | 0.9717% | 208.9462 | 209 | 209 | 205.7496 | 208.9821 | 1.547%
CE140 | 190 | 190 | 188.503 | 188.4525 | 190.1 | 189.5652 | 190.358 | 188.4525 | 190.358 | 189.5684 | 1.005% | 189.7529 | 189.7 | 189.7 | 187.7318 | 189.7176 | 1.047%
CE150 | 3637 | 3637 | 3635.601 | 3636.5768 | 3649.9 | 3636.9245 | 3636.3775 | 3635.601 | 3649.9 | 3638.4828 | 0.393% | 3637.1129 | 3637.1 | 3637.1 | 3635.1214 | 3637.1043 | 0.05452%
CE160 | 3632 | 3632 | 3630.452 | 3631.5944 | 3641.5 | 3631.7568 | 3631.4181 | 3630.452 | 3641.5 | 3632.9602 | 0.3041% | 3631.9893 | 3631.9 | 3631.9 | 3629.9738 | 3631.9298 | 0.05386%
CE165 | 3649 | 3649 | 3646.871 | 3648.007 | 3669.7 | 3648.5098 | 3647.9605 | 3646.871 | 3669.7 | 3651.2926 | 0.6252% | 3648.6381 | 3648.7 | 3648.7 | 3645.9633 | 3648.6794 | 0.07444%
CE170 | 1420 | 1419 | 1418.151 | 1418.5229 | 1431.5 | 1419.3245 | 1419.421 | 1418.151 | 1431.5 | 1420.8456 | 0.9395% | 1419.5129 | 1419.5 | 1419.5 | 1417.5137 | 1419.5043 | 0.1402%
CE180 | 1420 | 1419 | 1418.052 | 1418.5229 | 1457.1 | 1419.3245 | 1419.1707 | 1418.052 | 1457.1 | 1424.4529 | 2.741% | 1419.5129 | 1419.5 | 1419.5 | 1417.5533 | 1419.5043 | 0.1374%
CE185 | 1439 | 1419 | 1436.849 | 1437.2802 | 1530.8 | 1438.4832 | 1438.2925 | 1419 | 1530.8 | 1448.5293 | 7.718% | 1438.7062 | 1438.7 | 1438.7 | 1435.5625 | 1438.7021 | 0.2182%
CE190 | 190 | 190 | 188.49 | 188.4525 | 194.8 | 189.5652 | 189.8558 | 188.4525 | 194.8 | 190.1662 | 3.338% | 189.7529 | 189.7 | 189.7 | 187.7391 | 189.7176 | 1.043%
CE195 | 209 | 209 | 207.326 | 207.5029 | 220.9 | 208.7252 | 208.942 | 207.326 | 220.9 | 210.1995 | 6.458% | 208.9462 | 209 | 209 | 205.7557 | 208.9821 | 1.544%
CE200 | 4122 | 4062 | 4120.502 | 4121.6295 | 4144.5 | 4121.9808 | 4121.9808 | 4062 | 4144.5 | 4116.3704 | 2.004% | 4122.2309 | 4122.2 | 4122.2 | 4119.9223 | 4122.2103 | 0.0555%
Zone Load, Latent (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [7 empty] | Max | 1.547%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  |  | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE150 | 739 | 739 | 739.2 | 739.449 | 738.7 | 739.2 | 739.2 | 738.7 | 739.449 | 739.107 | 0.1013% | 739.2 | 739.2 | 739.2 | 739.1966 | 739.2 | 0.0004545%
CE160 | 739 | 739 | 739.2 | 739.449 | 739.1 | 739.2 | 739.2 | 739 | 739.449 | 739.1641 | 0.06074% | 739.2 | 739.2 | 739.2 | 739.1966 | 739.2 | 0.0004545%
CE165 | 739 | 739 | 739.2 | 739.449 | 738.9 | 739.2 | 739.2 | 738.9 | 739.449 | 739.1356 | 0.07428% | 739.2 | 739.2 | 739.2 | 739.1966 | 739.2 | 0.0004545%
CE170 | 739 | 739 | 739.2 | 739.449 | 737.8 | 739.2 | 739.2 | 737.8 | 739.449 | 738.9784 | 0.2231% | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 1.538e-14%
CE180 | 2957 | 2957 | 2956.8 | 2957.5029 | 2943.4 | 2956.8 | 2956.8 | 2943.4 | 2957.5029 | 2955.0433 | 0.4772% | 2956.8 | 2956.8 | 2956.8 | 2956.7866 | 2956.8 | 0.0004545%
CE185 | 2957 | 2957 | 2956.8 | 2957.5029 | 2946.3 | 2956.8 | 2956.8 | 2946.3 | 2957.5029 | 2955.4576 | 0.3791% | 2956.8 | 2956.8 | 2956.8 | 2956.7866 | 2956.8 | 0.0004545%
CE190 | 367 | 370 | 369.6 | 369.578 | 368 | 369.6 | 369.6 | 367 | 370 | 369.054 | 0.8129% | 369.6 | 369.6 | 369.6 | 369.5991 | 369.6 | 0.0002545%
CE195 | 367 | 370 | 369.6 | 369.578 | 368.4 | 369.6 | 369.6 | 367 | 370 | 369.1111 | 0.8128% | 369.6 | 369.6 | 369.6 | 369.5991 | 369.6 | 0.0002545%
CE200 | 1221 | 1221 | 1221.024 | 1221.2778 | 1222.4 | 1221.024 | 1221.024 | 1221 | 1222.4 | 1221.25 | 0.1146% | 1221.024 | 1221 | 1221 | 1220.9824 | 1221.008 | 0.0021%
|  | i221000a.wk3 q:bu77..ci146; 10/23/00 | [13 empty] | Max | 0.0021%
Latent Coil - Zone Load, (Should be 0) (kWh,thermal) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
CE100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 3.3138e-14 | 4.734e-15 |  | 0 | 0 | 0
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 2.6912e-15 | 3.8445e-16 |  | 0 | 0 | 0
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 3.8103e-15 | 5.4433e-16 |  | 0 | 0 | 0
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 3.1415e-14 | 4.4878e-15 |  | 0 | 0 | 0
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | -2.7533e-16 | 0 | -3.9334e-17 |  | 0 | 0 | 0
CE150 | 0 | 0 | 0 | 2.0516 | 0 | 0 | 0.00687 | 0 | 2.0516 | 0.29406 |  | -0.0044111 | 0 | 0.2
CE160 | 1 | 0 | 0 | 0 | 0 | 0 | -0.00534 | -0.00534 | 1 | 0.14209 |  | 0.039573 | 0 | -0.1
CE165 | 1 | 0 | 0 | 0.87925 | 0.1 | 0 | -0.01082 | -0.01082 | 1 | 0.2812 |  | 0.045435 | 0 | 0.1
CE170 | 1 | 0 | 0 | -0.58617 | 0 | 0 | 0.01152 | -0.58617 | 1 | 0.060765 |  | 0.1157 | 0 | 0.2
CE180 | 1 | 0 | 0 | -29.6014 | 0 | 0 | -0.00076 | -29.6014 | 1 | -4.086 |  | 0.67126 | 0 | -0.7
CE185 | 2 | 0 | 0 | -27.5498 | 0.1 | 0 | 0.01946 | -27.5498 | 2 | -3.6329 |  | 0.72237 | 0 | -0.6
CE190 | 3 | 0 | 0 | -3.2239 | 0 | 0 | 0.046846 | -3.2239 | 3 | -0.025296 |  | 0.11557 | 0 | 0.2
CE195 | 3 | 0 | 0 | -2.9308 | 0 | 0 | 0.0055 | -2.9308 | 3 | 0.010667 |  | 0.1294 | 0 | 0
CE200 | 1 | 0 | -0.024 | -2.0516 | 0 | 0 | 0 | -2.0516 | 1 | -0.15365 |  | 0.082262 | 0 | 0

## Indoor Temp Data
IEA HVAC BESTEST
Results taken from File i221000a.WK3, Sheet Q, Cells BE233:BT303
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
Mean IDB (°C) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  | IDB Mean | IDB Min | IDB Max | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.6346 | 22.2 | 22.6346 | 22.2954 | 1.949% | 22.2 | 22.2 | 22.216 | 22.1999 | 22.1999 | 22.1999 | 22.2053 | 0.02436%
CE110 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.2 | 22.2 | 22.5242 | 22.2 | 22.5242 | 22.2717 | 1.456% | 22.2 | 22.2 | 22.214 | 22.1999 | 22.1999 | 22.1999 | 22.2047 | 0.02152%
CE120 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 27.0785 | 26.7715 | 1.414% | 26.7 | 26.7 | 26.712 | 26.7 | 26.7 | 26.7 | 26.704 | 0.01498%
CE130 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 21.6377 | 22.2 | 22.0927 | 2.545% | 22.2 | 22.2 | 22.187 | 22.2 | 22.2 | 22.2 | 22.1957 | 0.01953%
CE140 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 21.5097 | 22.2 | 22.0744 | 3.127% | 22.2 | 22.2 | 22.185 | 22.2 | 22.2 | 22.2 | 22.195 | 0.02253%
CE150 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.6771 | 22.2 | 22.6771 | 22.3015 | 2.14% | 22.2 | 22.2 | 22.216 | 22.1772 | 22.176 | 22.178 | 22.2053 | 0.1268%
CE160 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 26.9948 | 26.7 | 26.9948 | 26.7596 | 1.102% | 26.7 | 26.7 | 26.714 | 26.6723 | 26.6697 | 26.6748 | 26.7047 | 0.1212%
CE165 | 23.3 | 23.3 | 23.4 | 23.4444 | 23.3 | 23.3 | 23.7805 | 23.3 | 23.7805 | 23.4036 | 2.053% | 23.3 | 23.3 | 23.317 | 23.28 | 23.2741 | 23.2806 | 23.3057 | 0.1103%
CE170 | 22.2 | 22.2 | 22.2 | 22.2222 | 22.2 | 22.2 | 22.1169 | 22.1169 | 22.2222 | 22.1913 | 0.4748% | 22.2 | 22.2 | 22.199 | 22.1809 | 22.1799 | 22.1815 | 22.1997 | 0.08446%
CE180 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.3344 | 22.2446 | 0.6041% | 22.2 | 22.2 | 22.205 | 22.157 | 22.1548 | 22.1581 | 22.2017 | 0.2013%
CE185 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.3682 | 22.2574 | 0.7556% | 22.2 | 22.2 | 22.206 | 22.1672 | 22.1627 | 22.1678 | 22.202 | 0.1567%
CE190 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.9469 | 21.9469 | 22.2 | 22.1369 | 1.143% | 22.2 | 22.2 | 22.194 | 22.1945 | 22.1943 | 22.1946 | 22.198 | 0.0159%
CE195 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 22.0113 | 22.0113 | 22.2 | 22.1461 | 0.8522% | 22.2 | 22.2 | 22.195 | 22.1956 | 22.1953 | 22.1957 | 22.1983 | 0.01232%
CE200 | 26.7 | 26.75 | 26.8 | 26.7778 | 26.7 | 26.7339 | 26.7339 | 26.7 | 26.8 | 26.7422 | 0.3739% | 26.7 | 26.7 | 26.713 | 26.6624 | 26.6613 | 26.6635 | 26.7043 | 0.1571%
(Max - Min)/Mean IDB (°C) | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [9 empty] | Max | 0.2013%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
CE100 | 0 | 0 | 0 | 0 | 0.00045045 | 0 | 0.049482 | 0 | 0.049482 | 0.0071332 |  | 0 | 0 | 0.0017105
CE110 | 0 | 0 | 0 | 0 | 0 | 0 | 0.047948 | 0 | 0.047948 | 0.0068498 |  | 0 | 0 | 0.0018907
CE120 | 0 | 0 | 0 | 0 | 0 | 0 | 0.077183 | 0 | 0.077183 | 0.011026 |  | 0 | 0 | 0.0017221
CE130 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056383 | 0 | 0.056383 | 0.0080547 |  | 0 | 0 | 0.0013521
CE140 | 0 | 0 | 0 | 0 | 0 | 0 | 0.069271 | 0 | 0.069271 | 0.0098959 |  | 0 | 0 | 0.0015326
CE150 | 0 | 0 | 0 | 0 | 0 | 0 | 0.053799 | 0 | 0.053799 | 0.0076855 |  | 0 | 0 | 0.0017105
CE160 | 0 | 0 | 0 | 0 | 0 | 0 | 0.045194 | 0 | 0.045194 | 0.0064563 |  | 0 | 0 | 0.0015722
CE165 | 0 | 0 | 0 | 0 | 0.00042918 | 0 | 0.051303 | 0 | 0.051303 | 0.0073902 |  | 0 | 0 | 0.0015439
CE170 | 0 | 0 | 0 | 0 | 0.00045045 | 0 | 0.049736 | 0 | 0.049736 | 0.0071695 |  | 0 | 0 | 0.0013064
CE180 | 0 | 0 | 0 | 0 | 0.00045045 | 0 | 0.034924 | 0 | 0.034924 | 0.0050535 |  | 0 | 0 | 0.00081063
CE185 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021459 | 0 | 0.021459 | 0.0030656 |  | 0 | 0 | 0.00072053
CE190 | 0 | 0 | 0 | 0 | 0.00045045 | 0 | 0.02825 | 0 | 0.02825 | 0.0041001 |  | 0 | 0 | 0.00072092
CE195 | 0 | 0 | 0 | 0 | 0.00045045 | 0 | 0.022716 | 0 | 0.022716 | 0.0033094 |  | 0 | 0 | 0.00063077
CE200 | 0 | 0 | 0 | 0 | 0.00037453 | 0 | 0 | 0 | 0.00037453 | 5.3505e-05 |  | 0 | 0 | 0
Humidity Ratio: Mean and (Max-Min)/Mean
Mean Humidity Ratio | [7 empty] | S t a t i s t i c s, A l l R e s u l t s
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical |  | HR Mean | HR Min | HR Max | Average | E+ vs Anal
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }} | Analytical | %Diff
CE100 | 0.0075 | 0.00692 | 0.0076 | 0.0074 | 0.0075 | 0.0075036 | 0.0075088 | 0.00692 | 0.0076 | 0.0074189 | 9.166% | 0.0074274 | 0.00734 | 0.007339 | 0.0074522 | 0.0074522 | 0.0074522 | 0.0073688 | 1.131%
CE110 | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065 | 0.0065938 | 0.0066309 | 0.0064 | 0.0070296 | 0.0066678 | 9.443% | 0.0065187 | 0.0064 | 0.006411 | 0.0065611 | 0.0065611 | 0.0065611 | 0.0064432 | 1.829%
CE120 | 0.008 | 0.00692 | 0.0078 | 0.0078 | 0.0072 | 0.0079506 | 0.0079517 | 0.00692 | 0.008 | 0.0076603 | 14.1% | 0.0078783 | 0.00786 | 0.007873 | 0.008011 | 0.008011 | 0.008011 | 0.0078704 | 1.786%
CE130 | 0.0075 | 0.00692 | 0.0076 | 0.0073 | 0.0075 | 0.0075036 | 0.0075194 | 0.00692 | 0.0076 | 0.0074061 | 9.182% | 0.0074274 | 0.00734 | 0.007339 | 0.0074578 | 0.0074578 | 0.0074578 | 0.0073688 | 1.208%
CE140 | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065 | 0.0065938 | 0.0065941 | 0.0064 | 0.0070601 | 0.0066526 | 9.923% | 0.0065187 | 0.0064 | 0.006402 | 0.0065668 | 0.0065668 | 0.0065668 | 0.0064402 | 1.966%
CE150 | 0.0083 | 0.00851 | 0.0082 | 0.0083 | 0.0084 | 0.0083236 | 0.0085152 | 0.0082 | 0.0085152 | 0.0083641 | 3.769% | 0.0082272 | 0.0082 | 0.00821 | 0.0083955 | 0.0083239 | 0.0084158 | 0.0082124 | 2.229%
CE160 | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.0103 | 0.010069 | 0.010236 | 0.009701 | 0.0103 | 0.010072 | 5.947% | 0.009969 | 0.00994 | 0.009946 | 0.01024 | 0.010152 | 0.010269 | 0.0099517 | 2.9%
CE165 | 0.0093 | 0.0098 | 0.0090039 | 0.0092 | 0.0094 | 0.0093021 | 0.0095112 | 0.0090039 | 0.0098 | 0.0093596 | 8.506% | 0.0092694 | 0.0092 | 0.009208 | 0.0093667 | 0.0092854 | 0.00939 | 0.0092258 | 1.527%
CE170 | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.0107 | 0.010471 | 0.010525 | 0.010471 | 0.0107 | 0.01057 | 2.168% | 0.010367 | 0.01045 | 0.010451 | 0.01055 | 0.010465 | 0.010582 | 0.010423 | 1.225%
CE180 | 0.0164 | 0.0162 | 0.016614 | 0.0164 | 0.0164 | 0.01631 | 0.016404 | 0.0162 | 0.016614 | 0.01639 | 2.526% | 0.01619 | 0.01623 | 0.01623 | 0.016161 | 0.016042 | 0.0162 | 0.016217 | 0.3412%
CE185 | 0.0162 | 0.0169 | 0.016441 | 0.0162 | 0.0161 | 0.016151 | 0.016279 | 0.0161 | 0.0169 | 0.016324 | 4.901% | 0.016056 | 0.01605 | 0.016059 | 0.016049 | 0.015924 | 0.016117 | 0.016055 | 0.03764%
CE190 | 0.016 | 0.0159 | 0.016254 | 0.0159 | 0.0161 | 0.015921 | 0.015707 | 0.015707 | 0.016254 | 0.015969 | 3.428% | 0.015796 | 0.0159 | 0.015891 | 0.015867 | 0.015709 | 0.016105 | 0.015862 | 0.02945%
CE195 | 0.0156 | 0.0163 | 0.015764 | 0.0155 | 0.0156 | 0.01547 | 0.015326 | 0.015326 | 0.0163 | 0.015651 | 6.223% | 0.015368 | 0.01544 | 0.015439 | 0.015464 | 0.015299 | 0.015907 | 0.015416 | 0.3169%
CE200 | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.0115 | 0.011281 | 0.011281 | 0.010933 | 0.0115 | 0.011285 | 5.025% | 0.011129 | 0.01109 | 0.011099 | 0.011419 | 0.011322 | 0.011447 | 0.011106 | 2.814%
(Max - Min)/Mean Humidity Ratio | [7 empty] | S t a t i s t i c s, A l l R e s u l t s | [9 empty] | Max | 2.9%
| CA-SIS | CLM2000 | DOE21E | DOE21E | Prometh | TRN-id | TRN-re |  |  |  | (Max-Min) |  | Analytical
| CASIS/EDF | CLIM2000/EDF | DOE21E/CIEMAT | DOE21E/NREL | PROKST/KST | TRNSYS-ideal/TUD | TRNYS-real/TUD | Min | Max | Mean | /Mean | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | EnergyPlus Ver {{ engine.config["EnergyPlusVersion"] }}
CE100 | 0 | 0.028902 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028902 | 0.0041288 |  | 0 | 0 | 0
CE110 | 0 | 0.028902 | 0.014226 | 0 | 0 | 0 | 0 | 0 | 0.028902 | 0.006161 |  | 0 | 0 | 0
CE120 | 0 | 0.028902 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028902 | 0.0041288 |  | 0 | 0 | 0
CE130 | 0 | 0.028902 | 0 | 0 | 0 | 0 | 0 | 0 | 0.028902 | 0.0041288 |  | 0 | 0 | 0
CE140 | 0 | 0.028902 | 0.014164 | 0 | 0 | 0 | 0 | 0 | 0.028902 | 0.0061523 |  | 0 | 0 | 0
CE150 | 0.012048 | 0.0011751 | 0 | 0 | 0.011905 | 0 | 0.013153 | 0 | 0.013153 | 0.0054687 |  | 0 | 0 | 0.00036541
CE160 | 0.019608 | 0 | 0.010308 | 0.010101 | 0.0097087 | 0 | 0.010747 | 0 | 0.019608 | 0.0086389 |  | 0 | 0 | 0.00040217
CE165 | 0.010753 | 0 | 0.011106 | 0 | 0.010638 | 0 | 0.012512 | 0 | 0.012512 | 0.0064298 |  | 0 | 0 | 0.0003258
CE170 | 0 | 0.00093458 | 0.0095289 | 0 | 0.0093458 | 0 | 0.023752 | 0 | 0.023752 | 0.0062231 |  | 0 | 0 | 0.00057411
CE180 | 0.018293 | 0 | 0.012038 | 0.012195 | 0.012195 | 0 | 0.040234 | 0 | 0.040234 | 0.013565 |  | 0 | 0 | 0.00092421
CE185 | 0.012346 | 0.0029586 | 0.018247 | 0.012346 | 0.018634 | 0 | 0.024571 | 0 | 0.024571 | 0.012729 |  | 0 | 0 | 0.00080951
CE190 | 0 | 0 | 0.018457 | 0.018868 | 0.012422 | 0 | 0.031196 | 0 | 0.031196 | 0.011563 |  | 0 | 0 | 0.00075514
CE195 | 0 | 0.006135 | 0.01903 | 0.019355 | 0.012821 | 0 | 0.024142 | 0 | 0.024142 | 0.01164 |  | 0 | 0 | 0.00064771
CE200 | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.0086957 | 0 | 0 | 0 | 0.017544 | 0.0063422 |  | 0 | 0 | 0