## L
HVBOUT2A.WK3, August 08, 2000
Output spreadsheet for HVAC BESTEST
EnergyPlus Version {{ engine.config["EnergyPlusVersion"] }}
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
| F e b r u a r y T o t a l s | [9 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
CE100 | 1520.1842 |  | 143.5848 |  | 3796.6945 | 3796.6945 | 0 | 3653.1097 | 3653.1097 | 0 | 2.4031 | 22.1999 | 0.0074522 | 2.4051 | 22.1999 | 0.0074522 | 2.3974 | 22.1999 | 0.0074522
CE110 | 1069.3313 |  | 127.5927 |  | 3762.6846 | 3762.6846 | 0 | 3635.0919 | 3635.0919 | 0 | 3.3994 | 22.1999 | 0.0065611 | 3.4022 | 22.1999 | 0.0065611 | 3.3935 | 22.1999 | 0.0065611
CE120 | 1006.6379 |  | 116.438 |  | 3746.3788 | 3746.3788 | 0 | 3629.9408 | 3629.9408 | 0 | 3.606 | 26.7 | 0.008011 | 3.609 | 26.7 | 0.008011 | 3.5998 | 26.7 | 0.008011
CE130 | 108.1197 |  | 10.2115 |  | 215.9611 | 215.9611 | 0 | 205.7496 | 205.7496 | 0 | 1.903 | 22.2 | 0.0074578 | 1.9053 | 22.2 | 0.0074578 | 1.897 | 22.2 | 0.0074578
CE140 | 67.7696 |  | 8.0856 |  | 195.8173 | 195.8173 | 0 | 187.7318 | 187.7318 | 0 | 2.7701 | 22.2 | 0.0065668 | 2.7735 | 22.2 | 0.0065668 | 2.7637 | 22.2 | 0.0065668
CE150 | 1197.6199 |  | 140.3497 |  | 4508.3212 | 3769.124 | 739.1972 | 4374.3181 | 3635.1214 | 739.1966 | 3.6525 | 22.1772 | 0.0083955 | 3.6619 | 22.178 | 0.0084158 | 3.6428 | 22.176 | 0.0083239
CE160 | 1132.2318 |  | 128.3806 |  | 4490.5145 | 3751.3173 | 739.1972 | 4369.1704 | 3629.9738 | 739.1966 | 3.8589 | 26.6723 | 0.01024 | 3.8696 | 26.6748 | 0.010269 | 3.8476 | 26.6697 | 0.010152
CE165 | 1491.5878 |  | 148.616 |  | 4527.873 | 3788.6753 | 739.1977 | 4385.1599 | 3645.9633 | 739.1966 | 2.9399 | 23.28 | 0.0093667 | 2.9486 | 23.2806 | 0.00939 | 2.9309 | 23.2741 | 0.0092854
CE170 | 635.4994 |  | 73.0391 |  | 2224.4208 | 1485.2201 | 739.2008 | 2156.7137 | 1417.5137 | 739.2 | 3.3937 | 22.1809 | 0.01055 | 3.4067 | 22.1815 | 0.010582 | 3.3792 | 22.1799 | 0.010465
CE180 | 1082.3259 |  | 118.4636 |  | 4480.7708 | 1523.978 | 2956.7927 | 4374.3398 | 1417.5533 | 2956.7866 | 4.0416 | 22.157 | 0.016161 | 4.062 | 22.1581 | 0.0162 | 4.0206 | 22.1548 | 0.016042
CE185 | 1540.5373 |  | 139.139 |  | 4521.5036 | 1564.7043 | 2956.7993 | 4392.349 | 1435.5625 | 2956.7866 | 2.8512 | 22.1672 | 0.016049 | 2.8674 | 22.1678 | 0.016117 | 2.8341 | 22.1627 | 0.015924
CE190 | 164.1636 |  | 18.0123 |  | 573.8077 | 204.2038 | 369.6039 | 557.3382 | 187.7391 | 369.5991 | 3.395 | 22.1945 | 0.015867 | 3.4737 | 22.1946 | 0.016105 | 3.3365 | 22.1943 | 0.015709
CE195 | 249.7096 |  | 22.6112 |  | 596.6464 | 227.0242 | 369.6221 | 575.3548 | 205.7557 | 369.5991 | 2.3041 | 22.1956 | 0.015464 | 2.4165 | 22.1957 | 0.015907 | 2.2341 | 22.1953 | 0.015299
CE200 | 1465.3737 |  | 153.4905 |  | 5483.8906 | 4262.9069 | 1220.9837 | 5340.9046 | 4119.9223 | 1220.9824 | 3.6447 | 26.6624 | 0.011419 | 3.6553 | 26.6635 | 0.011447 | 3.6334 | 26.6613 | 0.011322
Update separately

## A
RESULTS5-3.XLS | [7 empty] | INSTRUCTIONS
Output spreadsheet for HVAC BESTEST | [7 empty] | Import data so that Cell A1 of Sec5-3out.XLS is in A1 of Sheet "YD" (your data)
TAB OVER FOR INSTRUCTIONS | [7 empty] | Check that the first value (Total consumption kWh for E100) lands in YD!B25.
Data should land in "YD" cells as tabulated below. Your data will then appear in column M of Sheet A
and in rightmost column of each table on sheet Q. Chart update of "your data" is not automated.
Gives locations in participant spreadsheets (hvbtout.xls) | [7 empty] | See RESULTS5-3.DOC for spreadsheet navigation.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) |  |  | (°C) |  |  | (°C)
E100 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E110 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E120 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E130 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E140 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E150 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E160 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E165 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E170 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E180 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E185 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E190 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E195 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
E200 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
Energy Consumption, Total (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | Software
E100 | 1519 | 1520.817 | 1530 | 1522.2661 | 1511.9369 | 1530.548 | 1530.8 | 1530.6 | 1531 | 1520.1842 | 0
E110 | 1065 | 1061.196 | 1089 | 1066.9607 | 1061.9658 | 1076.2349 | 1077.2 | 1077.4 | 1077 | 1069.3313 | 0
E120 | 1003 | 1011.104 | 1012 | 1007.3023 | 1001.6637 | 1012.6774 | 1011 | 1011 | 1012 | 1006.6379 | 0
E130 | 106 | 105.419 | 109 | 108.7246 | 110.1161 | 110.5818 | 109.5 | 109.5 | 110 | 108.1197 | 0
E140 | 66 | 65.008 | 69 | 67.7641 | 68.6428 | 68.9953 | 68.5 | 68.3 | 68 | 67.7696 | 0
E150 | 1183 | 1202.424 | 1207 | 1199.055 | 1191.613 | 1206.49 | 1206.5 | 1206.5 | 1208 | 1197.6199 | 0
E160 | 1107 | 1137.63 | 1139 | 1136.7334 | 1132.8835 | 1140.44 | 1139.3 | 1138.9 | 1140 | 1132.2318 | 0
E165 | 1470 | 1499.447 | 1501 | 1499.7105 | 1489.9268 | 1497.8302 | 1499.7 | 1499.6 | 1502 | 1491.5878 | 0
E170 | 620 | 629.076 | 638 | 635.909 | 635.8287 | 641.1173 | 637.7 | 637.8 | 638 | 635.4994 | 0
E180 | 1080 | 1077.109 | 1082 | 1081.2706 | 1080.0377 | 1082.666 | 1082.3 | 1081.9 | 1083 | 1082.3259 | 0
E185 | 1547 | 1541.155 | 1543 | 1541.5256 | 1538.3972 | 1544.6397 | 1543.4 | 1542.9 | 1544 | 1540.5373 | 0
E190 | 160 | 160.219 | 164 | 163.9975 | 165.1202 | 165.173 | 164.1 | 164.2 | 164 | 164.1636 | 0
E195 | 246 | 244.919 | 250 | 249.7321 | 251.5799 | 252.1605 | 250 | 250 | 250 | 249.7096 | 0
E200 | 1440 | 1468.214 | 1464 | 1479.9926 | 1479.9926 | 1475.8104 | 1477.4 | 1477.1 | 1477 | 1465.3737 | 0
Energy Consumption, Compressor (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | Software
E100 | 1311 | 1307.458 | 1318 | 1311.1661 | 1302.7258 | 1318.8515 | 1319 | 1318.9 | 1319 | 0 | 0
E110 | 883 | 865.866 | 899 | 879.3187 | 875.8322 | 887.9378 | 889.2 | 889.4 | 889 | 0 | 0
E120 | 838 | 850.068 | 840 | 835.847 | 831.9292 | 840.8662 | 839.1 | 839.2 | 840 | 0 | 0
E130 | 93 | 93.198 | 94 | 93.6472 | 94.8489 | 95.2867 | 94.4 | 94.3 | 95 | 0 | 0
E140 | 56 | 54.799 | 57 | 55.8468 | 56.5735 | 56.924 | 56.5 | 56.4 | 57 | 0 | 0
E150 | 982 | 1007.094 | 999 | 992.0333 | 986.7503 | 998.9576 | 999.2 | 999.2 | 1000 | 0 | 0
E160 | 926 | 962.675 | 949 | 946.9958 | 944.3585 | 950.4111 | 949.4 | 949.1 | 950 | 0 | 0
E165 | 1256 | 1291.242 | 1281 | 1280.2205 | 1272.4664 | 1278.7205 | 1280.2 | 1280.2 | 1283 | 0 | 0
E170 | 523 | 538.959 | 530 | 528.3976 | 528.5837 | 532.9693 | 530 | 530.1 | 531 | 0 | 0
E180 | 912 | 914.262 | 908 | 907.1462 | 906.4398 | 908.1216 | 908 | 907.7 | 909 | 0 | 0
E185 | 1344 | 1342.681 | 1339 | 1336.897 | 1334.3908 | 1339.7996 | 1338.6 | 1338.2 | 1340 | 0 | 0
E190 | 138 | 139.423 | 138 | 137.5107 | 138.4572 | 138.4708 | 137.6 | 137.7 | 138 | 0 | 0
E195 | 217 | 218.867 | 217 | 216.4828 | 218.0909 | 218.6235 | 216.8 | 216.8 | 217 | 0 | 0
E200 | 1218 | 1249.027 | 1239 | 1252.8566 | 1252.8566 | 1248.8198 | 1250.2 | 1250 | 1250 | 0 | 0
Energy Consumption, Supply Fan (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-0500 | US-0401 | Software
E100 | 141 | 145.185 | 144 | 143.6481 | 142.3625 | 144.0538 | 144.1 | 144 | 144 | 143.5848 | 0
E110 | 122 | 132.917 | 129 | 127.6854 | 126.659 | 128.1312 | 127.9 | 127.9 | 128 | 127.5927 | 0
E120 | 110 | 109.581 | 117 | 116.6706 | 115.4998 | 116.9129 | 116.9 | 116.9 | 117 | 116.438 | 0
E130 | 8 | 8.316 | 10 | 10.2598 | 10.3889 | 10.4079 | 10.3 | 10.3 | 10 | 10.2115 | 0
E140 | 6 | 6.947 | 8 | 8.1094 | 8.2128 | 8.2142 | 8.1 | 8.1 | 8 | 8.0856 | 0
E150 | 136 | 132.917 | 141 | 140.8727 | 139.4036 | 141.2203 | 141.1 | 141.1 | 141 | 140.3497 | 0
E160 | 121 | 119.052 | 129 | 129.1114 | 128.2863 | 129.3096 | 129.2 | 129.2 | 129 | 128.3806 | 0
E165 | 145 | 141.678 | 150 | 149.3574 | 147.976 | 149.0983 | 149.3 | 149.3 | 149 | 148.616 | 0
E170 | 63 | 61.322 | 73 | 73.1586 | 72.9774 | 73.5918 | 73.2 | 73.2 | 73 | 73.0391 | 0
E180 | 112 | 110.813 | 119 | 118.487 | 118.1287 | 118.7728 | 118.6 | 118.5 | 118 | 118.4636 | 0
E185 | 137 | 135.056 | 139 | 139.2444 | 138.821 | 139.3882 | 139.4 | 139.3 | 139 | 139.139 | 0
E190 | 14 | 14.151 | 18 | 18.0236 | 18.1435 | 18.1701 | 18 | 18 | 18 | 18.0123 | 0
E195 | 18 | 17.728 | 23 | 22.6253 | 22.7884 | 22.821 | 22.6 | 22.6 | 23 | 22.6112 | 0
E200 | 151 | 149.151 | 153 | 154.56 | 154.56 | 154.4611 | 154.6 | 154.6 | 154 | 153.4905 | 0
Energy Consumption, Condenser Fan (kWh,e)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 67 | 68.174 | 68 | 67.452 | 66.8486 | 67.6427 | 67.6 | 67.6 | 68 | 0 | 0
E110 | 60 | 62.413 | 61 | 59.9566 | 59.4747 | 60.166 | 60.1 | 60.1 | 60 | 0 | 0
E120 | 55 | 51.455 | 55 | 54.7846 | 54.2347 | 54.8982 | 54.9 | 54.9 | 55 | 0 | 0
E130 | 5 | 3.905 | 5 | 4.8176 | 4.8783 | 4.8872 | 4.8 | 4.8 | 5 | 0 | 0
E140 | 4 | 3.262 | 4 | 3.8079 | 3.8565 | 3.8571 | 3.8 | 3.8 | 4 | 0 | 0
E150 | 65 | 62.413 | 66 | 66.1491 | 65.4591 | 66.3121 | 66.3 | 66.2 | 66 | 0 | 0
E160 | 60 | 55.903 | 61 | 60.6262 | 60.2388 | 60.7193 | 60.7 | 60.7 | 61 | 0 | 0
E165 | 69 | 66.527 | 70 | 70.1326 | 69.4843 | 70.0114 | 70.1 | 70.1 | 70 | 0 | 0
E170 | 34 | 28.795 | 34 | 34.3527 | 34.2676 | 34.5562 | 34.4 | 34.4 | 34 | 0 | 0
E180 | 56 | 52.034 | 56 | 55.6374 | 55.4691 | 55.7716 | 55.7 | 55.7 | 56 | 0 | 0
E185 | 66 | 63.418 | 65 | 65.3842 | 65.1855 | 65.4519 | 65.4 | 65.4 | 65 | 0 | 0
E190 | 8 | 6.645 | 9 | 8.4632 | 8.5195 | 8.5321 | 8.5 | 8.5 | 8 | 0 | 0
E195 | 11 | 8.324 | 11 | 10.6241 | 10.7006 | 10.716 | 10.6 | 10.6 | 11 | 0 | 0
E200 | 71 | 70.036 | 72 | 72.576 | 72.576 | 72.5296 | 72.6 | 72.6 | 73 | 0 | 0
Coil Load, Total (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 3793.9625 | 3841.47 | 3800 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 3800 | 3796.6945 | 0
E110 | 3755.5686 | 3803.58 | 3766 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 3765 | 3762.6846 | 0
E120 | 3739.1559 | 3763.48 | 3749 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 3749 | 3746.3788 | 0
E130 | 215.1231 | 215.778 | 219 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 219 | 215.9611 | 0
E140 | 194.6073 | 195.53 | 198 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 198 | 195.8173 | 0
E150 | 4527.5498 | 4542.78 | 4517 | 4516.9958 | 4515.0285 | 4517.5274 | 4517.4 | 4518.3 | 4517 | 4508.3212 | 0
E160 | 4508.4994 | 4516.378 | 4500 | 4500.0682 | 4498.8816 | 4500.5449 | 4500.3 | 4499.9 | 4501 | 4490.5145 | 0
E165 | 4548.9449 | 4567.458 | 4538 | 4537.0685 | 4535.1008 | 4536.998 | 4537.3 | 4537.9 | 4538 | 4527.873 | 0
E170 | 2236.5182 | 2226.057 | 2232 | 2231.6851 | 2231.6345 | 2232.3427 | 2231.9 | 2232.5 | 2233 | 2224.4208 | 0
E180 | 4534.5838 | 4509.984 | 4495 | 4494.6115 | 4494.0999 | 4495.2651 | 4494.9 | 4493.8 | 4495 | 4480.7708 | 0
E185 | 4582.6495 | 4564.894 | 4535 | 4534.5283 | 4533.9432 | 4535.1231 | 4534.9 | 4533.9 | 4507 | 4521.5036 | 0
E190 | 578.5463 | 572.607 | 577 | 577.1889 | 577.6703 | 577.5279 | 577.3 | 577.7 | 578 | 573.8077 | 0
E195 | 601.6999 | 595.24 | 601 | 600.9508 | 601.339 | 601.3744 | 601.2 | 601.2 | 602 | 596.6464 | 0
E200 | 5521.9812 | 5534.2 | 5436 | 5497.5648 | 5497.5648 | 5497.8008 | 5497.8 | 5497.8 | 5498 | 5483.8906 | 0
Coil Load, Sensible (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 3793.9625 | 3841.47 | 3800 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 3800 | 3796.6945 | 0
E110 | 3755.5686 | 3803.58 | 3766 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 3765 | 3762.6846 | 0
E120 | 3739.1559 | 3763.48 | 3749 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 3749 | 3746.3788 | 0
E130 | 215.1231 | 215.778 | 219 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 219 | 215.9611 | 0
E140 | 194.6073 | 195.53 | 198 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 198 | 195.8173 | 0
E150 | 3786.0492 | 3803.58 | 3778 | 3777.7958 | 3775.8216 | 3778.3318 | 3778.2 | 3779 | 3778 | 3769.124 | 0
E160 | 3769.0504 | 3777.178 | 3761 | 3760.8682 | 3759.6868 | 3761.3053 | 3761.1 | 3760.8 | 3761 | 3751.3173 | 0
E165 | 3808.6166 | 3828.258 | 3798 | 3797.8685 | 3795.9117 | 3797.7525 | 3798.1 | 3798.6 | 3798 | 3788.6753 | 0
E170 | 1497.6553 | 1486.857 | 1493 | 1492.4851 | 1492.423 | 1493.027 | 1492.7 | 1493.1 | 1493 | 1485.2201 | 0
E180 | 1606.6823 | 1553.184 | 1538 | 1537.8115 | 1537.3001 | 1537.7939 | 1538.1 | 1537.7 | 1537 | 1523.978 | 0
E185 | 1652.6964 | 1608.094 | 1578 | 1577.7283 | 1577.1233 | 1577.6007 | 1578.1 | 1577.7 | 1548 | 1564.7043 | 0
E190 | 212.1923 | 203.007 | 208 | 207.5889 | 208.0235 | 207.8123 | 207.7 | 207.9 | 208 | 204.2038 | 0
E195 | 235.0528 | 225.64 | 232 | 231.3508 | 231.7335 | 231.645 | 231.6 | 231.6 | 232 | 227.0242 | 0
E200 | 4302.755 | 4313.176 | 4215 | 4276.5408 | 4276.5408 | 4276.6945 | 4276.8 | 4276.8 | 4276 | 4262.9069 | 0
Coil Load, Latent (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 0 | 0 | 0 | 0 | 0
E110 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 0 | 0 | 0 | 0 | 0
E120 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 0 | 0 | 0 | 0 | 0
E130 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 0 | 0 | 0 | 0 | 0
E140 | 0 | 0 | 0 | 0 | -2.7533e-16 | 0 | 0 | 0 | 0 | 0 | 0
E150 | 741.5006 | 739.2 | 739 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 739 | 739.1972 | 0
E160 | 739.449 | 739.2 | 739 | 739.2 | 739.1947 | 739.2396 | 739.2 | 739.1 | 740 | 739.1972 | 0
E165 | 740.3283 | 739.2 | 739 | 739.2 | 739.1892 | 739.2454 | 739.2 | 739.3 | 740 | 739.1977 | 0
E170 | 738.8628 | 739.2 | 739 | 739.2 | 739.2115 | 739.3157 | 739.2 | 739.4 | 740 | 739.2008 | 0
E180 | 2927.9015 | 2956.8 | 2957 | 2956.8 | 2956.7992 | 2957.4713 | 2956.8 | 2956.1 | 2958 | 2956.7927 | 0
E185 | 2929.9531 | 2956.8 | 2957 | 2956.8 | 2956.8195 | 2957.5224 | 2956.8 | 2956.2 | 2959 | 2956.7993 | 0
E190 | 366.354 | 369.6 | 370 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 370 | 369.6039 | 0
E195 | 366.6471 | 369.6 | 370 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 370 | 369.6221 | 0
E200 | 1219.2263 | 1221 | 1221 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 1222 | 1220.9837 | 0
Envelope Load, Total (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 3655.3341 | 3654.42 | 3656 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 3656 | 3653.1097 | 0
E110 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.0919 | 0
E120 | 3631.5944 | 3630.472 | 3632 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3629.9408 | 0
E130 | 207.5029 | 207.344 | 209 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 209 | 205.7496 | 0
E140 | 188.4525 | 188.503 | 190 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 190 | 187.7318 | 0
E150 | 4376.0258 | 4374.801 | 4376 | 4376.1245 | 4375.5775 | 4376.3129 | 4376.3 | 4376.3 | 4376 | 4374.3181 | 0
E160 | 4371.0434 | 4369.652 | 4371 | 4370.9568 | 4370.6181 | 4371.1893 | 4371.1 | 4371.1 | 4371 | 4369.1704 | 0
E165 | 4387.456 | 4386.071 | 4388 | 4387.7098 | 4387.1605 | 4387.8381 | 4387.9 | 4387.9 | 4388 | 4385.1599 | 0
E170 | 2157.9719 | 2157.351 | 2159 | 2158.5245 | 2158.621 | 2158.7129 | 2158.7 | 2158.7 | 2159 | 2156.7137 | 0
E180 | 4376.0258 | 4374.852 | 4376 | 4376.1245 | 4375.9707 | 4376.3129 | 4376.3 | 4376.3 | 4376 | 4374.3398 | 0
E185 | 4394.7831 | 4393.649 | 4396 | 4395.2832 | 4395.0925 | 4395.5062 | 4395.5 | 4395.5 | 4396 | 4392.349 | 0
E190 | 558.0305 | 558.09 | 559 | 559.1652 | 559.4558 | 559.3529 | 559.3 | 559.3 | 557 | 557.3382 | 0
E195 | 577.0809 | 576.926 | 579 | 578.3252 | 578.542 | 578.5462 | 578.6 | 578.6 | 576 | 575.3548 | 0
E200 | 5342.9074 | 5341.526 | 5283 | 5343.0048 | 5343.0048 | 5343.2549 | 5343.2 | 5343.2 | 5343 | 5340.9046 | 0
Envelope Load, Sensible (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 3655.3341 | 3654.42 | 3656 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 3656 | 3653.1097 | 0
E110 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.0919 | 0
E120 | 3631.5944 | 3630.472 | 3632 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3629.9408 | 0
E130 | 207.5029 | 207.344 | 209 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 209 | 205.7496 | 0
E140 | 188.4525 | 188.503 | 190 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 190 | 187.7318 | 0
E150 | 3636.5768 | 3635.601 | 3637 | 3636.9245 | 3636.3775 | 3637.1129 | 3637.1 | 3637.1 | 3637 | 3635.1214 | 0
E160 | 3631.5944 | 3630.452 | 3632 | 3631.7568 | 3631.4181 | 3631.9893 | 3631.9 | 3631.9 | 3632 | 3629.9738 | 0
E165 | 3648.007 | 3646.871 | 3649 | 3648.5098 | 3647.9605 | 3648.6381 | 3648.7 | 3648.7 | 3649 | 3645.9633 | 0
E170 | 1418.5229 | 1418.151 | 1420 | 1419.3245 | 1419.421 | 1419.5129 | 1419.5 | 1419.5 | 1420 | 1417.5137 | 0
E180 | 1418.5229 | 1418.052 | 1420 | 1419.3245 | 1419.1707 | 1419.5129 | 1419.5 | 1419.5 | 1420 | 1417.5533 | 0
E185 | 1437.2802 | 1436.849 | 1439 | 1438.4832 | 1438.2925 | 1438.7062 | 1438.7 | 1438.7 | 1439 | 1435.5625 | 0
E190 | 188.4525 | 188.49 | 190 | 189.5652 | 189.8558 | 189.7529 | 189.7 | 189.7 | 190 | 187.7391 | 0
E195 | 207.5029 | 207.326 | 209 | 208.7252 | 208.942 | 208.9462 | 209 | 209 | 209 | 205.7557 | 0
E200 | 4121.6295 | 4120.502 | 4062 | 4121.9808 | 4121.9808 | 4122.2309 | 4122.2 | 4122.2 | 4122 | 4119.9223 | 0
Envelope Load, Latent (kWh,thermal)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E150 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966 | 0
E160 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966 | 0
E165 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.1966 | 0
E170 | 739.449 | 739.2 | 739 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739 | 739.2 | 0
E180 | 2957.5029 | 2956.8 | 2957 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2957 | 2956.7866 | 0
E185 | 2957.5029 | 2956.8 | 2957 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2957 | 2956.7866 | 0
E190 | 369.578 | 369.6 | 370 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 367 | 369.5991 | 0
E195 | 369.578 | 369.6 | 370 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 367 | 369.5991 | 0
E200 | 1221.2778 | 1221.024 | 1221 | 1221.024 | 1221.024 | 1221.024 | 1221 | 1221 | 1221 | 1220.9824 | 0
Mean COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 2.4064 | 2.4304 | 2.389 | 2.4017 | 2.4184 | 2.3889 | 2.39 | 2.39 | 2.39 | 2.4031 | 0
E110 | 3.4146 | 3.4589 | 3.342 | 3.4087 | 3.4271 | 3.3795 | 3.38 | 3.38 | 3.38 | 3.3994 | 0
E120 | 3.623 | 3.6139 | 3.59 | 3.6054 | 3.6313 | 3.5865 | 3.59 | 3.59 | 3.59 | 3.606 | 0
E130 | 1.953 | 1.9752 | 1.909 | 1.9198 | 1.9163 | 1.8895 | 1.91 | 1.91 | 1.91 | 1.903 | 0
E140 | 2.854 | 2.9151 | 2.734 | 2.7974 | 2.7996 | 2.7502 | 2.77 | 2.77 | 2.77 | 2.7701 | 0
E150 | 3.7 | 3.6675 | 3.63 | 3.6496 | 3.6734 | 3.6273 | 3.63 | 3.63 | 3.62 | 3.6525 | 0
E160 | 3.95 | 3.8658 | 3.84 | 3.8452 | 3.8599 | 3.8329 | 3.84 | 3.84 | 3.84 | 3.8589 | 0
E165 | 2.9853 | 2.9514 | 2.92 | 2.9257 | 2.9449 | 2.9295 | 2.93 | 2.93 | 2.92 | 2.9399 | 0
E170 | 3.477 | 3.4423 | 3.39 | 3.3944 | 3.4033 | 3.3672 | 3.39 | 3.39 | 3.38 | 3.3937 | 0
E180 | 4.026 | 4.0842 | 4.04 | 4.0472 | 4.055 | 4.0423 | 4.04 | 4.04 | 4.04 | 4.0416 | 0
E185 | 2.823 | 2.8744 | 2.85 | 2.8512 | 2.8574 | 2.8458 | 2.85 | 2.85 | 2.85 | 2.8512 | 0
E190 | 3.457 | 3.4865 | 3.41 | 3.4096 | 3.4048 | 3.3865 | 3.41 | 3.41 | 3.41 | 3.395 | 0
E195 | 2.337 | 2.3598 | 2.31 | 2.3158 | 2.3054 | 2.2944 | 2.31 | 2.31 | 2.31 | 2.3041 | 0
E200 | 3.708 | 3.6677 | 3.61 | 3.6102 | 3.6102 | 3.6206 | 3.62 | 3.62 | 3.62 | 3.6447 | 0
Mean IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.6346 | 22.2 | 22.2 | 22.216 | 22.2 | 22.1999 | 0
E110 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.5242 | 22.2 | 22.2 | 22.214 | 22.2 | 22.1999 | 0
E120 | 26.7222 | 26.8 | 26.7 | 26.7 | 27.0785 | 26.7 | 26.7 | 26.712 | 26.7 | 26.7 | 0
E130 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.6377 | 22.2 | 22.2 | 22.187 | 22.2 | 22.2 | 0
E140 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.5097 | 22.2 | 22.2 | 22.185 | 22.2 | 22.2 | 0
E150 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.6771 | 22.2 | 22.2 | 22.216 | 22.2 | 22.1772 | 0
E160 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.9948 | 26.7 | 26.7 | 26.714 | 26.7 | 26.6723 | 0
E165 | 23.4444 | 23.4 | 23.3 | 23.3 | 23.7805 | 23.3 | 23.3 | 23.317 | 23.3 | 23.28 | 0
E170 | 22.2222 | 22.2 | 22.2 | 22.2 | 22.1169 | 22.2 | 22.2 | 22.199 | 22.2 | 22.1809 | 0
E180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.3344 | 22.2 | 22.2 | 22.205 | 22.2 | 22.157 | 0
E185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.3682 | 22.2 | 22.2 | 22.206 | 22.2 | 22.1672 | 0
E190 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.9469 | 22.2 | 22.2 | 22.194 | 22.2 | 22.1945 | 0
E195 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.0113 | 22.2 | 22.2 | 22.195 | 22.2 | 22.1956 | 0
E200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.7339 | 26.7 | 26.7 | 26.713 | 26.7 | 26.6624 | 0
Mean Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0.0074 | 0.0076 | 0.00691 | 0.0075036 | 0.0075088 | 0.0074274 | 0.00734 | 0.007339 | 0.0075 | 0.0074522 | 0
E110 | 0.0064 | 0.0070296 | 0.00692 | 0.0065938 | 0.0066309 | 0.0065187 | 0.0064 | 0.006411 | 0.0066 | 0.0065611 | 0
E120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.0079517 | 0.0078783 | 0.00786 | 0.007873 | 0.008 | 0.008011 | 0
E130 | 0.0073 | 0.0076 | 0.00691 | 0.0075036 | 0.0075194 | 0.0074274 | 0.00734 | 0.007339 | 0.0075 | 0.0074578 | 0
E140 | 0.0064 | 0.0070601 | 0.00692 | 0.0065938 | 0.0065941 | 0.0065187 | 0.0064 | 0.006402 | 0.0065 | 0.0065668 | 0
E150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.0085152 | 0.0082272 | 0.0082 | 0.00821 | 0.0083 | 0.0083955 | 0
E160 | 0.0099 | 0.009701 | 0.0101 | 0.010069 | 0.010236 | 0.009969 | 0.00994 | 0.009946 | 0.0102 | 0.01024 | 0
E165 | 0.0092 | 0.0090039 | 0.00985 | 0.0093021 | 0.0095112 | 0.0092694 | 0.0092 | 0.009208 | 0.0093 | 0.0093667 | 0
E170 | 0.0105 | 0.010494 | 0.0107 | 0.010471 | 0.010525 | 0.010367 | 0.01045 | 0.010451 | 0.0106 | 0.01055 | 0
E180 | 0.0164 | 0.016614 | 0.0164 | 0.01631 | 0.016404 | 0.01619 | 0.01623 | 0.01623 | 0.0164 | 0.016161 | 0
E185 | 0.0162 | 0.016441 | 0.0171 | 0.016151 | 0.016279 | 0.016056 | 0.01605 | 0.016059 | 0.0162 | 0.016049 | 0
E190 | 0.0159 | 0.016254 | 0.0161 | 0.015921 | 0.015707 | 0.015796 | 0.0159 | 0.015891 | 0.016 | 0.015867 | 0
E195 | 0.0155 | 0.015764 | 0.0164 | 0.01547 | 0.015326 | 0.015368 | 0.01544 | 0.015439 | 0.0156 | 0.015464 | 0
E200 | 0.0111 | 0.010933 | 0.0115 | 0.011281 | 0.011281 | 0.011129 | 0.01109 | 0.011099 | 0.0114 | 0.011419 | 0
Maximum COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 2.407 | 2.4324 | 2.392 | 2.4017 | 2.4184 | 2.3889 | 0 | 2.3893 | 2.39 | 2.4051 | 0
E110 | 3.417 | 3.4626 | 3.357 | 3.4087 | 3.4553 | 3.3795 | 0 | 3.3783 | 3.38 | 3.4022 | 0
E120 | 3.625 | 3.6153 | 3.596 | 3.6054 | 3.6541 | 3.5865 | 0 | 3.5941 | 3.59 | 3.609 | 0
E130 | 1.961 | 1.9809 | 1.923 | 1.9198 | 2.0033 | 1.8895 | 0 | 1.9079 | 1.91 | 1.9053 | 0
E140 | 2.882 | 2.9278 | 2.833 | 2.7974 | 2.8848 | 2.7502 | 0 | 2.7701 | 2.77 | 2.7735 | 0
E150 | 3.709 | 3.6706 | 3.63 | 3.6496 | 3.6952 | 3.6273 | 0 | 3.6295 | 3.63 | 3.6619 | 0
E160 | 3.957 | 3.8682 | 3.85 | 3.8452 | 3.8606 | 3.8329 | 0 | 3.838 | 3.84 | 3.8696 | 0
E165 | 2.989 | 2.9533 | 2.93 | 2.9257 | 2.9584 | 2.9295 | 0 | 2.9269 | 2.94 | 2.9486 | 0
E170 | 3.485 | 3.446 | 3.4 | 3.3944 | 3.4645 | 3.3672 | 0 | 3.3859 | 3.38 | 3.4067 | 0
E180 | 4.053 | 4.0893 | 4.05 | 4.0472 | 4.0754 | 4.0423 | 0 | 4.0442 | 4.05 | 4.062 | 0
E185 | 2.844 | 2.8778 | 2.85 | 2.8512 | 2.8622 | 2.8458 | 0 | 2.8485 | 2.86 | 2.8674 | 0
E190 | 3.489 | 3.5 | 3.45 | 3.4096 | 3.508 | 3.3865 | 0 | 3.4087 | 3.41 | 3.4737 | 0
E195 | 2.36 | 2.3681 | 2.33 | 2.3158 | 2.4571 | 2.2944 | 0 | 2.3143 | 2.31 | 2.4165 | 0
E200 | 3.717 | 3.6716 | 3.61 | 3.6102 | 3.6102 | 3.6206 | 0 | 3.6173 | 3.63 | 3.6553 | 0
Max IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 22.3333 | 22.3 | 22.2 | 22.2 | 23.21 | 22.2 | 0 | 22.235 | 22.2 | 22.1999 | 0
E110 | 22.2778 | 22.3 | 22.2 | 22.2 | 23.06 | 22.2 | 0 | 22.235 | 22.2 | 22.1999 | 0
E120 | 26.7222 | 26.8 | 26.7 | 26.7 | 28.26 | 26.7 | 0 | 26.735 | 26.7 | 26.7 | 0
E130 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 | 0 | 22.202 | 22.2 | 22.2 | 0
E140 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 | 0 | 22.202 | 22.2 | 22.2 | 0
E150 | 22.3333 | 22.3 | 22.2 | 22.2 | 23.28 | 22.2 | 0 | 22.235 | 22.2 | 22.178 | 0
E160 | 26.7222 | 26.8 | 26.7 | 26.7 | 27.61 | 26.7 | 0 | 26.735 | 26.7 | 26.6748 | 0
E165 | 23.4444 | 23.4 | 22.2 | 23.3 | 24.48 | 23.3 | 0 | 23.335 | 23.3 | 23.2806 | 0
E170 | 22.2222 | 22.2 | 22.2 | 22.2 | 22.67 | 22.2 | 0 | 22.214 | 22.2 | 22.1815 | 0
E180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.79 | 22.2 | 0 | 22.214 | 22.2 | 22.1581 | 0
E185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.61 | 22.2 | 0 | 22.214 | 22.2 | 22.1678 | 0
E190 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.25 | 22.2 | 0 | 22.202 | 22.2 | 22.1946 | 0
E195 | 22.1111 | 22.1 | 22.2 | 22.2 | 22.26 | 22.2 | 0 | 22.202 | 22.2 | 22.1957 | 0
E200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.73 | 26.7 | 0 | 26.713 | 26.7 | 26.6635 | 0
Max Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0.0074 | 0.0076 | 0.00699 | 0.0075036 | 0.007509 | 0.0074274 | 0 | 0.007339 | 0.0075 | 0.0074522 | 0
E110 | 0.0064 | 0.0071 | 0.00699 | 0.0065938 | 0.006631 | 0.0065187 | 0 | 0.006411 | 0.0066 | 0.0065611 | 0
E120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.007952 | 0.0078783 | 0 | 0.007873 | 0.008 | 0.008011 | 0
E130 | 0.0073 | 0.0076 | 0.00691 | 0.0075036 | 0.007519 | 0.0074274 | 0 | 0.007339 | 0.0075 | 0.0074578 | 0
E140 | 0.0064 | 0.0071 | 0.00692 | 0.0065938 | 0.006594 | 0.0065187 | 0 | 0.006402 | 0.0065 | 0.0065668 | 0
E150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.008566 | 0.0082272 | 0 | 0.008212 | 0.0084 | 0.0084158 | 0
E160 | 0.0099 | 0.0098 | 0.0101 | 0.010069 | 0.01029 | 0.009969 | 0 | 0.009948 | 0.0103 | 0.010269 | 0
E165 | 0.0092 | 0.0091 | 0.00985 | 0.0093021 | 0.009553 | 0.0092694 | 0 | 0.00921 | 0.0094 | 0.00939 | 0
E170 | 0.0105 | 0.0105 | 0.0107 | 0.010471 | 0.01065 | 0.010367 | 0 | 0.010454 | 0.106 | 0.010582 | 0
E180 | 0.0165 | 0.0167 | 0.0164 | 0.01631 | 0.01679 | 0.01619 | 0 | 0.016237 | 0.0165 | 0.0162 | 0
E185 | 0.0163 | 0.0166 | 0.0171 | 0.016151 | 0.01648 | 0.016056 | 0 | 0.016065 | 0.0163 | 0.016117 | 0
E190 | 0.0161 | 0.0164 | 0.0161 | 0.015921 | 0.01595 | 0.015796 | 0 | 0.015897 | 0.016 | 0.016105 | 0
E195 | 0.0156 | 0.0159 | 0.0165 | 0.01547 | 0.01551 | 0.015368 | 0 | 0.015444 | 0.0156 | 0.015907 | 0
E200 | 0.0111 | 0.011 | 0.0115 | 0.011281 | 0.01128 | 0.011129 | 0 | 0.011099 | 0.0115 | 0.011447 | 0
Minimum COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 2.404 | 2.4287 | 2.39 | 2.4017 | 2.4184 | 2.3889 | 0 | 2.389 | 2.39 | 2.3974 | 0
E110 | 3.413 | 3.4566 | 3.322 | 3.4087 | 3.419 | 3.3795 | 0 | 3.377 | 3.38 | 3.3935 | 0
E120 | 3.621 | 3.6124 | 3.583 | 3.6054 | 3.6095 | 3.5865 | 0 | 3.593 | 3.59 | 3.5998 | 0
E130 | 1.944 | 1.956 | 1.85 | 1.9198 | 1.6737 | 1.8895 | 0 | 1.908 | 1.91 | 1.897 | 0
E140 | 2.828 | 2.8958 | 2.68 | 2.7974 | 2.3127 | 2.7502 | 0 | 2.77 | 2.77 | 2.7637 | 0
E150 | 3.691 | 3.6652 | 3.62 | 3.6496 | 3.6611 | 3.6273 | 0 | 3.626 | 3.62 | 3.6428 | 0
E160 | 3.944 | 3.8641 | 3.83 | 3.8452 | 3.8212 | 3.8329 | 0 | 3.837 | 3.83 | 3.8476 | 0
E165 | 2.981 | 2.9498 | 2.92 | 2.9257 | 2.9336 | 2.9295 | 0 | 2.926 | 2.91 | 2.9309 | 0
E170 | 3.471 | 3.4386 | 3.38 | 3.3944 | 3.3167 | 3.3672 | 0 | 3.385 | 3.38 | 3.3792 | 0
E180 | 4.014 | 4.0798 | 4.04 | 4.0472 | 4.028 | 4.0423 | 0 | 4.044 | 4.03 | 4.0206 | 0
E185 | 2.815 | 2.871 | 2.84 | 2.8512 | 2.8362 | 2.8458 | 0 | 2.848 | 2.84 | 2.8341 | 0
E190 | 3.424 | 3.475 | 3.37 | 3.4096 | 3.1652 | 3.3865 | 0 | 3.409 | 3.41 | 3.3365 | 0
E195 | 2.321 | 2.3497 | 2.29 | 2.3158 | 2.2587 | 2.2944 | 0 | 2.314 | 2.31 | 2.2341 | 0
E200 | 3.698 | 3.6716 | 3.61 | 3.6102 | 3.6102 | 3.6206 | 0 | 3.617 | 3.61 | 3.6334 | 0
Min IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.09 | 22.2 | 0 | 22.197 | 22.2 | 22.1999 | 0
E110 | 22.2778 | 22.3 | 22.2 | 22.2 | 21.98 | 22.2 | 0 | 22.193 | 22.2 | 22.1999 | 0
E120 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.17 | 26.7 | 0 | 26.689 | 26.7 | 26.7 | 0
E130 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.03 | 22.2 | 0 | 22.172 | 22.2 | 22.2 | 0
E140 | 22.1111 | 22.1 | 22.2 | 22.2 | 20.76 | 22.2 | 0 | 22.168 | 22.2 | 22.2 | 0
E150 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.06 | 22.2 | 0 | 22.197 | 22.2 | 22.176 | 0
E160 | 26.7222 | 26.8 | 26.7 | 26.7 | 26.39 | 26.7 | 0 | 26.693 | 26.7 | 26.6697 | 0
E165 | 23.4444 | 23.4 | 22.2 | 23.3 | 23.26 | 23.3 | 0 | 23.299 | 23.3 | 23.2741 | 0
E170 | 22.2222 | 22.2 | 22.2 | 22.2 | 21.57 | 22.2 | 0 | 22.185 | 22.2 | 22.1799 | 0
E180 | 22.2778 | 22.3 | 22.2 | 22.2 | 22.01 | 22.2 | 0 | 22.196 | 22.2 | 22.1548 | 0
E185 | 22.3333 | 22.3 | 22.2 | 22.2 | 22.13 | 22.2 | 0 | 22.198 | 22.2 | 22.1627 | 0
E190 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.63 | 22.2 | 0 | 22.186 | 22.2 | 22.1943 | 0
E195 | 22.1111 | 22.1 | 22.2 | 22.2 | 21.76 | 22.2 | 0 | 22.188 | 22.2 | 22.1953 | 0
E200 | 26.7778 | 26.8 | 26.7 | 26.7339 | 26.73 | 26.7 | 0 | 26.713 | 26.7 | 26.6613 | 0
Min Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0.0074 | 0.0076 | 0.00684 | 0.0075036 | 0.007509 | 0.0074274 | 0 | 0.007339 | 0.0075 | 0.0074522 | 0
E110 | 0.0064 | 0.007 | 0.00684 | 0.0065938 | 0.006631 | 0.0065187 | 0 | 0.006411 | 0.0066 | 0.0065611 | 0
E120 | 0.0078 | 0.0078 | 0.007 | 0.0079506 | 0.007952 | 0.0078783 | 0 | 0.007873 | 0.008 | 0.008011 | 0
E130 | 0.0073 | 0.0076 | 0.00684 | 0.0075036 | 0.007519 | 0.0074274 | 0 | 0.007339 | 0.0075 | 0.0074578 | 0
E140 | 0.0064 | 0.007 | 0.00684 | 0.0065938 | 0.006594 | 0.0065187 | 0 | 0.006402 | 0.0065 | 0.0065668 | 0
E150 | 0.0083 | 0.0082 | 0.00853 | 0.0083236 | 0.008454 | 0.0082272 | 0 | 0.008209 | 0.0083 | 0.0083239 | 0
E160 | 0.0098 | 0.0097 | 0.0101 | 0.010069 | 0.01018 | 0.009969 | 0 | 0.009944 | 0.0101 | 0.010152 | 0
E165 | 0.0092 | 0.009 | 0.00984 | 0.0093021 | 0.009434 | 0.0092694 | 0 | 0.009207 | 0.0093 | 0.0092854 | 0
E170 | 0.0105 | 0.0104 | 0.0107 | 0.010471 | 0.0104 | 0.010367 | 0 | 0.010448 | 0.106 | 0.010465 | 0
E180 | 0.0163 | 0.0165 | 0.0164 | 0.01631 | 0.01613 | 0.01619 | 0 | 0.016222 | 0.0162 | 0.016042 | 0
E185 | 0.0161 | 0.0163 | 0.017 | 0.016151 | 0.01608 | 0.016056 | 0 | 0.016052 | 0.0161 | 0.015924 | 0
E190 | 0.0158 | 0.0161 | 0.0161 | 0.015921 | 0.01546 | 0.015796 | 0 | 0.015885 | 0.016 | 0.015709 | 0
E195 | 0.0153 | 0.0156 | 0.0164 | 0.01547 | 0.01514 | 0.015368 | 0 | 0.015434 | 0.0156 | 0.015299 | 0
E200 | 0.011 | 0.0109 | 0.0115 | 0.011281 | 0.01128 | 0.011129 | 0 | 0.011099 | 0.0113 | 0.011322 | 0
Deltas begin around row 500
Delta Calcs
(Max - Min)/Mean COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | Software
E100 | 0.0012467 | 0.0015062 | 0.00083717 | 0 | 0 | 0 | 0 | 0.00012552 | 0 | 0.0031826 | #DIV/0!
E110 | 0.0011714 | 0.0017378 | 0.010473 | 0 | 0.010592 | 0 | 0 | 0.00038462 | 0 | 0.0025513 | #DIV/0!
E120 | 0.0011041 | 0.00079758 | 0.0036212 | 0 | 0.012271 | 0 | 0 | 0.00030641 | 0 | 0.0025503 | #DIV/0!
E130 | 0.0087046 | 0.012602 | 0.03824 | 0 | 0.17198 | 0 | 0 | -5.2356e-05 | 0 | 0.0043691 | #DIV/0!
E140 | 0.018921 | 0.010989 | 0.055962 | 0 | 0.20433 | 0 | 0 | 3.6101e-05 | 0 | 0.003545 | #DIV/0!
E150 | 0.0048649 | 0.0014674 | 0.0027548 | 0 | 0.0092759 | 0 | 0 | 0.00096419 | 0.0027624 | 0.0052381 | #DIV/0!
E160 | 0.0032911 | 0.0010614 | 0.0052083 | 0 | 0.010193 | 0 | 0 | 0.00026042 | 0.0026042 | 0.0057024 | #DIV/0!
E165 | 0.0026798 | 0.0012002 | 0.0034247 | 0 | 0.0084429 | 0 | 0 | 0.00030717 | 0.010274 | 0.006025 | #DIV/0!
E170 | 0.0040265 | 0.0021466 | 0.0058997 | 0 | 0.043444 | 0 | 0 | 0.00026549 | 0 | 0.0081135 | #DIV/0!
E180 | 0.009687 | 0.0023307 | 0.0024752 | 0 | 0.011687 | 0 | 0 | 4.9505e-05 | 0.0049505 | 0.010241 | #DIV/0!
E185 | 0.010273 | 0.0023597 | 0.0035088 | 0 | 0.0091078 | 0 | 0 | 0.00017544 | 0.0070175 | 0.011693 | #DIV/0!
E190 | 0.018802 | 0.0071705 | 0.02346 | 0 | 0.10066 | 0 | 0 | -8.7977e-05 | 0 | 0.040402 | #DIV/0!
E195 | 0.016688 | 0.0078108 | 0.017316 | 0 | 0.08606 | 0 | 0 | 0.00012987 | 0 | 0.079144 | #DIV/0!
E200 | 0.0051241 | -1.2839e-05 | 0 | 0 | 0 | 0 | 0 | 8.2873e-05 | 0.0055249 | 0.0060171 | #DIV/0!
(Max - Min)/Mean IDB (°C)
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your Data
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | software
E100 | 0 | 0 | 0 | 0 | 0.049482 | 0 | 0 | 0.0017105 | 0 | 7.6728e-07 | #DIV/0!
E110 | 0 | 0 | 0 | 0 | 0.047948 | 0 | 0 | 0.0018907 | 0 | 3.9213e-07 | #DIV/0!
E120 | 0 | 0 | 0 | 0 | 0.077183 | 0 | 0 | 0.0017221 | 0 | 2.5833e-09 | #DIV/0!
E130 | 0 | 0 | 0 | 0 | 0.056383 | 0 | 0 | 0.0013521 | 0 | 2.8008e-09 | #DIV/0!
E140 | 0 | 0 | 0 | 0 | 0.069271 | 0 | 0 | 0.0015326 | 0 | 1.0566e-09 | #DIV/0!
E150 | 0 | 0 | 0 | 0 | 0.053799 | 0 | 0 | 0.0017105 | 0 | 9.1726e-05 | #DIV/0!
E160 | 0 | 0 | 0 | 0 | 0.045194 | 0 | 0 | 0.0015722 | 0 | 0.00019269 | #DIV/0!
E165 | 0 | 0 | 0 | 0 | 0.051303 | 0 | 0 | 0.0015439 | 0 | 0.00027951 | #DIV/0!
E170 | 0 | 0 | 0 | 0 | 0.049736 | 0 | 0 | 0.0013064 | 0 | 7.1143e-05 | #DIV/0!
E180 | 0 | 0 | 0 | 0 | 0.034924 | 0 | 0 | 0.00081063 | 0 | 0.00014949 | #DIV/0!
E185 | 0 | 0 | 0 | 0 | 0.021459 | 0 | 0 | 0.00072053 | 0 | 0.00022693 | #DIV/0!
E190 | 0 | 0 | 0 | 0 | 0.02825 | 0 | 0 | 0.00072092 | 0 | 1.2134e-05 | #DIV/0!
E195 | 0 | 0 | 0 | 0 | 0.022716 | 0 | 0 | 0.00063077 | 0 | 1.7277e-05 | #DIV/0!
E200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3697e-05 | #DIV/0!
(Max - Min)/Mean Humidity Ratio
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your Data
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | software
E100 | 0 | 0 | 0.021708 | 0 | 0 | 0 | 0 | 0 | 0 | 4.0271e-14 | #DIV/0!
E110 | 0 | 0.014226 | 0.021676 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4154e-14 | #DIV/0!
E120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.88e-14 | #DIV/0!
E130 | 0 | 0 | 0.01013 | 0 | 0 | 0 | 0 | 0 | 0 | 1.006e-13 | #DIV/0!
E140 | 0 | 0.014164 | 0.011561 | 0 | 0 | 0 | 0 | 0 | 0 | 8.374e-14 | #DIV/0!
E150 | 0 | 0 | 0 | 0 | 0.013153 | 0 | 0 | 0.00036541 | 0.012048 | 0.010954 | #DIV/0!
E160 | 0.010101 | 0.010308 | 0 | 0 | 0.010747 | 0 | 0 | 0.00040217 | 0.019608 | 0.011333 | #DIV/0!
E165 | 0 | 0.011106 | 0.0010152 | 0 | 0.012512 | 0 | 0 | 0.0003258 | 0.010753 | 0.011171 | #DIV/0!
E170 | 0 | 0.0095289 | 0 | 0 | 0.023752 | 0 | 0 | 0.00057411 | 0 | 0.011126 | #DIV/0!
E180 | 0.012195 | 0.012038 | 0 | 0 | 0.040234 | 0 | 0 | 0.00092421 | 0.018293 | 0.0097718 | #DIV/0!
E185 | 0.012346 | 0.018247 | 0.005848 | 0 | 0.024571 | 0 | 0 | 0.00080951 | 0.012346 | 0.012009 | #DIV/0!
E190 | 0.018868 | 0.018457 | 0 | 0 | 0.031196 | 0 | 0 | 0.00075514 | 0 | 0.024976 | #DIV/0!
E195 | 0.019355 | 0.01903 | 0.0060976 | 0 | 0.024142 | 0 | 0 | 0.00064771 | 0 | 0.039296 | #DIV/0!
E200 | 0.009009 | 0.0091467 | 0 | 0 | 0 | 0 | 0 | 0 | 0.017544 | 0.010952 | #DIV/0!
Delta COP
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your Data
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | software
E110-E100 | 1.0082 | 1.0285 | 0.953 | 1.0069 | 1.0087 | 0.99059 | 0.99 | 0.99 | 0.99 | 0.99634 | 0
E120-E110 | 0.20837 | 0.155 | 0.248 | 0.19677 | 0.20416 | 0.20704 | 0.21 | 0.21 | 0.21 | 0.2066 | 0
E120-E100 | 1.2166 | 1.1835 | 1.201 | 1.2037 | 1.2129 | 1.1976 | 1.2 | 1.2 | 1.2 | 1.2029 | 0
E130-E100 | -0.45341 | -0.4552 | -0.48 | -0.48198 | -0.50212 | -0.49937 | -0.48 | -0.48 | -0.48 | -0.50009 | 0
E140-E130 | 0.901 | 0.9399 | 0.825 | 0.87767 | 0.88334 | 0.86071 | 0.86 | 0.86 | 0.86 | 0.86717 | 0
E140-E110 | -0.56063 | -0.5438 | -0.608 | -0.61124 | -0.6275 | -0.62925 | -0.61 | -0.61 | -0.61 | -0.62926 | 0
E150-E110 | 0.28537 | 0.2086 | 0.288 | 0.24097 | 0.24631 | 0.24783 | 0.25 | 0.25 | 0.24 | 0.2531 | 0
E160-E150 | 0.25 | 0.1983 | 0.21 | 0.19555 | 0.18654 | 0.20563 | 0.21 | 0.21 | 0.22 | 0.20639 | 0
E165-E160 | -0.96474 | -0.9144 | -0.92 | -0.91948 | -0.91505 | -0.90343 | -0.91 | -0.91 | -0.92 | -0.91897 | 0
E170-E150 | -0.223 | -0.2252 | -0.24 | -0.25525 | -0.27013 | -0.26014 | -0.24 | -0.24 | -0.24 | -0.25878 | 0
E180-E150 | 0.326 | 0.4167 | 0.41 | 0.39757 | 0.38162 | 0.41502 | 0.41 | 0.41 | 0.42 | 0.3891 | 0
E180-E170 | 0.549 | 0.6419 | 0.65 | 0.65282 | 0.65175 | 0.67516 | 0.65 | 0.65 | 0.66 | 0.64788 | 0
E185-E180 | -1.203 | -1.2098 | -1.19 | -1.196 | -1.1976 | -1.1965 | -1.19 | -1.19 | -1.19 | -1.1904 | 0
E190-E180 | -0.569 | -0.5977 | -0.63 | -0.63762 | -0.65027 | -0.65583 | -0.63 | -0.63 | -0.63 | -0.64659 | 0
E190-E140 | 0.603 | 0.5714 | 0.676 | 0.61216 | 0.60515 | 0.63627 | 0.64 | 0.64 | 0.64 | 0.62487 | 0
E195-E190 | -1.12 | -1.1267 | -1.1 | -1.0938 | -1.0994 | -1.0921 | -1.1 | -1.1 | -1.1 | -1.0909 | 0
E195-E185 | -0.48603 | -0.5146 | -0.54 | -0.53547 | -0.55209 | -0.55141 | -0.54 | -0.54 | -0.54 | -0.54708 | 0
E195-E130 | 0.384 | 0.3846 | 0.401 | 0.39602 | 0.3891 | 0.40487 | 0.4 | 0.4 | 0.4 | 0.40112 | 0
E200-E100 | 1.3016 | 1.2373 | 1.221 | 1.2084 | 1.1918 | 1.2317 | 1.23 | 1.23 | 1.23 | 1.2417 | 0
Delta Qtot
| DOE2.1E | DOE2.1E | C2000 | TRNSYS 14.2 | TRNSYS 14.2 | Analyitic | Analyitic | Analyitic | CA-SIS | E+ | Your Data
| NREL | CIEM/0800 | EDF-12/00 | TUD-ideal | TUD-real | TUD-8/00 | HTAL1 | HTAL2 | EDF-1000 | US-0401 | software
E110-E100 | -454 | -459.621 | -441 | -455.3055 | -449.9711 | -454.3131 | -453.6 | -453.2 | -454 | -450.8529 | 0
E120-E110 | -62 | -50.092 | -77 | -59.6584 | -60.3021 | -63.5575 | -66.2 | -66.4 | -65 | -62.6934 | 0
E120-E100 | -516 | -509.713 | -518 | -514.9639 | -510.2732 | -517.8706 | -519.8 | -519.6 | -519 | -513.5463 | 0
E130-E100 | -1413 | -1415.398 | -1421 | -1413.5415 | -1401.8208 | -1419.9663 | -1421.3 | -1421.1 | -1421 | -1412.0645 | 0
E140-E130 | -40 | -40.411 | -40 | -40.9605 | -41.4733 | -41.5864 | -41 | -41.2 | -42 | -40.3501 | 0
E140-E110 | -999 | -996.188 | -1020 | -999.1966 | -993.323 | -1007.2396 | -1008.7 | -1009.1 | -1009 | -1001.5617 | 0
E150-E110 | 118 | 141.228 | 118 | 132.0944 | 129.6472 | 130.2551 | 129.3 | 129.1 | 131 | 128.2886 | 0
E160-E150 | -76 | -64.794 | -68 | -62.3216 | -58.7295 | -66.05 | -67.2 | -67.6 | -68 | -65.3881 | 0
E165-E160 | 363 | 361.817 | 362 | 362.977 | 357.0433 | 357.3902 | 360.4 | 360.7 | 362 | 359.356 | 0
E170-E150 | -563 | -573.348 | -569 | -563.1461 | -555.7842 | -565.3727 | -568.8 | -568.7 | -570 | -562.1205 | 0
E180-E150 | -103 | -125.315 | -125 | -117.7844 | -111.5753 | -123.824 | -124.2 | -124.6 | -125 | -115.294 | 0
E180-E170 | 460 | 448.033 | 444 | 445.3617 | 444.2089 | 441.5487 | 444.6 | 444.1 | 445 | 446.8265 | 0
E185-E180 | 467 | 464.046 | 461 | 460.255 | 458.3596 | 461.9737 | 461.1 | 461 | 461 | 458.2115 | 0
E190-E180 | -920 | -916.89 | -918 | -917.2731 | -914.9174 | -917.493 | -918.2 | -917.7 | -919 | -918.1623 | 0
E190-E140 | 94 | 95.211 | 95 | 96.2334 | 96.4774 | 96.1777 | 95.6 | 95.9 | 96 | 96.394 | 0
E195-E190 | 86 | 84.7 | 86 | 85.7346 | 86.4597 | 86.9875 | 85.9 | 85.8 | 86 | 85.546 | 0
E195-E185 | -1301 | -1296.236 | -1293 | -1291.7935 | -1286.8173 | -1292.4792 | -1293.4 | -1292.9 | -1294 | -1290.8277 | 0
E195-E130 | 140 | 139.5 | 141 | 141.0075 | 141.4638 | 141.5788 | 140.5 | 140.5 | 140 | 141.5899 | 0
E200-E100 | -79 | -52.603 | -66 | -42.2735 | -31.9443 | -54.7376 | -53.4 | -53.5 | -54 | -54.8104 | 0
Del Qcomp | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | -428 | -441.592 | -419 | -431.8474 | -426.8936 | -430.9138 | -429.8 | -429.5 | -430 | 0 | 0
E120-E110 | -45 | -15.798 | -59 | -43.4717 | -43.903 | -47.0715 | -50.1 | -50.2 | -49 | 0 | 0
E120-E100 | -473 | -457.39 | -478 | -475.319 | -470.7965 | -477.9853 | -479.9 | -479.7 | -479 | 0 | 0
E130-E100 | -1218 | -1214.26 | -1224 | -1217.5188 | -1207.8769 | -1223.5648 | -1224.6 | -1224.6 | -1224 | 0 | 0
E140-E130 | -37 | -38.399 | -37 | -37.8005 | -38.2753 | -38.3628 | -37.9 | -37.9 | -38 | 0 | 0
E140-E110 | -827 | -811.067 | -842 | -823.472 | -819.2586 | -831.0138 | -832.7 | -833 | -832 | 0 | 0
E150-E110 | 99 | 141.228 | 100 | 112.7146 | 110.9181 | 111.0199 | 110 | 109.8 | 111 | 0 | 0
E160-E150 | -56 | -44.419 | -50 | -45.0374 | -42.3919 | -48.5466 | -49.8 | -50.1 | -50 | 0 | 0
E165-E160 | 330 | 328.567 | 332 | 333.2246 | 328.108 | 328.3094 | 330.8 | 331.1 | 333 | 0 | 0
E170-E150 | -459 | -468.135 | -469 | -463.6356 | -458.1666 | -465.9883 | -469.2 | -469.1 | -469 | 0 | 0
E180-E150 | -70 | -92.832 | -91 | -84.887 | -80.3105 | -90.836 | -91.2 | -91.5 | -91 | 0 | 0
E180-E170 | 389 | 375.303 | 378 | 378.7486 | 377.8561 | 375.1523 | 378 | 377.6 | 378 | 0 | 0
E185-E180 | 432 | 428.419 | 431 | 429.7507 | 427.9509 | 431.6779 | 430.6 | 430.5 | 431 | 0 | 0
E190-E180 | -774 | -774.839 | -770 | -769.6356 | -767.9826 | -769.6508 | -770.4 | -770 | -771 | 0 | 0
E190-E140 | 82 | 84.624 | 81 | 81.6639 | 81.8837 | 81.5469 | 81.1 | 81.3 | 81 | 0 | 0
E195-E190 | 79 | 79.444 | 79 | 78.9721 | 79.6337 | 80.1527 | 79.2 | 79.1 | 79 | 0 | 0
E195-E185 | -1127 | -1123.814 | -1122 | -1120.4142 | -1116.2999 | -1121.176 | -1121.8 | -1121.4 | -1123 | 0 | 0
E195-E130 | 124 | 125.669 | 123 | 122.8356 | 123.242 | 123.3368 | 122.4 | 122.5 | 122 | 0 | 0
E200-E100 | -93 | -58.431 | -79 | -58.3094 | -49.8691 | -70.0317 | -68.8 | -68.9 | -69 | 0 | 0
Del Q IDfan | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | -19 | -12.268 | -15 | -15.9627 | -15.7035 | -15.9226 | -16.2 | -16.1 | -16 | -15.9921 | 0
E120-E110 | -12 | -23.336 | -12 | -11.0148 | -11.1592 | -11.2183 | -11 | -11 | -11 | -11.1547 | 0
E120-E100 | -31 | -35.604 | -27 | -26.9774 | -26.8627 | -27.1409 | -27.2 | -27.1 | -27 | -27.1468 | 0
E130-E100 | -133 | -136.869 | -134 | -133.3883 | -131.9736 | -133.646 | -133.8 | -133.7 | -134 | -133.3733 | 0
E140-E130 | -2 | -1.369 | -2 | -2.1503 | -2.1761 | -2.1936 | -2.2 | -2.2 | -2 | -2.1259 | 0
E140-E110 | -116 | -125.97 | -121 | -119.5759 | -118.4462 | -119.917 | -119.8 | -119.8 | -120 | -119.5071 | 0
E150-E110 | 14 | 0 | 12 | 13.1873 | 12.7446 | 13.0891 | 13.2 | 13.2 | 13 | 12.757 | 0
E160-E150 | -15 | -13.865 | -12 | -11.7613 | -11.1173 | -11.9106 | -11.9 | -11.9 | -12 | -11.9691 | 0
E165-E160 | 24 | 22.626 | 21 | 20.246 | 19.6897 | 19.7887 | 20.1 | 20.1 | 20 | 20.2354 | 0
E170-E150 | -73 | -71.595 | -68 | -67.7141 | -66.4261 | -67.6284 | -67.9 | -67.9 | -68 | -67.3106 | 0
E180-E150 | -24 | -22.104 | -22 | -22.3857 | -21.2749 | -22.4474 | -22.5 | -22.6 | -23 | -21.8861 | 0
E180-E170 | 49 | 49.491 | 46 | 45.3284 | 45.1513 | 45.181 | 45.4 | 45.3 | 45 | 45.4245 | 0
E185-E180 | 25 | 24.243 | 20 | 20.7574 | 20.6923 | 20.6154 | 20.8 | 20.8 | 21 | 20.6754 | 0
E190-E180 | -98 | -96.662 | -101 | -100.4635 | -99.9852 | -100.6027 | -100.6 | -100.5 | -100 | -100.4513 | 0
E190-E140 | 8 | 7.204 | 10 | 9.9142 | 9.9306 | 9.9559 | 9.9 | 9.9 | 10 | 9.9268 | 0
E195-E190 | 4 | 3.577 | 5 | 4.6017 | 4.6449 | 4.6509 | 4.6 | 4.6 | 5 | 4.5989 | 0
E195-E185 | -119 | -117.328 | -116 | -116.6191 | -116.0326 | -116.5672 | -116.8 | -116.7 | -116 | -116.5278 | 0
E195-E130 | 10 | 9.412 | 13 | 12.3655 | 12.3994 | 12.4132 | 12.3 | 12.3 | 13 | 12.3997 | 0
E200-E100 | 10 | 3.966 | 9 | 10.9119 | 12.1975 | 10.4073 | 10.5 | 10.6 | 10 | 9.9058 | 0
Del Q ODfan | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | -7 | -5.761 | -7 | -7.4954 | -7.374 | -7.4767 | -7.5 | -7.5 | -8 | 0 | 0
E120-E110 | -5 | -10.958 | -6 | -5.172 | -5.24 | -5.2677 | -5.2 | -5.2 | -5 | 0 | 0
E120-E100 | -12 | -16.719 | -13 | -12.6674 | -12.6139 | -12.7444 | -12.7 | -12.7 | -13 | 0 | 0
E130-E100 | -62 | -64.269 | -63 | -62.6344 | -61.9703 | -62.7555 | -62.8 | -62.8 | -63 | 0 | 0
E140-E130 | -1 | -0.643 | -1 | -1.0097 | -1.0218 | -1.03 | -1 | -1 | -1 | 0 | 0
E140-E110 | -56 | -59.151 | -57 | -56.1487 | -55.6182 | -56.3088 | -56.3 | -56.3 | -56 | 0 | 0
E150-E110 | 5 | 0 | 5 | 6.1925 | 5.9844 | 6.1462 | 6.2 | 6.1 | 6 | 0 | 0
E160-E150 | -5 | -6.51 | -5 | -5.5228 | -5.2203 | -5.5928 | -5.6 | -5.5 | -5 | 0 | 0
E165-E160 | 9 | 10.624 | 9 | 9.5064 | 9.2456 | 9.2921 | 9.4 | 9.4 | 9 | 0 | 0
E170-E150 | -31 | -33.618 | -32 | -31.7964 | -31.1915 | -31.756 | -31.9 | -31.8 | -32 | 0 | 0
E180-E150 | -9 | -10.379 | -10 | -10.5117 | -9.99 | -10.5405 | -10.6 | -10.5 | -10 | 0 | 0
E180-E170 | 22 | 23.239 | 22 | 21.2847 | 21.2015 | 21.2154 | 21.3 | 21.3 | 22 | 0 | 0
E185-E180 | 10 | 11.384 | 9 | 9.7468 | 9.7164 | 9.6803 | 9.7 | 9.7 | 9 | 0 | 0
E190-E180 | -48 | -45.389 | -47 | -47.1741 | -46.9496 | -47.2395 | -47.2 | -47.2 | -48 | 0 | 0
E190-E140 | 4 | 3.383 | 5 | 4.6553 | 4.6631 | 4.6749 | 4.7 | 4.7 | 4 | 0 | 0
E195-E190 | 3 | 1.679 | 2 | 2.1608 | 2.1811 | 2.1839 | 2.1 | 2.1 | 3 | 0 | 0
E195-E185 | -55 | -55.094 | -54 | -54.7601 | -54.4849 | -54.7359 | -54.8 | -54.8 | -54 | 0 | 0
E195-E130 | 6 | 4.419 | 6 | 5.8064 | 5.8223 | 5.8288 | 5.8 | 5.8 | 6 | 0 | 0
E200-E100 | 4 | 1.862 | 4 | 5.124 | 5.7274 | 4.8869 | 5 | 5 | 5 | 0 | 0
Del Q coil,t | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | -38.3939 | -37.89 | -34 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | -35 | -34.0099 | 0
E120-E110 | -16.4127 | -40.1 | -17 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | -16 | -16.3058 | 0
E120-E100 | -54.8066 | -77.99 | -51 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | -51 | -50.3157 | 0
E130-E100 | -3578.8394 | -3625.692 | -3581 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | -3581 | -3580.7334 | 0
E140-E130 | -20.5158 | -20.248 | -21 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | -21 | -20.1438 | 0
E140-E110 | -3560.9613 | -3608.05 | -3568 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | -3567 | -3566.8672 | 0
E150-E110 | 771.9812 | 739.2 | 751 | 752.3846 | 751.7923 | 752.2836 | 752.4 | 753 | 752 | 745.6367 | 0
E160-E150 | -19.0504 | -26.402 | -17 | -16.9277 | -16.1469 | -16.9825 | -17.1 | -18.4 | -16 | -17.8067 | 0
E165-E160 | 40.4455 | 51.08 | 38 | 37.0003 | 36.2193 | 36.4531 | 37 | 38 | 37 | 37.3585 | 0
E170-E150 | -2291.0317 | -2316.723 | -2285 | -2285.3107 | -2283.394 | -2285.1847 | -2285.5 | -2285.8 | -2284 | -2283.9004 | 0
E180-E150 | 7.034 | -32.796 | -22 | -22.3843 | -20.9286 | -22.2623 | -22.5 | -24.5 | -22 | -27.5505 | 0
E180-E170 | 2298.0657 | 2283.927 | 2263 | 2262.9264 | 2262.4654 | 2262.9224 | 2263 | 2261.3 | 2262 | 2256.3499 | 0
E185-E180 | 48.0657 | 54.91 | 40 | 39.9168 | 39.8433 | 39.858 | 40 | 40.1 | 12 | 40.7328 | 0
E190-E180 | -3956.0375 | -3937.377 | -3918 | -3917.4227 | -3916.4296 | -3917.7372 | -3917.6 | -3916.1 | -3917 | -3906.9631 | 0
E190-E140 | 383.939 | 377.077 | 379 | 379.514 | 379.106 | 379.5607 | 379.4 | 380.4 | 380 | 377.9903 | 0
E195-E190 | 23.1536 | 22.633 | 24 | 23.7619 | 23.6687 | 23.8465 | 23.9 | 23.5 | 24 | 22.8387 | 0
E195-E185 | -3980.9496 | -3969.654 | -3934 | -3933.5775 | -3932.6042 | -3933.7487 | -3933.7 | -3932.7 | -3905 | -3924.8572 | 0
E195-E130 | 386.5768 | 379.462 | 382 | 381.9655 | 381.5695 | 382.0203 | 381.9 | 382 | 383 | 380.6852 | 0
E200-E100 | 1728.0188 | 1692.73 | 1636 | 1697.8282 | 1699.6157 | 1697.4409 | 1697.4 | 1697.4 | 1698 | 1687.1961 | 0
Del Q coil,s | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | -38.3939 | -37.89 | -34 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | -35 | -34.0099 | 0
E120-E110 | -16.4127 | -40.1 | -17 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | -16 | -16.3058 | 0
E120-E100 | -54.8066 | -77.99 | -51 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | -51 | -50.3157 | 0
E130-E100 | -3578.8394 | -3625.692 | -3581 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | -3581 | -3580.7334 | 0
E140-E130 | -20.5158 | -20.248 | -21 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | -21 | -20.1438 | 0
E140-E110 | -3560.9613 | -3608.05 | -3568 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | -3567 | -3566.8672 | 0
E150-E110 | 30.4807 | 0 | 12 | 13.1846 | 12.5854 | 13.088 | 13.2 | 13.7 | 13 | 6.4394 | 0
E160-E150 | -16.9988 | -26.402 | -17 | -16.9277 | -16.1348 | -17.0265 | -17.1 | -18.2 | -17 | -17.8067 | 0
E165-E160 | 39.5662 | 51.08 | 37 | 37.0003 | 36.2248 | 36.4472 | 37 | 37.8 | 37 | 37.3579 | 0
E170-E150 | -2288.3939 | -2316.723 | -2285 | -2285.3107 | -2283.3986 | -2285.3048 | -2285.5 | -2285.9 | -2285 | -2283.904 | 0
E180-E150 | -2179.3669 | -2250.396 | -2240 | -2239.9843 | -2238.5215 | -2240.5379 | -2240.1 | -2241.3 | -2241 | -2245.146 | 0
E180-E170 | 109.027 | 66.327 | 45 | 45.3264 | 44.8771 | 44.7669 | 45.4 | 44.6 | 44 | 38.758 | 0
E185-E180 | 46.0141 | 54.91 | 40 | 39.9168 | 39.8232 | 39.8069 | 40 | 40 | 11 | 40.7262 | 0
E190-E180 | -1394.49 | -1350.177 | -1330 | -1330.2227 | -1329.2766 | -1329.9815 | -1330.4 | -1329.8 | -1329 | -1319.7742 | 0
E190-E140 | 17.585 | 7.477 | 10 | 9.914 | 9.4592 | 9.8452 | 9.8 | 10.6 | 10 | 8.3865 | 0
E195-E190 | 22.8605 | 22.633 | 24 | 23.7619 | 23.71 | 23.8326 | 23.9 | 23.7 | 24 | 22.8205 | 0
E195-E185 | -1417.6436 | -1382.454 | -1346 | -1346.3775 | -1345.3897 | -1345.9558 | -1346.5 | -1346.1 | -1316 | -1337.68 | 0
E195-E130 | 19.9297 | 9.862 | 13 | 12.3655 | 11.964 | 12.2909 | 12.3 | 12.4 | 13 | 11.0631 | 0
E200-E100 | 508.7925 | 471.706 | 415 | 476.8042 | 478.5917 | 476.3346 | 476.4 | 476.4 | 476 | 466.2125 | 0
Del Qcoil,lat | DOE2/N | DOE2/C | C2000 | TRN-id | TRN-re | An-TUD | An-HTAL1 | An-HTAL2 | CA-SIS | E+ | Your Data
E110-E100 | 0 | 0 | 0 | 0 | -3.0447e-14 | 0 | 0 | 0 | 0 | 0 | 0
E120-E110 | 0 | 0 | 0 | 0 | 1.1191e-15 | 0 | 0 | 0 | 0 | 0 | 0
E120-E100 | 0 | 0 | 0 | 0 | -2.9328e-14 | 0 | 0 | 0 | 0 | 0 | 0
E130-E100 | 0 | 0 | 0 | 0 | -1.7231e-15 | 0 | 0 | 0 | 0 | 0 | 0
E140-E130 | 0 | 0 | 0 | 0 | -3.169e-14 | 0 | 0 | 0 | 0 | 0 | 0
E140-E110 | 0 | 0 | 0 | 0 | -2.9665e-15 | 0 | 0 | 0 | 0 | 0 | 0
E150-E110 | 741.5006 | 739.2 | 739 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 739 | 739.1972 | 0
E160-E150 | -2.0516 | 0 | 0 | 0 | -0.01221 | 0.043984 | 0 | -0.3 | 1 | -2.4939e-05 | 0
E165-E160 | 0.87925 | 0 | 0 | 0 | -0.00548 | 0.005862 | 0 | 0.2 | 0 | 0.00055101 | 0
E170-E150 | -2.6377 | 0 | 0 | 0 | 0.00465 | 0.12011 | 0 | 0 | 1 | 0.0035566 | 0
E180-E150 | 2186.4009 | 2217.6 | 2218 | 2217.6 | 2217.5924 | 2218.2757 | 2217.6 | 2216.7 | 2219 | 2217.5955 | 0
E180-E170 | 2189.0387 | 2217.6 | 2218 | 2217.6 | 2217.5877 | 2218.1556 | 2217.6 | 2216.7 | 2218 | 2217.592 | 0
E185-E180 | 2.0516 | 0 | 0 | 0 | 0.02022 | 0.051109 | 0 | 0.1 | 1 | 0.0065461 | 0
E190-E180 | -2561.5475 | -2587.2 | -2587 | -2587.2 | -2587.1524 | -2587.7557 | -2587.2 | -2586.3 | -2588 | -2587.1889 | 0
E190-E140 | 366.354 | 369.6 | 370 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 370 | 369.6039 | 0
E195-E190 | 0.29308 | 0 | 0 | 0 | -0.041346 | 0.013833 | 0 | -0.2 | 0 | 0.018237 | 0
E195-E185 | -2563.306 | -2587.2 | -2587 | -2587.2 | -2587.214 | -2587.793 | -2587.2 | -2586.6 | -2589 | -2587.1772 | 0
E195-E130 | 366.6471 | 369.6 | 370 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 370 | 369.6221 | 0
E200-E100 | 1219.2263 | 1221 | 1221 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 1222 | 1220.9837 | 0

## YD
RESULTS5-3.XLS
Output spreadsheet for HVAC BESTEST
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Zone Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Zone Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100
E110
E120
E130
E140
E150
E160
E165
E170
E180
E185
E190
E195
E200

## B
d:\e\iea22\hvabtest\results\doe2\21EJNA2A.WK3, February 14, 2000
Output spreadsheet for HVAC BESTEST
DOE-2.1E by NREL.
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio | Qfan,heat | - Qfan | /Qfan | /Qcoil
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | (kWh) | (kWh) | (frac) | (frac)
E100 | 1519 | 1311 | 141 | 67 | 3793.9625 | 3793.9625 | 0 | 3655.3341 | 3655.3341 | 0 | 2.4064 | 22.3333 | 0.0074 | 2.407 | 22.3333 | 0.0074 | 2.404 | 22.3333 | 0.0074 | 138.6284 | -2.3716 | -0.017108 | -0.00062511
E110 | 1065 | 883 | 122 | 60 | 3755.5686 | 3755.5686 | 0 | 3636.5768 | 3636.5768 | 0 | 3.4146 | 22.2778 | 0.0064 | 3.417 | 22.2778 | 0.0064 | 3.413 | 22.2778 | 0.0064 | 118.9918 | -3.0082 | -0.025281 | -0.000801
E120 | 1003 | 838 | 110 | 55 | 3739.1559 | 3739.1559 | 0 | 3631.5944 | 3631.5944 | 0 | 3.623 | 26.7222 | 0.0078 | 3.625 | 26.7222 | 0.0078 | 3.621 | 26.7222 | 0.0078 | 107.5615 | -2.4385 | -0.02267 | -0.00065214
E130 | 106 | 93 | 8 | 5 | 215.1231 | 215.1231 | 0 | 207.5029 | 207.5029 | 0 | 1.953 | 22.1111 | 0.0073 | 1.961 | 22.1111 | 0.0073 | 1.944 | 22.1111 | 0.0073 | 7.6202 | -0.37984 | -0.049846 | -0.0017657
E140 | 66 | 56 | 6 | 4 | 194.6073 | 194.6073 | 0 | 188.4525 | 188.4525 | 0 | 2.854 | 22.1111 | 0.0064 | 2.882 | 22.1111 | 0.0064 | 2.828 | 22.1111 | 0.0064 | 6.1547 | 0.15475 | 0.025143 | 0.00079518
E150 | 1183 | 982 | 136 | 65 | 4527.5498 | 3786.0492 | 741.5006 | 4376.0258 | 3636.5768 | 739.449 | 3.7 | 22.3333 | 0.0083 | 3.709 | 22.3333 | 0.0083 | 3.691 | 22.3333 | 0.0083 | 149.4725 | 13.4725 | 0.090133 | 0.0029757
E160 | 1107 | 926 | 121 | 60 | 4508.4994 | 3769.0504 | 739.449 | 4371.0434 | 3631.5944 | 739.449 | 3.95 | 26.7222 | 0.0099 | 3.957 | 26.7222 | 0.0099 | 3.944 | 26.7222 | 0.0098 | 137.456 | 16.456 | 0.11972 | 0.00365
E165 | 1470 | 1256 | 145 | 69 | 4548.9449 | 3808.6166 | 740.3283 | 4387.456 | 3648.007 | 739.449 | 2.9853 | 23.4444 | 0.0092 | 2.989 | 23.4444 | 0.0092 | 2.981 | 23.4444 | 0.0092 | 160.6096 | 15.6096 | 0.09719 | 0.0034315
E170 | 620 | 523 | 63 | 34 | 2236.5182 | 1497.6553 | 738.8628 | 2157.9719 | 1418.5229 | 739.449 | 3.477 | 22.2222 | 0.0105 | 3.485 | 22.2222 | 0.0105 | 3.471 | 22.2222 | 0.0105 | 79.1325 | 16.1325 | 0.20387 | 0.0072132
E180 | 1080 | 912 | 112 | 56 | 4534.5838 | 1606.6823 | 2927.9015 | 4376.0258 | 1418.5229 | 2957.5029 | 4.026 | 22.2778 | 0.0164 | 4.053 | 22.2778 | 0.0165 | 4.014 | 22.2778 | 0.0163 | 188.1594 | 76.1594 | 0.40476 | 0.016795
E185 | 1547 | 1344 | 137 | 66 | 4582.6495 | 1652.6964 | 2929.9531 | 4394.7831 | 1437.2802 | 2957.5029 | 2.823 | 22.3333 | 0.0162 | 2.844 | 22.3333 | 0.0163 | 2.815 | 22.3333 | 0.0161 | 215.4162 | 78.4162 | 0.36402 | 0.017112
E190 | 160 | 138 | 14 | 8 | 578.5463 | 212.1923 | 366.354 | 558.0305 | 188.4525 | 369.578 | 3.457 | 22.1111 | 0.0159 | 3.489 | 22.1111 | 0.0161 | 3.424 | 22.1111 | 0.0158 | 23.7397 | 9.7397 | 0.41027 | 0.016835
E195 | 246 | 217 | 18 | 11 | 601.6999 | 235.0528 | 366.6471 | 577.0809 | 207.5029 | 369.578 | 2.337 | 22.1111 | 0.0155 | 2.36 | 22.1111 | 0.0156 | 2.321 | 22.1111 | 0.0153 | 27.5498 | 9.5498 | 0.34664 | 0.015871
E200 | 1440 | 1218 | 151 | 71 | 5521.9812 | 4302.755 | 1219.2263 | 5342.9074 | 4121.6295 | 1221.2778 | 3.708 | 26.7778 | 0.0111 | 3.717 | 26.7778 | 0.0111 | 3.698 | 26.7778 | 0.011 | 181.1254 | 30.1254 | 0.16632 | 0.0054555
COP=(net refr effect)/(total elec)=((env sens)+(coil lat)); sens coil = (tot coil)-(lat coil); compr elec = (compr+odfan elec)-(odfan elec)
Envelope sensible includes adjustment for simulated zone temp (delta 0-0.1 C), from "QNOW" [sensible zone extraction].
Note: (fan elec) .NE. (total coil)-(sens coil), worsens with increasing humidity, check with jjh.
raw data here |  |  |  |  | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
INSTRUCTIONS |  | Compressor | Supply | Condenser |  | Fan heat | [6 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | + od fan | Fan | (od) Fan | Total | (tot-sns-lat) | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kBtu) | (kWh) | (kBtu) | (kBtu) | (kBtu) | (kBtu) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100 |  | 1378 | 141 | 67 | 12945 | 138.6284 | 0 |  | 12472 | 0 |  | 72.2 | 0.0074 |  | 72.2 | 0.0074 |  | 72.2 | 0.0074
E110 |  | 943 | 122 | 60 | 12814 | 118.9918 | 0 |  | 12408 | 0 |  | 72.1 | 0.0064 |  | 72.1 | 0.0064 |  | 72.1 | 0.0064
E120 |  | 893 | 110 | 55 | 12758 | 107.5615 | 0 |  | 12391 | 0 |  | 80.1 | 0.0078 |  | 80.1 | 0.0078 |  | 80.1 | 0.0078
E130 |  | 98 | 8 | 5 | 734 | 7.6202 | 0 |  | 708 | 0 |  | 71.8 | 0.0073 |  | 71.8 | 0.0073 |  | 71.8 | 0.0073
E140 |  | 60 | 6 | 4 | 664 | 6.1547 | 0 |  | 643 | 0 |  | 71.8 | 0.0064 |  | 71.8 | 0.0064 |  | 71.8 | 0.0064
E150 |  | 1047 | 136 | 65 | 15448 | 149.4725 | 2530 |  | 12408 | 2523 |  | 72.2 | 0.0083 |  | 72.2 | 0.0083 |  | 72.2 | 0.0083
E160 |  | 986 | 121 | 60 | 15383 | 137.456 | 2523 |  | 12391 | 2523 |  | 80.1 | 0.0099 |  | 80.1 | 0.0099 |  | 80.1 | 0.0098
E165 |  | 1325 | 145 | 69 | 15521 | 160.6096 | 2526 |  | 12447 | 2523 |  | 74.2 | 0.0092 |  | 74.2 | 0.0092 |  | 74.2 | 0.0092
E170 |  | 557 | 63 | 34 | 7631 | 79.1325 | 2521 |  | 4840 | 2523 |  | 72 | 0.0105 |  | 72 | 0.0105 |  | 72 | 0.0105
E180 |  | 968 | 112 | 56 | 15472 | 188.1594 | 9990 |  | 4840 | 10091 |  | 72.1 | 0.0164 |  | 72.1 | 0.0165 |  | 72.1 | 0.0163
E185 |  | 1410 | 137 | 66 | 15636 | 215.4162 | 9997 |  | 4904 | 10091 |  | 72.2 | 0.0162 |  | 72.2 | 0.0163 |  | 72.2 | 0.0161
E190 |  | 146 | 14 | 8 | 1974 | 23.7397 | 1250 |  | 643 | 1261 |  | 71.8 | 0.0159 |  | 71.8 | 0.0161 |  | 71.8 | 0.0158
E195 |  | 228 | 18 | 11 | 2053 | 27.5498 | 1251 |  | 708 | 1261 |  | 71.8 | 0.0155 |  | 71.8 | 0.0156 |  | 71.8 | 0.0153
E200 |  | 1289 | 151 | 71 | 18841 | 181.1254 | 4160 |  | 14063 | 4167 |  | 80.2 | 0.0111 |  | 80.2 | 0.0111 |  | 80.2 | 0.011
Table "tkfanheat". Fan Heat Discrepancy
d:\e\iea22\hvabtest\results\doe2\21ejna2a.wk3 a:63; 31 jan 00
F e b r u a r y T o t a l s
| Supply | Evaporator Coil Load |  |  | Envelope Load |  |  | Qfan,heat | (del Qfan) | (del Qfan)
Cases | Fan | Total | Sensible | Latent | Sensible | Latent | Qfan,heat | - Qfan | /Qfan | /Qcoil
E160 | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (frac) | (frac)
E100 | 141 | 3793.9625 | 3793.9625 | 0 | 3655.3341 | 0 | 138.6284 | -2.3716 | -0.017108 | -0.00062511
E110 | 122 | 3755.5686 | 3755.5686 | 0 | 3636.5768 | 0 | 118.9918 | -3.0082 | -0.025281 | -0.000801
E120 | 110 | 3739.1559 | 3739.1559 | 0 | 3631.5944 | 0 | 107.5615 | -2.4385 | -0.02267 | -0.00065214
E130 | 8 | 215.1231 | 215.1231 | 0 | 207.5029 | 0 | 7.6202 | -0.37984 | -0.049846 | -0.0017657
E140 | 6 | 194.6073 | 194.6073 | 0 | 188.4525 | 0 | 6.1547 | 0.15475 | 0.025143 | 0.00079518
E150 | 136 | 4527.5498 | 3786.0492 | 741.5006 | 3636.5768 | 739.449 | 149.4725 | 13.4725 | 0.090133 | 0.0029757
E160 | 121 | 4508.4994 | 3769.0504 | 739.449 | 3631.5944 | 739.449 | 137.456 | 16.456 | 0.11972 | 0.00365
E165 | 145 | 4548.9449 | 3808.6166 | 740.3283 | 3648.007 | 739.449 | 160.6096 | 15.6096 | 0.09719 | 0.0034315
E170 | 63 | 2236.5182 | 1497.6553 | 738.8628 | 1418.5229 | 739.449 | 79.1325 | 16.1325 | 0.20387 | 0.0072132
E180 | 112 | 4534.5838 | 1606.6823 | 2927.9015 | 1418.5229 | 2957.5029 | 188.1594 | 76.1594 | 0.40476 | 0.016795
E185 | 137 | 4582.6495 | 1652.6964 | 2929.9531 | 1437.2802 | 2957.5029 | 215.4162 | 78.4162 | 0.36402 | 0.017112
E190 | 14 | 578.5463 | 212.1923 | 366.354 | 188.4525 | 369.578 | 23.7397 | 9.7397 | 0.41027 | 0.016835
E195 | 18 | 601.6999 | 235.0528 | 366.6471 | 207.5029 | 369.578 | 27.5498 | 9.5498 | 0.34664 | 0.015871
E200 | 151 | 5521.9812 | 4302.755 | 1219.2263 | 4121.6295 | 1221.2778 | 181.1254 | 30.1254 | 0.16632 | 0.0054555
E100R2EP | 141 | 3794.2556 | 3794.2556 | 0 | 3655.3341 | 0 | 138.9215 | -2.0785 | -0.014962 | -0.00054781
E180R2EP | 112 | 4534.8769 | 1606.9754 | 2927.9015 | 1418.5229 | 2957.5029 | 188.4525 | 76.4525 | 0.40569 | 0.016859

## C
HVBTOUT1.WK3, August 26, 1997
Output spreadsheet for HVAC BESTEST
CIEMAT: cie0600b.wk3 b:a1..b:v38; 01 jun 00
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through Q and rows 13 through 27. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means and maxima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP are defined in Appendix C.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) | fan heat | error %
E100 | 1520.817 | 1307.458 | 145.185 | 68.174 | 3841.47 | 3841.47 | 0 | 3654.42 | 3654.42 | 0 | 2.4304 | 22.3 | 0.0076 | 2.4324 | 22.3 | 0.0076 | 2.4287 | 22.3 | 0.0076 | 187.05 | 0.011018
E110 | 1061.196 | 865.866 | 132.917 | 62.413 | 3803.58 | 3803.58 | 0 | 3635.601 | 3635.601 | 0 | 3.4589 | 22.3 | 0.0070296 | 3.4626 | 22.3 | 0.0071 | 3.4566 | 22.3 | 0.007 | 167.979 | 0.0093039
E120 | 1011.104 | 850.068 | 109.581 | 51.455 | 3763.48 | 3763.48 | 0 | 3630.472 | 3630.472 | 0 | 3.6139 | 26.8 | 0.0078 | 3.6153 | 26.8 | 0.0078 | 3.6124 | 26.8 | 0.0078 | 133.008 | 0.0062638
E130 | 105.419 | 93.198 | 8.316 | 3.905 | 215.778 | 215.778 | 0 | 207.344 | 207.344 | 0 | 1.9752 | 22.1 | 0.0076 | 1.9809 | 22.1 | 0.0076 | 1.956 | 22.1 | 0.0076 | 8.434 | 0.00054716
E140 | 65.008 | 54.799 | 6.947 | 3.262 | 195.53 | 195.53 | 0 | 188.503 | 188.503 | 0 | 2.9151 | 22.1 | 0.0070601 | 2.9278 | 22.1 | 0.0071 | 2.8958 | 22.1 | 0.007 | 7.027 | 0.00040931
E150 | 1202.424 | 1007.094 | 132.917 | 62.413 | 4542.78 | 3803.58 | 739.2 | 4374.801 | 3635.601 | 739.2 | 3.6675 | 22.3 | 0.0082 | 3.6706 | 22.3 | 0.0082 | 3.6652 | 22.3 | 0.0082 | 167.979 | 0.0093039
E160 | 1137.63 | 962.675 | 119.052 | 55.903 | 4516.378 | 3777.178 | 739.2 | 4369.652 | 3630.452 | 739.2 | 3.8658 | 26.8 | 0.009701 | 3.8682 | 26.8 | 0.0098 | 3.8641 | 26.8 | 0.0097 | 146.726 | 0.0073807
E165 | 1499.447 | 1291.242 | 141.678 | 66.527 | 4567.458 | 3828.258 | 739.2 | 4386.071 | 3646.871 | 739.2 | 2.9514 | 23.4 | 0.0090039 | 2.9533 | 23.4 | 0.0091 | 2.9498 | 23.4 | 0.009 | 181.387 | 0.010481
E170 | 629.076 | 538.959 | 61.322 | 28.795 | 2226.057 | 1486.857 | 739.2 | 2157.351 | 1418.151 | 739.2 | 3.4423 | 22.2 | 0.010494 | 3.446 | 22.2 | 0.0105 | 3.4386 | 22.2 | 0.0104 | 68.706 | 0.004991
E180 | 1077.109 | 914.262 | 110.813 | 52.034 | 4509.984 | 1553.184 | 2956.8 | 4374.852 | 1418.052 | 2956.8 | 4.0842 | 22.3 | 0.016614 | 4.0893 | 22.3 | 0.0167 | 4.0798 | 22.3 | 0.0165 | 135.132 | 0.015907
E185 | 1541.155 | 1342.681 | 135.056 | 63.418 | 4564.894 | 1608.094 | 2956.8 | 4393.649 | 1436.849 | 2956.8 | 2.8744 | 22.3 | 0.016441 | 2.8778 | 22.3 | 0.0166 | 2.871 | 22.3 | 0.0163 | 171.245 | 0.023022
E190 | 160.219 | 139.423 | 14.151 | 6.645 | 572.607 | 203.007 | 369.6 | 558.09 | 188.49 | 369.6 | 3.4865 | 22.1 | 0.016254 | 3.5 | 22.1 | 0.0164 | 3.475 | 22.1 | 0.0161 | 14.517 | 0.0018061
E195 | 244.919 | 218.867 | 17.728 | 8.324 | 595.24 | 225.64 | 369.6 | 576.926 | 207.326 | 369.6 | 2.3598 | 22.1 | 0.015764 | 2.3681 | 22.1 | 0.0159 | 2.3497 | 22.1 | 0.0156 | 18.314 | 0.0026038
E200 | 1468.214 | 1249.027 | 149.151 | 70.036 | 5534.2 | 4313.176 | 1221 | 5341.526 | 4120.502 | 1221.024 | 3.6677 | 26.8 | 0.010933 | 3.6716 | 26.8 | 0.011 | 3.6716 | 26.8 | 0.0109 | 192.674 | 0.010194

## D
Output spreadsheet for HVAC BESTEST
EDF CLIM2000-12/00 with automated extrap
see EDF modeler report.
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
BESTEST1
| February totals | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load |  | February mean
|  | Cooling energy consumption | Supply | Condenser | Evaporator coil load |  |  | Enveloppe load |  |  |  |  | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100 | 1530 | 1318 | 144 | 68 | 3800 | 3800 | 0 | 3656 | 3656 | 0 | 2.389 | 22.2 | 0.00691 | 2.392 | 22.2 | 0.00699 | 2.39 | 22.2 | 0.00684
E110 | 1089 | 899 | 129 | 61 | 3766 | 3766 | 0 | 3637 | 3637 | 0 | 3.342 | 22.2 | 0.00692 | 3.357 | 22.2 | 0.00699 | 3.322 | 22.2 | 0.00684
E120 | 1012 | 840 | 117 | 55 | 3749 | 3749 | 0 | 3632 | 3632 | 0 | 3.59 | 26.7 | 0.007 | 3.596 | 26.7 | 0.007 | 3.583 | 26.7 | 0.007
E130 | 109 | 94 | 10 | 5 | 219 | 219 | 0 | 209 | 209 | 0 | 1.909 | 22.2 | 0.00691 | 1.923 | 22.2 | 0.00691 | 1.85 | 22.2 | 0.00684
E140 | 69 | 57 | 8 | 4 | 198 | 198 | 0 | 190 | 190 | 0 | 2.734 | 22.2 | 0.00692 | 2.833 | 22.2 | 0.00692 | 2.68 | 22.2 | 0.00684
E150 | 1207 | 999 | 141 | 66 | 4517 | 3778 | 739 | 4376 | 3637 | 739 | 3.63 | 22.2 | 0.00853 | 3.63 | 22.2 | 0.00853 | 3.62 | 22.2 | 0.00853
E160 | 1139 | 949 | 129 | 61 | 4500 | 3761 | 739 | 4371 | 3632 | 739 | 3.84 | 26.7 | 0.0101 | 3.85 | 26.7 | 0.0101 | 3.83 | 26.7 | 0.0101
E165 | 1501 | 1281 | 150 | 70 | 4538 | 3798 | 739 | 4388 | 3649 | 739 | 2.92 | 23.3 | 0.00985 | 2.93 | 22.2 | 0.00985 | 2.92 | 22.2 | 0.00984
E170 | 638 | 530 | 73 | 34 | 2232 | 1493 | 739 | 2159 | 1420 | 739 | 3.39 | 22.2 | 0.0107 | 3.4 | 22.2 | 0.0107 | 3.38 | 22.2 | 0.0107
E180 | 1082 | 908 | 119 | 56 | 4495 | 1538 | 2957 | 4376 | 1420 | 2957 | 4.04 | 22.2 | 0.0164 | 4.05 | 22.2 | 0.0164 | 4.04 | 22.2 | 0.0164
E185 | 1543 | 1339 | 139 | 65 | 4535 | 1578 | 2957 | 4396 | 1439 | 2957 | 2.85 | 22.2 | 0.0171 | 2.85 | 22.2 | 0.0171 | 2.84 | 22.2 | 0.017
E190 | 164 | 138 | 18 | 9 | 577 | 208 | 370 | 559 | 190 | 370 | 3.41 | 22.2 | 0.0161 | 3.45 | 22.2 | 0.0161 | 3.37 | 22.2 | 0.0161
E195 | 250 | 217 | 23 | 11 | 601 | 232 | 370 | 579 | 209 | 370 | 2.31 | 22.2 | 0.0164 | 2.33 | 22.2 | 0.0165 | 2.29 | 22.2 | 0.0164
E200 | 1464 | 1239 | 153 | 72 | 5436 | 4215 | 1221 | 5283 | 4062 | 1221 | 3.61 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0115

## E
Blank

## F
HVBTOUT2.WK3, May 1998
Output spreadsheet for HVAC BESTEST
Dresden TRNSYS 14.2: Note, combine DRESDEN.WK3 a1..q38 at e:a1
Ideal" results no min/on off requirement
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  |  |  | February Totals | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
Cases | Cooling Energie Consumption | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  | Envelope Load | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg]
E100 | 1522.2661 | 1311.1661 | 143.6481 | 67.452 | 3799.7366 | 3799.7366 | 0 | 3656.0832 | 3656.0832 | 0 | 2.4017 | 22.2 | 0.0075036 | 2.4017 | 22.2 | 0.0075036 | 2.4017 | 22.2 | 0.0075036
E110 | 1066.9607 | 879.3187 | 127.6854 | 59.9566 | 3764.6112 | 3764.6112 | 0 | 3636.9245 | 3636.9245 | 0 | 3.4087 | 22.2 | 0.0065938 | 3.4087 | 22.2 | 0.0065938 | 3.4087 | 22.2 | 0.0065938
E120 | 1007.3023 | 835.847 | 116.6706 | 54.7846 | 3748.4294 | 3748.4294 | 0 | 3631.7568 | 3631.7568 | 0 | 3.6054 | 26.7 | 0.0079506 | 3.6054 | 26.7 | 0.0079506 | 3.6054 | 26.7 | 0.0079506
E130 | 108.7246 | 93.6472 | 10.2598 | 4.8176 | 218.9853 | 218.9853 | 0 | 208.7252 | 208.7252 | 0 | 1.9198 | 22.2 | 0.0075036 | 1.9198 | 22.2 | 0.0075036 | 1.9198 | 22.2 | 0.0075036
E140 | 67.7641 | 55.8468 | 8.1094 | 3.8079 | 197.6748 | 197.6748 | 0 | 189.5652 | 189.5652 | 0 | 2.7974 | 22.2 | 0.0065938 | 2.7974 | 22.2 | 0.0065938 | 2.7974 | 22.2 | 0.0065938
E150 | 1199.055 | 992.0333 | 140.8727 | 66.1491 | 4516.9958 | 3777.7958 | 739.2 | 4376.1245 | 3636.9245 | 739.2 | 3.6496 | 22.2 | 0.0083236 | 3.6496 | 22.2 | 0.0083236 | 3.6496 | 22.2 | 0.0083236
E160 | 1136.7334 | 946.9958 | 129.1114 | 60.6262 | 4500.0682 | 3760.8682 | 739.2 | 4370.9568 | 3631.7568 | 739.2 | 3.8452 | 26.7 | 0.010069 | 3.8452 | 26.7 | 0.010069 | 3.8452 | 26.7 | 0.010069
E165 | 1499.7105 | 1280.2205 | 149.3574 | 70.1326 | 4537.0685 | 3797.8685 | 739.2 | 4387.7098 | 3648.5098 | 739.2 | 2.9257 | 23.3 | 0.0093021 | 2.9257 | 23.3 | 0.0093021 | 2.9257 | 23.3 | 0.0093021
E170 | 635.909 | 528.3976 | 73.1586 | 34.3527 | 2231.6851 | 1492.4851 | 739.2 | 2158.5245 | 1419.3245 | 739.2 | 3.3944 | 22.2 | 0.010471 | 3.3944 | 22.2 | 0.010471 | 3.3944 | 22.2 | 0.010471
E180 | 1081.2706 | 907.1462 | 118.487 | 55.6374 | 4494.6115 | 1537.8115 | 2956.8 | 4376.1245 | 1419.3245 | 2956.8 | 4.0472 | 22.2 | 0.01631 | 4.0472 | 22.2 | 0.01631 | 4.0472 | 22.2 | 0.01631
E185 | 1541.5256 | 1336.897 | 139.2444 | 65.3842 | 4534.5283 | 1577.7283 | 2956.8 | 4395.2832 | 1438.4832 | 2956.8 | 2.8512 | 22.2 | 0.016151 | 2.8512 | 22.2 | 0.016151 | 2.8512 | 22.2 | 0.016151
E190 | 163.9975 | 137.5107 | 18.0236 | 8.4632 | 577.1889 | 207.5889 | 369.6 | 559.1652 | 189.5652 | 369.6 | 3.4096 | 22.2 | 0.015921 | 3.4096 | 22.2 | 0.015921 | 3.4096 | 22.2 | 0.015921
E195 | 249.7321 | 216.4828 | 22.6253 | 10.6241 | 600.9508 | 231.3508 | 369.6 | 578.3252 | 208.7252 | 369.6 | 2.3158 | 22.2 | 0.01547 | 2.3158 | 22.2 | 0.01547 | 2.3158 | 22.2 | 0.01547
E200 | 1479.9926 | 1252.8566 | 154.56 | 72.576 | 5497.5648 | 4276.5408 | 1221.024 | 5343.0048 | 4121.9808 | 1221.024 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.7339 | 0.011281

## G
HVBTOUT2.WK3, 23 May 2000
Output spreadsheet for HVAC BESTEST
"Real control minimum on/off time results
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
TRNSYS, realistic controller, 23 May 00
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  |  |  | February Totals | [6 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
Cases | Cooling Energie Consumption | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  | Envelope Load | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] | [kWh] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg] |  | [°C] | [kg/kg]
E100 | 1511.9369 | 1302.7258 | 142.3625 | 66.8486 | 3797.9491 | 3797.9491 | 3.3138e-14 | 3655.5859 | 3655.5859 | 0 | 2.4184 | 22.6346 | 0.0075088 | 2.4184 | 23.21 | 0.007509 | 2.4184 | 22.09 | 0.007509
E110 | 1061.9658 | 875.8322 | 126.659 | 59.4747 | 3763.2362 | 3763.2362 | 2.6912e-15 | 3636.5534 | 3636.5534 | 0 | 3.4271 | 22.5242 | 0.0066309 | 3.4553 | 23.06 | 0.006631 | 3.419 | 21.98 | 0.006631
E120 | 1001.6637 | 831.9292 | 115.4998 | 54.2347 | 3746.8105 | 3746.8105 | 3.8103e-15 | 3631.3216 | 3631.3216 | 0 | 3.6313 | 27.0785 | 0.0079517 | 3.6541 | 28.26 | 0.007952 | 3.6095 | 26.17 | 0.007952
E130 | 110.1161 | 94.8489 | 10.3889 | 4.8783 | 219.7695 | 219.7695 | 3.1415e-14 | 209.371 | 209.371 | 0 | 1.9163 | 21.6377 | 0.0075194 | 2.0033 | 22.25 | 0.007519 | 1.6737 | 21.03 | 0.007519
E140 | 68.6428 | 56.5735 | 8.2128 | 3.8565 | 198.5643 | 198.5643 | -2.7533e-16 | 190.358 | 190.358 | 0 | 2.7996 | 21.5097 | 0.0065941 | 2.8848 | 22.25 | 0.006594 | 2.3127 | 20.76 | 0.006594
E150 | 1191.613 | 986.7503 | 139.4036 | 65.4591 | 4515.0285 | 3775.8216 | 739.2069 | 4375.5775 | 3636.3775 | 739.2 | 3.6734 | 22.6771 | 0.0085152 | 3.6952 | 23.28 | 0.008566 | 3.6611 | 22.06 | 0.008454
E160 | 1132.8835 | 944.3585 | 128.2863 | 60.2388 | 4498.8816 | 3759.6868 | 739.1947 | 4370.6181 | 3631.4181 | 739.2 | 3.8599 | 26.9948 | 0.010236 | 3.8606 | 27.61 | 0.01029 | 3.8212 | 26.39 | 0.01018
E165 | 1489.9268 | 1272.4664 | 147.976 | 69.4843 | 4535.1008 | 3795.9117 | 739.1892 | 4387.1605 | 3647.9605 | 739.2 | 2.9449 | 23.7805 | 0.0095112 | 2.9584 | 24.48 | 0.009553 | 2.9336 | 23.26 | 0.009434
E170 | 635.8287 | 528.5837 | 72.9774 | 34.2676 | 2231.6345 | 1492.423 | 739.2115 | 2158.621 | 1419.421 | 739.2 | 3.4033 | 22.1169 | 0.010525 | 3.4645 | 22.67 | 0.01065 | 3.3167 | 21.57 | 0.0104
E180 | 1080.0377 | 906.4398 | 118.1287 | 55.4691 | 4494.0999 | 1537.3001 | 2956.7992 | 4375.9707 | 1419.1707 | 2956.8 | 4.055 | 22.3344 | 0.016404 | 4.0754 | 22.79 | 0.01679 | 4.028 | 22.01 | 0.01613
E185 | 1538.3972 | 1334.3908 | 138.821 | 65.1855 | 4533.9432 | 1577.1233 | 2956.8195 | 4395.0925 | 1438.2925 | 2956.8 | 2.8574 | 22.3682 | 0.016279 | 2.8622 | 22.61 | 0.01648 | 2.8362 | 22.13 | 0.01608
E190 | 165.1202 | 138.4572 | 18.1435 | 8.5195 | 577.6703 | 208.0235 | 369.6468 | 559.4558 | 189.8558 | 369.6 | 3.4048 | 21.9469 | 0.015707 | 3.508 | 22.25 | 0.01595 | 3.1652 | 21.63 | 0.01546
E195 | 251.5799 | 218.0909 | 22.7884 | 10.7006 | 601.339 | 231.7335 | 369.6055 | 578.542 | 208.942 | 369.6 | 2.3054 | 22.0113 | 0.015326 | 2.4571 | 22.26 | 0.01551 | 2.2587 | 21.76 | 0.01514
E200 | 1479.9926 | 1252.8566 | 154.56 | 72.576 | 5497.5648 | 4276.5408 | 1221.024 | 5343.0048 | 4121.9808 | 1221.024 | 3.6102 | 26.7339 | 0.011281 | 3.6102 | 26.73 | 0.01128 | 3.6102 | 26.73 | 0.01128

## H
HVBTOUT2.WK3, September 02, 1998
Output spreadsheet for HVAC BESTEST
TUD Analytical Verification
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to columns B through T and rows 25 through 38. The protection
option has been employed to help assure that data is input in the correct cells.
3. February totals are consumption and or loads just for the month of February. Similarly,
February means, maxima, and minima are those values just for the month of February.
4. Cooling Energy Consumption, Evaporator Coil Load, Envelope Load, and COP (Coefficient
of Performance) are defined in the Glossary appendix.
TUD Analytical Verication, 10 Aug 00 |  |  |  | Patm = 101325 Pa; difference between saturation enthalpy and zone air enthalpy considered
[5 empty] | F e b r u a r y T o t a l s | [6 empty] | February Mean |  | February Maximum |  |  | February Minimum
|  | Cooling Energy Consumption |  |  | Evaporator Coil Load |  |  |  | Envelope Load
|  |  | Supply | Condenser | [8 empty] | Humidity |  |  | Humidity |  |  | Humidity
Cases | Total | Compressor | Fan | Fan | Total | Sensible | Latent | Total | Sensible | Latent | COP | IDB | Ratio | COP | IDB | Ratio | COP | IDB | Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg) |  | (°C) | (kg/kg)
E100 | 1530.548 | 1318.8515 | 144.0538 | 67.6427 | 3800.3599 | 3800.3599 | 0 | 3656.3062 | 3656.3062 | 0 | 2.3889 | 22.2 | 0.0074274 | 2.3889 | 22.2 | 0.0074274 | 2.3889 | 22.2 | 0.0074274
E110 | 1076.2349 | 887.9378 | 128.1312 | 60.166 | 3765.2438 | 3765.2438 | 0 | 3637.1129 | 3637.1129 | 0 | 3.3795 | 22.2 | 0.0065187 | 3.3795 | 22.2 | 0.0065187 | 3.3795 | 22.2 | 0.0065187
E120 | 1012.6774 | 840.8662 | 116.9129 | 54.8982 | 3748.902 | 3748.902 | 0 | 3631.9893 | 3631.9893 | 0 | 3.5865 | 26.7 | 0.0078783 | 3.5865 | 26.7 | 0.0078783 | 3.5865 | 26.7 | 0.0078783
E130 | 110.5818 | 95.2867 | 10.4079 | 4.8872 | 219.3541 | 219.3541 | 0 | 208.9462 | 208.9462 | 0 | 1.8895 | 22.2 | 0.0074274 | 1.8895 | 22.2 | 0.0074274 | 1.8895 | 22.2 | 0.0074274
E140 | 68.9953 | 56.924 | 8.2142 | 3.8571 | 197.9671 | 197.9671 | 0 | 189.7529 | 189.7529 | 0 | 2.7502 | 22.2 | 0.0065187 | 2.7502 | 22.2 | 0.0065187 | 2.7502 | 22.2 | 0.0065187
E150 | 1206.49 | 998.9576 | 141.2203 | 66.3121 | 4517.5274 | 3778.3318 | 739.1956 | 4376.3129 | 3637.1129 | 739.2 | 3.6273 | 22.2 | 0.0082272 | 3.6273 | 22.2 | 0.0082272 | 3.6273 | 22.2 | 0.0082272
E160 | 1140.44 | 950.4111 | 129.3096 | 60.7193 | 4500.5449 | 3761.3053 | 739.2396 | 4371.1893 | 3631.9893 | 739.2 | 3.8329 | 26.7 | 0.009969 | 3.8329 | 26.7 | 0.009969 | 3.8329 | 26.7 | 0.009969
E165 | 1497.8302 | 1278.7205 | 149.0983 | 70.0114 | 4536.998 | 3797.7525 | 739.2454 | 4387.8381 | 3648.6381 | 739.2 | 2.9295 | 23.3 | 0.0092694 | 2.9295 | 23.3 | 0.0092694 | 2.9295 | 23.3 | 0.0092694
E170 | 641.1173 | 532.9693 | 73.5918 | 34.5562 | 2232.3427 | 1493.027 | 739.3157 | 2158.7129 | 1419.5129 | 739.2 | 3.3672 | 22.2 | 0.010367 | 3.3672 | 22.2 | 0.010367 | 3.3672 | 22.2 | 0.010367
E180 | 1082.666 | 908.1216 | 118.7728 | 55.7716 | 4495.2651 | 1537.7939 | 2957.4713 | 4376.3129 | 1419.5129 | 2956.8 | 4.0423 | 22.2 | 0.01619 | 4.0423 | 22.2 | 0.01619 | 4.0423 | 22.2 | 0.01619
E185 | 1544.6397 | 1339.7996 | 139.3882 | 65.4519 | 4535.1231 | 1577.6007 | 2957.5224 | 4395.5062 | 1438.7062 | 2956.8 | 2.8458 | 22.2 | 0.016056 | 2.8458 | 22.2 | 0.016056 | 2.8458 | 22.2 | 0.016056
E190 | 165.173 | 138.4708 | 18.1701 | 8.5321 | 577.5279 | 207.8123 | 369.7156 | 559.3529 | 189.7529 | 369.6 | 3.3865 | 22.2 | 0.015796 | 3.3865 | 22.2 | 0.015796 | 3.3865 | 22.2 | 0.015796
E195 | 252.1605 | 218.6235 | 22.821 | 10.716 | 601.3744 | 231.645 | 369.7294 | 578.5462 | 208.9462 | 369.6 | 2.2944 | 22.2 | 0.015368 | 2.2944 | 22.2 | 0.015368 | 2.2944 | 22.2 | 0.015368
E200 | 1475.8104 | 1248.8198 | 154.4611 | 72.5296 | 5497.8008 | 4276.6945 | 1221.1063 | 5343.2549 | 4122.2309 | 1221.024 | 3.6206 | 26.7 | 0.011129 | 3.6206 | 26.7 | 0.011129 | 3.6206 | 26.7 | 0.011129

## I
27 | 1999
HTAL1 (analytical verification) updated by jn 15 Aug 00 (Markus' results sent 25 Jul 00)
100 | 1530.8 | 1319 | 144.1 | 67.6 | 3800.4 | 3800.4 | 0 | 3656.3 | 3656.3 | 0 | 2.39 | 22.2 | 0.00734
110 | 1077.2 | 889.2 | 127.9 | 60.1 | 3765 | 3765 | 0 | 3637.1 | 3637.1 | 0 | 3.38 | 22.2 | 0.0064
120 | 1011 | 839.1 | 116.9 | 54.9 | 3748.8 | 3748.8 | 0 | 3631.9 | 3631.9 | 0 | 3.59 | 26.7 | 0.00786
130 | 109.5 | 94.4 | 10.3 | 4.8 | 219.3 | 219.3 | 0 | 209 | 209 | 0 | 1.91 | 22.2 | 0.00734
140 | 68.5 | 56.5 | 8.1 | 3.8 | 197.9 | 197.9 | 0 | 189.7 | 189.7 | 0 | 2.77 | 22.2 | 0.0064
150 | 1206.5 | 999.2 | 141.1 | 66.3 | 4517.4 | 3778.2 | 739.2 | 4376.3 | 3637.1 | 739.2 | 3.63 | 22.2 | 0.0082
160 | 1139.3 | 949.4 | 129.2 | 60.7 | 4500.3 | 3761.1 | 739.2 | 4371.1 | 3631.9 | 739.2 | 3.84 | 26.7 | 0.00994
165 | 1499.7 | 1280.2 | 149.3 | 70.1 | 4537.3 | 3798.1 | 739.2 | 4387.9 | 3648.7 | 739.2 | 2.93 | 23.3 | 0.0092
170 | 637.7 | 530 | 73.2 | 34.4 | 2231.9 | 1492.7 | 739.2 | 2158.7 | 1419.5 | 739.2 | 3.39 | 22.2 | 0.01045
180 | 1082.3 | 908 | 118.6 | 55.7 | 4494.9 | 1538.1 | 2956.8 | 4376.3 | 1419.5 | 2956.8 | 4.04 | 22.2 | 0.01623
185 | 1543.4 | 1338.6 | 139.4 | 65.4 | 4534.9 | 1578.1 | 2956.8 | 4395.5 | 1438.7 | 2956.8 | 2.85 | 22.2 | 0.01605
190 | 164.1 | 137.6 | 18 | 8.5 | 577.3 | 207.7 | 369.6 | 559.3 | 189.7 | 369.6 | 3.41 | 22.2 | 0.0159
195 | 250 | 216.8 | 22.6 | 10.6 | 601.2 | 231.6 | 369.6 | 578.6 | 209 | 369.6 | 2.31 | 22.2 | 0.01544
200 | 1477.4 | 1250.2 | 154.6 | 72.6 | 5497.8 | 4276.8 | 1221 | 5343.2 | 4122.2 | 1221 | 3.62 | 26.7 | 0.01109

## J
HTAL numerical solution ("HTAL2"), 05 sep 00
100 | 1530.6 | 1318.9 | 144 | 67.6 | 3800.4 | 3800.4 | 0 | 3656.3 | 3656.3 | 0 | 2.39 | 22.216 | 0.007339 | 2.3893 | 22.235 | 0.007339 | 2.389 | 22.197 | 0.007339
110 | 1077.4 | 889.4 | 127.9 | 60.1 | 3765.3 | 3765.3 | 0 | 3637.1 | 3637.1 | 0 | 3.38 | 22.214 | 0.006411 | 3.3783 | 22.235 | 0.006411 | 3.377 | 22.193 | 0.006411
120 | 1011 | 839.2 | 116.9 | 54.9 | 3748.5 | 3748.5 | 0 | 3631.9 | 3631.9 | 0 | 3.59 | 26.712 | 0.007873 | 3.5941 | 26.735 | 0.007873 | 3.593 | 26.689 | 0.007873
130 | 109.5 | 94.3 | 10.3 | 4.8 | 219.2 | 219.2 | 0 | 209 | 209 | 0 | 1.91 | 22.187 | 0.007339 | 1.9079 | 22.202 | 0.007339 | 1.908 | 22.172 | 0.007339
140 | 68.3 | 56.4 | 8.1 | 3.8 | 197.3 | 197.3 | 0 | 189.7 | 189.7 | 0 | 2.77 | 22.185 | 0.006402 | 2.7701 | 22.202 | 0.006402 | 2.77 | 22.168 | 0.006402
150 | 1206.5 | 999.2 | 141.1 | 66.2 | 4518.3 | 3779 | 739.4 | 4376.3 | 3637.1 | 739.2 | 3.63 | 22.216 | 0.00821 | 3.6295 | 22.235 | 0.008212 | 3.626 | 22.197 | 0.008209
160 | 1138.9 | 949.1 | 129.2 | 60.7 | 4499.9 | 3760.8 | 739.1 | 4371.1 | 3631.9 | 739.2 | 3.84 | 26.714 | 0.009946 | 3.838 | 26.735 | 0.009948 | 3.837 | 26.693 | 0.009944
165 | 1499.6 | 1280.2 | 149.3 | 70.1 | 4537.9 | 3798.6 | 739.3 | 4387.9 | 3648.7 | 739.2 | 2.93 | 23.317 | 0.009208 | 2.9269 | 23.335 | 0.00921 | 2.926 | 23.299 | 0.009207
170 | 637.8 | 530.1 | 73.2 | 34.4 | 2232.5 | 1493.1 | 739.4 | 2158.7 | 1419.5 | 739.2 | 3.39 | 22.199 | 0.010451 | 3.3859 | 22.214 | 0.010454 | 3.385 | 22.185 | 0.010448
180 | 1081.9 | 907.7 | 118.5 | 55.7 | 4493.8 | 1537.7 | 2956.1 | 4376.3 | 1419.5 | 2956.8 | 4.04 | 22.205 | 0.01623 | 4.0442 | 22.214 | 0.016237 | 4.044 | 22.196 | 0.016222
185 | 1542.9 | 1338.2 | 139.3 | 65.4 | 4533.9 | 1577.7 | 2956.2 | 4395.5 | 1438.7 | 2956.8 | 2.85 | 22.206 | 0.016059 | 2.8485 | 22.214 | 0.016065 | 2.848 | 22.198 | 0.016052
190 | 164.2 | 137.7 | 18 | 8.5 | 577.7 | 207.9 | 369.8 | 559.3 | 189.7 | 369.6 | 3.41 | 22.194 | 0.015891 | 3.4087 | 22.202 | 0.015897 | 3.409 | 22.186 | 0.015885
195 | 250 | 216.8 | 22.6 | 10.6 | 601.2 | 231.6 | 369.6 | 578.6 | 209 | 369.6 | 2.31 | 22.195 | 0.015439 | 2.3143 | 22.202 | 0.015444 | 2.314 | 22.188 | 0.015434
200 | 1477.1 | 1250 | 154.6 | 72.6 | 5497.8 | 4276.8 | 1221 | 5343.2 | 4122.2 | 1221 | 3.62 | 26.713 | 0.011099 | 3.6173 | 26.713 | 0.011099 | 3.617 | 26.713 | 0.011099

## K
CA-SIS 05/00
Entered at A25 from CASI0500.WK3 a:a7..a:t20
| February Totals | [9 empty] | February Mean |  |  | February Maximum |  |  | February Minimum
| cooloing energy Consumption |  |  |  | Evaporator coil Load |  |  | envelope load
cases | Total | compres-sor | supply fan | conden-ser fan | total | sensible | latent | total | sensible | latent | COP | IDB | humidity ratio | COP | IDB | humidity ratio | COP | IDB | humidity ratio
| kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh |  | °C | kg/kg |  | °C | kg/kg |  | °C | kg/kg
E100 | 1531 | 1319 | 144 | 68 | 3800 | 3800 | 0 | 3656 | 3656 | 0 | 2.39 | 22.2 | 0.0075 | 2.39 | 22.2 | 0.0075 | 2.39 | 22.2 | 0.0075
E110 | 1077 | 889 | 128 | 60 | 3765 | 3765 | 0 | 3637 | 3637 | 0 | 3.38 | 22.2 | 0.0066 | 3.38 | 22.2 | 0.0066 | 3.38 | 22.2 | 0.0066
E120 | 1012 | 840 | 117 | 55 | 3749 | 3749 | 0 | 3632 | 3632 | 0 | 3.59 | 26.7 | 0.008 | 3.59 | 26.7 | 0.008 | 3.59 | 26.7 | 0.008
E130 | 110 | 95 | 10 | 5 | 219 | 219 | 0 | 209 | 209 | 0 | 1.91 | 22.2 | 0.0075 | 1.91 | 22.2 | 0.0075 | 1.91 | 22.2 | 0.0075
E140 | 68 | 57 | 8 | 4 | 198 | 198 | 0 | 190 | 190 | 0 | 2.77 | 22.2 | 0.0065 | 2.77 | 22.2 | 0.0065 | 2.77 | 22.2 | 0.0065
E150 | 1208 | 1000 | 141 | 66 | 4517 | 3778 | 739 | 4376 | 3637 | 739 | 3.62 | 22.2 | 0.0083 | 3.63 | 22.2 | 0.0084 | 3.62 | 22.2 | 0.0083
E160 | 1140 | 950 | 129 | 61 | 4501 | 3761 | 740 | 4371 | 3632 | 739 | 3.84 | 26.7 | 0.0102 | 3.84 | 26.7 | 0.0103 | 3.83 | 26.7 | 0.0101
E165 | 1502 | 1283 | 149 | 70 | 4538 | 3798 | 740 | 4388 | 3649 | 739 | 2.92 | 23.3 | 0.0093 | 2.94 | 23.3 | 0.0094 | 2.91 | 23.3 | 0.0093
E170 | 638 | 531 | 73 | 34 | 2233 | 1493 | 740 | 2159 | 1420 | 739 | 3.38 | 22.2 | 0.0106 | 3.38 | 22.2 | 0.106 | 3.38 | 22.2 | 0.106
E180 | 1083 | 909 | 118 | 56 | 4495 | 1537 | 2958 | 4376 | 1420 | 2957 | 4.04 | 22.2 | 0.0164 | 4.05 | 22.2 | 0.0165 | 4.03 | 22.2 | 0.0162
E185 | 1544 | 1340 | 139 | 65 | 4507 | 1548 | 2959 | 4396 | 1439 | 2957 | 2.85 | 22.2 | 0.0162 | 2.86 | 22.2 | 0.0163 | 2.84 | 22.2 | 0.0161
E190 | 164 | 138 | 18 | 8 | 578 | 208 | 370 | 557 | 190 | 367 | 3.41 | 22.2 | 0.016 | 3.41 | 22.2 | 0.016 | 3.41 | 22.2 | 0.016
E195 | 250 | 217 | 23 | 11 | 602 | 232 | 370 | 576 | 209 | 367 | 2.31 | 22.2 | 0.0156 | 2.31 | 22.2 | 0.0156 | 2.31 | 22.2 | 0.0156
E200 | 1477 | 1250 | 154 | 73 | 5498 | 4276 | 1222 | 5343 | 4122 | 1221 | 3.62 | 26.7 | 0.0114 | 3.63 | 26.7 | 0.0115 | 3.61 | 26.7 | 0.0113

## Q
RESULTS.XLS5-3, October 15, 2002 | [5 empty] | SEE SHEET 'A' FOR INSTRUCTIONS
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e) | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 1531 | 1530 | 1520.817 | 1519 | 1520.1842 | 1522.2661 | 1511.9369 | 1511.9369 | 1531 | 1.246% | 1530.548 | 1530.8 | 1530.6 | 0
E110 | 1077 | 1089 | 1061.196 | 1065 | 1069.3313 | 1066.9607 | 1061.9658 | 1061.196 | 1089 | 2.583% | 1076.2349 | 1077.2 | 1077.4 | 0
E120 | 1012 | 1012 | 1011.104 | 1003 | 1006.6379 | 1007.3023 | 1001.6637 | 1001.6637 | 1012 | 1.021% | 1012.6774 | 1011 | 1011 | 0
E130 | 110 | 109 | 105.419 | 106 | 108.1197 | 108.7246 | 110.1161 | 105.419 | 110.1161 | 4.248% | 110.5818 | 109.5 | 109.5 | 0
E140 | 68 | 69 | 65.008 | 66 | 67.7696 | 67.7641 | 68.6428 | 65.008 | 69 | 5.786% | 68.9953 | 68.5 | 68.3 | 0
E150 | 1208 | 1207 | 1202.424 | 1183 | 1197.6199 | 1199.055 | 1191.613 | 1183 | 1208 | 2.072% | 1206.49 | 1206.5 | 1206.5 | 0
E160 | 1140 | 1139 | 1137.63 | 1107 | 1132.2318 | 1136.7334 | 1132.8835 | 1107 | 1140 | 2.894% | 1140.44 | 1139.3 | 1138.9 | 0
E165 | 1502 | 1501 | 1499.447 | 1470 | 1491.5878 | 1499.7105 | 1489.9268 | 1470 | 1502 | 2.136% | 1497.8302 | 1499.7 | 1499.6 | 0
E170 | 638 | 638 | 629.076 | 620 | 635.4994 | 635.909 | 635.8287 | 620 | 638 | 2.808% | 641.1173 | 637.7 | 637.8 | 0
E180 | 1083 | 1082 | 1077.109 | 1080 | 1082.3259 | 1081.2706 | 1080.0377 | 1077.109 | 1083 | 0.5441% | 1082.666 | 1082.3 | 1081.9 | 0
E185 | 1544 | 1543 | 1541.155 | 1547 | 1540.5373 | 1541.5256 | 1538.3972 | 1538.3972 | 1547 | 0.5569% | 1544.6397 | 1543.4 | 1542.9 | 0
E190 | 164 | 164 | 160.219 | 160 | 164.1636 | 163.9975 | 165.1202 | 160 | 165.1202 | 3.1% | 165.173 | 164.1 | 164.2 | 0
E195 | 250 | 250 | 244.919 | 246 | 249.7096 | 249.7321 | 251.5799 | 244.919 | 251.5799 | 2.642% | 252.1605 | 250 | 250 | 0
E200 | 1477 | 1464 | 1468.214 | 1440 | 1465.3737 | 1479.9926 | 1479.9926 | 1440 | 1479.9926 | 2.71% | 1475.8104 | 1477.4 | 1477.1 | 0
Energy Consumption, Compressor (kWh,e) | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 1319 | 1318 | 1307.458 | 1311 |  | 1311.1661 | 1302.7258 | 1302.7258 | 1319 | 1.234% | 1318.8515 | 1319 | 1318.9 | 0
E110 | 889 | 899 | 865.866 | 883 |  | 879.3187 | 875.8322 | 865.866 | 899 | 3.732% | 887.9378 | 889.2 | 889.4 | 0
E120 | 840 | 840 | 850.068 | 838 |  | 835.847 | 831.9292 | 831.9292 | 850.068 | 2.157% | 840.8662 | 839.1 | 839.2 | 0
E130 | 95 | 94 | 93.198 | 93 |  | 93.6472 | 94.8489 | 93 | 95 | 2.099% | 95.2867 | 94.4 | 94.3 | 0
E140 | 57 | 57 | 54.799 | 56 |  | 55.8468 | 56.5735 | 54.799 | 57 | 3.867% | 56.924 | 56.5 | 56.4 | 0
E150 | 1000 | 999 | 1007.094 | 982 |  | 992.0333 | 986.7503 | 982 | 1007.094 | 2.512% | 998.9576 | 999.2 | 999.2 | 0
E160 | 950 | 949 | 962.675 | 926 |  | 946.9958 | 944.3585 | 926 | 962.675 | 3.859% | 950.4111 | 949.4 | 949.1 | 0
E165 | 1283 | 1281 | 1291.242 | 1256 |  | 1280.2205 | 1272.4664 | 1256 | 1291.242 | 2.756% | 1278.7205 | 1280.2 | 1280.2 | 0
E170 | 531 | 530 | 538.959 | 523 |  | 528.3976 | 528.5837 | 523 | 538.959 | 2.994% | 532.9693 | 530 | 530.1 | 0
E180 | 909 | 908 | 914.262 | 912 |  | 907.1462 | 906.4398 | 906.4398 | 914.262 | 0.8614% | 908.1216 | 908 | 907.7 | 0
E185 | 1340 | 1339 | 1342.681 | 1344 |  | 1336.897 | 1334.3908 | 1334.3908 | 1344 | 0.7172% | 1339.7996 | 1338.6 | 1338.2 | 0
E190 | 138 | 138 | 139.423 | 138 |  | 137.5107 | 138.4572 | 137.5107 | 139.423 | 1.381% | 138.4708 | 137.6 | 137.7 | 0
E195 | 217 | 217 | 218.867 | 217 |  | 216.4828 | 218.0909 | 216.4828 | 218.867 | 1.091% | 218.6235 | 216.8 | 216.8 | 0
E200 | 1250 | 1239 | 1249.027 | 1218 |  | 1252.8566 | 1252.8566 | 1218 | 1252.8566 | 2.791% | 1248.8198 | 1250.2 | 1250 | 0
Energy Consumption, Supply Fan (kWh,e) | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 144 | 144 | 145.185 | 141 | 143.5848 | 143.6481 | 142.3625 | 141 | 145.185 | 2.905% | 144.0538 | 144.1 | 144 | 0
E110 | 128 | 129 | 132.917 | 122 | 127.5927 | 127.6854 | 126.659 | 122 | 132.917 | 8.52% | 128.1312 | 127.9 | 127.9 | 0
E120 | 117 | 117 | 109.581 | 110 | 116.438 | 116.6706 | 115.4998 | 109.581 | 117 | 6.346% | 116.9129 | 116.9 | 116.9 | 0
E130 | 10 | 10 | 8.316 | 8 | 10.2115 | 10.2598 | 10.3889 | 8 | 10.3889 | 22.95% | 10.4079 | 10.3 | 10.3 | 0
E140 | 8 | 8 | 6.947 | 6 | 8.0856 | 8.1094 | 8.2128 | 6 | 8.2128 | 26.94% | 8.2142 | 8.1 | 8.1 | 0
E150 | 141 | 141 | 132.917 | 136 | 140.3497 | 140.8727 | 139.4036 | 132.917 | 141 | 5.724% | 141.2203 | 141.1 | 141.1 | 0
E160 | 129 | 129 | 119.052 | 121 | 128.3806 | 129.1114 | 128.2863 | 119.052 | 129.1114 | 7.779% | 129.3096 | 129.2 | 129.2 | 0
E165 | 149 | 150 | 141.678 | 145 | 148.616 | 149.3574 | 147.976 | 141.678 | 150 | 5.582% | 149.0983 | 149.3 | 149.3 | 0
E170 | 73 | 73 | 61.322 | 63 | 73.0391 | 73.1586 | 72.9774 | 61.322 | 73.1586 | 16.08% | 73.5918 | 73.2 | 73.2 | 0
E180 | 118 | 119 | 110.813 | 112 | 118.4636 | 118.487 | 118.1287 | 110.813 | 119 | 6.893% | 118.7728 | 118.6 | 118.5 | 0
E185 | 139 | 139 | 135.056 | 137 | 139.139 | 139.2444 | 138.821 | 135.056 | 139.2444 | 3.005% | 139.3882 | 139.4 | 139.3 | 0
E190 | 18 | 18 | 14.151 | 14 | 18.0123 | 18.0236 | 18.1435 | 14 | 18.1435 | 22.8% | 18.1701 | 18 | 18 | 0
E195 | 23 | 23 | 17.728 | 18 | 22.6112 | 22.6253 | 22.7884 | 17.728 | 23 | 23.1% | 22.821 | 22.6 | 22.6 | 0
E200 | 154 | 153 | 149.151 | 151 | 153.4905 | 154.56 | 154.56 | 149.151 | 154.56 | 3.502% | 154.4611 | 154.6 | 154.6 | 0
Energy Consumption, Condenser Fan (kWh,e) | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 68 | 68 | 68.174 | 67 |  | 67.452 | 66.8486 | 66.8486 | 68.174 | 1.959% | 67.6427 | 67.6 | 67.6 | 0
E110 | 60 | 61 | 62.413 | 60 |  | 59.9566 | 59.4747 | 59.4747 | 62.413 | 4.884% | 60.166 | 60.1 | 60.1 | 0
E120 | 55 | 55 | 51.455 | 55 |  | 54.7846 | 54.2347 | 51.455 | 55 | 6.457% | 54.8982 | 54.9 | 54.9 | 0
E130 | 5 | 5 | 3.905 | 5 |  | 4.8176 | 4.8783 | 3.905 | 5 | 22.41% | 4.8872 | 4.8 | 4.8 | 0
E140 | 4 | 4 | 3.262 | 4 |  | 3.8079 | 3.8565 | 3.262 | 4 | 19.13% | 3.8571 | 3.8 | 3.8 | 0
E150 | 66 | 66 | 62.413 | 65 |  | 66.1491 | 65.4591 | 62.413 | 66.1491 | 5.634% | 66.3121 | 66.3 | 66.2 | 0
E160 | 61 | 61 | 55.903 | 60 |  | 60.6262 | 60.2388 | 55.903 | 61 | 8.394% | 60.7193 | 60.7 | 60.7 | 0
E165 | 70 | 70 | 66.527 | 69 |  | 70.1326 | 69.4843 | 66.527 | 70.1326 | 5.15% | 70.0114 | 70.1 | 70.1 | 0
E170 | 34 | 34 | 28.795 | 34 |  | 34.3527 | 34.2676 | 28.795 | 34.3527 | 16.08% | 34.5562 | 34.4 | 34.4 | 0
E180 | 56 | 56 | 52.034 | 56 |  | 55.6374 | 55.4691 | 52.034 | 56 | 7.111% | 55.7716 | 55.7 | 55.7 | 0
E185 | 65 | 65 | 63.418 | 66 |  | 65.3842 | 65.1855 | 63.418 | 66 | 3.945% | 65.4519 | 65.4 | 65.4 | 0
E190 | 8 | 9 | 6.645 | 8 |  | 8.4632 | 8.5195 | 6.645 | 9 | 27.6% | 8.5321 | 8.5 | 8.5 | 0
E195 | 11 | 11 | 8.324 | 11 |  | 10.6241 | 10.7006 | 8.324 | 11 | 24.97% | 10.716 | 10.6 | 10.6 | 0
E200 | 73 | 72 | 70.036 | 71 |  | 72.576 | 72.576 | 70.036 | 73 | 4.087% | 72.5296 | 72.6 | 72.6 | 0
results5-3.xls q:a06..p75; 10/15/02
[15 empty] | Coil Loads: Total, Sensible, and Latent | [14 empty] | Zone Loads: Total, Sensible, and Latent
[15 empty] | Coil Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | Zone Load, Total (kWh,thermal) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3796.6945 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4 | 0 | E100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3653.1097 | 3656.0832 | 3655.5859 | 3653.1097 | 3656.0832 | 0.08133% | 3656.3062 | 3656.3 | 3656.3 | 0
[15 empty] | E110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3762.6846 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3 | 0 | E110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.0919 | 3636.9245 | 3636.5534 | 3635.0919 | 3637 | 0.05246% | 3637.1129 | 3637.1 | 3637.1 | 0
[15 empty] | E120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.3788 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6488% | 3748.902 | 3748.8 | 3748.5 | 0 | E120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3629.9408 | 3631.7568 | 3631.3216 | 3629.9408 | 3632 | 0.0567% | 3631.9893 | 3631.9 | 3631.9 | 0
[15 empty] | E130 | 219 | 219 | 215.778 | 215.1231 | 215.9611 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.118% | 219.3541 | 219.3 | 219.2 | 0 | E130 | 209 | 209 | 207.344 | 207.5029 | 205.7496 | 208.7252 | 209.371 | 205.7496 | 209.371 | 1.733% | 208.9462 | 209 | 209 | 0
[15 empty] | E140 | 198 | 198 | 195.53 | 194.6073 | 195.8173 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 1.999% | 197.9671 | 197.9 | 197.3 | 0 | E140 | 190 | 190 | 188.503 | 188.4525 | 187.7318 | 189.5652 | 190.358 | 187.7318 | 190.358 | 1.384% | 189.7529 | 189.7 | 189.7 | 0
[15 empty] | E150 | 4517 | 4517 | 4542.78 | 4527.5498 | 4508.3212 | 4516.9958 | 4515.0285 | 4508.3212 | 4542.78 | 0.7628% | 4517.5274 | 4517.4 | 4518.3 | 0 | E150 | 4376 | 4376 | 4374.801 | 4376.0258 | 4374.3181 | 4376.1245 | 4375.5775 | 4374.3181 | 4376.1245 | 0.04128% | 4376.3129 | 4376.3 | 4376.3 | 0
[15 empty] | E160 | 4501 | 4500 | 4516.378 | 4508.4994 | 4490.5145 | 4500.0682 | 4498.8816 | 4490.5145 | 4516.378 | 0.5747% | 4500.5449 | 4500.3 | 4499.9 | 0 | E160 | 4371 | 4371 | 4369.652 | 4371.0434 | 4369.1704 | 4370.9568 | 4370.6181 | 4369.1704 | 4371.0434 | 0.04285% | 4371.1893 | 4371.1 | 4371.1 | 0
[15 empty] | E165 | 4538 | 4538 | 4567.458 | 4548.9449 | 4527.873 | 4537.0685 | 4535.1008 | 4527.873 | 4567.458 | 0.8725% | 4536.998 | 4537.3 | 4537.9 | 0 | E165 | 4388 | 4388 | 4386.071 | 4387.456 | 4385.1599 | 4387.7098 | 4387.1605 | 4385.1599 | 4388 | 0.06473% | 4387.8381 | 4387.9 | 4387.9 | 0
[15 empty] | E170 | 2233 | 2232 | 2226.057 | 2236.5182 | 2224.4208 | 2231.6851 | 2231.6345 | 2224.4208 | 2236.5182 | 0.5419% | 2232.3427 | 2231.9 | 2232.5 | 0 | E170 | 2159 | 2159 | 2157.351 | 2157.9719 | 2156.7137 | 2158.5245 | 2158.621 | 2156.7137 | 2159 | 0.1059% | 2158.7129 | 2158.7 | 2158.7 | 0
[15 empty] | E180 | 4495 | 4495 | 4509.984 | 4534.5838 | 4480.7708 | 4494.6115 | 4494.0999 | 4480.7708 | 4534.5838 | 1.197% | 4495.2651 | 4494.9 | 4493.8 | 0 | E180 | 4376 | 4376 | 4374.852 | 4376.0258 | 4374.3398 | 4376.1245 | 4375.9707 | 4374.3398 | 4376.1245 | 0.04078% | 4376.3129 | 4376.3 | 4376.3 | 0
[15 empty] | E185 | 4507 | 4535 | 4564.894 | 4582.6495 | 4521.5036 | 4534.5283 | 4533.9432 | 4507 | 4582.6495 | 1.668% | 4535.1231 | 4534.9 | 4533.9 | 0 | E185 | 4396 | 4396 | 4393.649 | 4394.7831 | 4392.349 | 4395.2832 | 4395.0925 | 4392.349 | 4396 | 0.08306% | 4395.5062 | 4395.5 | 4395.5 | 0
[15 empty] | E190 | 578 | 577 | 572.607 | 578.5463 | 573.8077 | 577.1889 | 577.6703 | 572.607 | 578.5463 | 1.028% | 577.5279 | 577.3 | 577.7 | 0 | E190 | 557 | 559 | 558.09 | 558.0305 | 557.3382 | 559.1652 | 559.4558 | 557 | 559.4558 | 0.439% | 559.3529 | 559.3 | 559.3 | 0
[15 empty] | E195 | 602 | 601 | 595.24 | 601.6999 | 596.6464 | 600.9508 | 601.339 | 595.24 | 602 | 1.124% | 601.3744 | 601.2 | 601.2 | 0 | E195 | 576 | 579 | 576.926 | 577.0809 | 575.3548 | 578.3252 | 578.542 | 575.3548 | 579 | 0.6301% | 578.5462 | 578.6 | 578.6 | 0
[15 empty] | E200 | 5498 | 5436 | 5534.2 | 5521.9812 | 5483.8906 | 5497.5648 | 5497.5648 | 5436 | 5534.2 | 1.786% | 5497.8008 | 5497.8 | 5497.8 | 0 | E200 | 5343 | 5283 | 5341.526 | 5342.9074 | 5340.9046 | 5343.0048 | 5343.0048 | 5283 | 5343.0048 | 1.123% | 5343.2549 | 5343.2 | 5343.2 | 0
[15 empty] | Coil Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | Zone Load, Sensible (kWh,thermal) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 3800 | 3800 | 3841.47 | 3793.9625 | 3796.6945 | 3799.7366 | 3797.9491 | 3793.9625 | 3841.47 | 1.25% | 3800.3599 | 3800.4 | 3800.4 | 0 | E100 | 3656 | 3656 | 3654.42 | 3655.3341 | 3653.1097 | 3656.0832 | 3655.5859 | 3653.1097 | 3656.0832 | 0.08133% | 3656.3062 | 3656.3 | 3656.3 | 0
[15 empty] | E110 | 3765 | 3766 | 3803.58 | 3755.5686 | 3762.6846 | 3764.6112 | 3763.2362 | 3755.5686 | 3803.58 | 1.275% | 3765.2438 | 3765 | 3765.3 | 0 | E110 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.0919 | 3636.9245 | 3636.5534 | 3635.0919 | 3637 | 0.05246% | 3637.1129 | 3637.1 | 3637.1 | 0
[15 empty] | E120 | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.3788 | 3748.4294 | 3746.8105 | 3739.1559 | 3763.48 | 0.6488% | 3748.902 | 3748.8 | 3748.5 | 0 | E120 | 3632 | 3632 | 3630.472 | 3631.5944 | 3629.9408 | 3631.7568 | 3631.3216 | 3629.9408 | 3632 | 0.0567% | 3631.9893 | 3631.9 | 3631.9 | 0
[15 empty] | E130 | 219 | 219 | 215.778 | 215.1231 | 215.9611 | 218.9853 | 219.7695 | 215.1231 | 219.7695 | 2.118% | 219.3541 | 219.3 | 219.2 | 0 | E130 | 209 | 209 | 207.344 | 207.5029 | 205.7496 | 208.7252 | 209.371 | 205.7496 | 209.371 | 1.733% | 208.9462 | 209 | 209 | 0
[15 empty] | E140 | 198 | 198 | 195.53 | 194.6073 | 195.8173 | 197.6748 | 198.5643 | 194.6073 | 198.5643 | 1.999% | 197.9671 | 197.9 | 197.3 | 0 | E140 | 190 | 190 | 188.503 | 188.4525 | 187.7318 | 189.5652 | 190.358 | 187.7318 | 190.358 | 1.384% | 189.7529 | 189.7 | 189.7 | 0
[15 empty] | E150 | 3778 | 3778 | 3803.58 | 3786.0492 | 3769.124 | 3777.7958 | 3775.8216 | 3769.124 | 3803.58 | 0.9119% | 3778.3318 | 3778.2 | 3779 | 0 | E150 | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.1214 | 3636.9245 | 3636.3775 | 3635.1214 | 3637 | 0.05165% | 3637.1129 | 3637.1 | 3637.1 | 0
[15 empty] | E160 | 3761 | 3761 | 3777.178 | 3769.0504 | 3751.3173 | 3760.8682 | 3759.6868 | 3751.3173 | 3777.178 | 0.6875% | 3761.3053 | 3761.1 | 3760.8 | 0 | E160 | 3632 | 3632 | 3630.452 | 3631.5944 | 3629.9738 | 3631.7568 | 3631.4181 | 3629.9738 | 3632 | 0.05579% | 3631.9893 | 3631.9 | 3631.9 | 0
[15 empty] | E165 | 3798 | 3798 | 3828.258 | 3808.6166 | 3788.6753 | 3797.8685 | 3795.9117 | 3788.6753 | 3828.258 | 1.042% | 3797.7525 | 3798.1 | 3798.6 | 0 | E165 | 3649 | 3649 | 3646.871 | 3648.007 | 3645.9633 | 3648.5098 | 3647.9605 | 3645.9633 | 3649 | 0.08323% | 3648.6381 | 3648.7 | 3648.7 | 0
[15 empty] | E170 | 1493 | 1493 | 1486.857 | 1497.6553 | 1485.2201 | 1492.4851 | 1492.423 | 1485.2201 | 1497.6553 | 0.8329% | 1493.027 | 1492.7 | 1493.1 | 0 | E170 | 1420 | 1420 | 1418.151 | 1418.5229 | 1417.5137 | 1419.3245 | 1419.421 | 1417.5137 | 1420 | 0.1752% | 1419.5129 | 1419.5 | 1419.5 | 0
[15 empty] | E180 | 1537 | 1538 | 1553.184 | 1606.6823 | 1523.978 | 1537.8115 | 1537.3001 | 1523.978 | 1606.6823 | 5.378% | 1537.7939 | 1538.1 | 1537.7 | 0 | E180 | 1420 | 1420 | 1418.052 | 1418.5229 | 1417.5533 | 1419.3245 | 1419.1707 | 1417.5533 | 1420 | 0.1724% | 1419.5129 | 1419.5 | 1419.5 | 0
[15 empty] | E185 | 1548 | 1578 | 1608.094 | 1652.6964 | 1564.7043 | 1577.7283 | 1577.1233 | 1548 | 1652.6964 | 6.636% | 1577.6007 | 1578.1 | 1577.7 | 0 | E185 | 1439 | 1439 | 1436.849 | 1437.2802 | 1435.5625 | 1438.4832 | 1438.2925 | 1435.5625 | 1439 | 0.2389% | 1438.7062 | 1438.7 | 1438.7 | 0
[15 empty] | E190 | 208 | 208 | 203.007 | 212.1923 | 204.2038 | 207.5889 | 208.0235 | 203.007 | 212.1923 | 4.42% | 207.8123 | 207.7 | 207.9 | 0 | E190 | 190 | 190 | 188.49 | 188.4525 | 187.7391 | 189.5652 | 189.8558 | 187.7391 | 190 | 1.191% | 189.7529 | 189.7 | 189.7 | 0
[15 empty] | E195 | 232 | 232 | 225.64 | 235.0528 | 227.0242 | 231.3508 | 231.7335 | 225.64 | 235.0528 | 4.063% | 231.645 | 231.6 | 231.6 | 0 | E195 | 209 | 209 | 207.326 | 207.5029 | 205.7557 | 208.7252 | 208.942 | 205.7557 | 209 | 1.553% | 208.9462 | 209 | 209 | 0
[15 empty] | E200 | 4276 | 4215 | 4313.176 | 4302.755 | 4262.9069 | 4276.5408 | 4276.5408 | 4215 | 4313.176 | 2.296% | 4276.6945 | 4276.8 | 4276.8 | 0 | E200 | 4122 | 4062 | 4120.502 | 4121.6295 | 4119.9223 | 4121.9808 | 4121.9808 | 4062 | 4122 | 1.456% | 4122.2309 | 4122.2 | 4122.2 | 0
[15 empty] | Coil Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | Zone Load, Latent (kWh,thermal) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 3.3138e-14 |  | 0 | 0 | 0 | 0 | E100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 2.6912e-15 |  | 0 | 0 | 0 | 0 | E110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 3.8103e-15 |  | 0 | 0 | 0 | 0 | E120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E130 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 3.1415e-14 |  | 0 | 0 | 0 | 0 | E130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E140 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | -2.7533e-16 | 0 |  | 0 | 0 | 0 | 0 | E140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E150 | 739 | 739 | 739.2 | 741.5006 | 739.1972 | 739.2 | 739.2069 | 739 | 741.5006 | 0.3383% | 739.1956 | 739.2 | 739.4 | 0 | E150 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2 | 0
[15 empty] | E160 | 740 | 739 | 739.2 | 739.449 | 739.1972 | 739.2 | 739.1947 | 739 | 740 | 0.1353% | 739.2396 | 739.2 | 739.1 | 0 | E160 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2 | 0
[15 empty] | E165 | 740 | 739 | 739.2 | 740.3283 | 739.1977 | 739.2 | 739.1892 | 739 | 740.3283 | 0.1797% | 739.2454 | 739.2 | 739.3 | 0 | E165 | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2 | 0
[15 empty] | E170 | 740 | 739 | 739.2 | 738.8628 | 739.2008 | 739.2 | 739.2115 | 738.8628 | 740 | 0.1538% | 739.3157 | 739.2 | 739.4 | 0 | E170 | 739 | 739 | 739.2 | 739.449 | 739.2 | 739.2 | 739.2 | 739 | 739.449 | 0.06074% | 739.2 | 739.2 | 739.2 | 0
[15 empty] | E180 | 2958 | 2957 | 2956.8 | 2927.9015 | 2956.7927 | 2956.8 | 2956.7992 | 2927.9015 | 2958 | 1.018% | 2957.4713 | 2956.8 | 2956.1 | 0 | E180 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8 | 0
[15 empty] | E185 | 2959 | 2957 | 2956.8 | 2929.9531 | 2956.7993 | 2956.8 | 2956.8195 | 2929.9531 | 2959 | 0.9821% | 2957.5224 | 2956.8 | 2956.2 | 0 | E185 | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.7866 | 2957.5029 | 0.02423% | 2956.8 | 2956.8 | 2956.8 | 0
[15 empty] | E190 | 370 | 370 | 369.6 | 366.354 | 369.6039 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8 | 0 | E190 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6 | 0
[15 empty] | E195 | 370 | 370 | 369.6 | 366.6471 | 369.6221 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9068% | 369.7294 | 369.6 | 369.6 | 0 | E195 | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 367 | 370 | 0.8117% | 369.6 | 369.6 | 369.6 | 0
[15 empty] | E200 | 1222 | 1221 | 1221 | 1219.2263 | 1220.9837 | 1221.024 | 1221.024 | 1219.2263 | 1222 | 0.2271% | 1221.1063 | 1221 | 1221 | 0 | E200 | 1221 | 1221 | 1221.024 | 1221.2778 | 1220.9824 | 1221.024 | 1221.024 | 1220.9824 | 1221.2778 | 0.0242% | 1221.024 | 1221 | 1221 | 0
[17 empty] | results5-3.xls q:bc77..br147; 10/15/02 | [14 empty] | results5-3.xls q:bt77..ch147; 10/15/02
[15 empty] | Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal) | [7 empty] | Statistics, All Results | [6 empty] | Latent Coil - Zone Load, (Should be 0) (kWh,thermal) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 144 | 144 | 187.05 | 138.6284 | 143.5848 | 143.6534 | 142.3632 | 138.6284 | 187.05 | 33.61% | 144.0536 | 144.1 | 144.1 | 0 | E100 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 3.3138e-14 |  | 0 | 0 | 0 | 0
[15 empty] | E110 | 128 | 129 | 167.979 | 118.9918 | 127.5927 | 127.6867 | 126.6828 | 118.9918 | 167.979 | 38.23% | 128.1309 | 127.9 | 128.2 | 0 | E110 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 2.6912e-15 |  | 0 | 0 | 0 | 0
[15 empty] | E120 | 117 | 117 | 133.008 | 107.5615 | 116.438 | 116.6726 | 115.4889 | 107.5615 | 133.008 | 21.77% | 116.9127 | 116.9 | 116.6 | 0 | E120 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 3.8103e-15 |  | 0 | 0 | 0 | 0
[15 empty] | E130 | 10 | 10 | 8.434 | 7.6202 | 10.2115 | 10.2601 | 10.3985 | 7.6202 | 10.3985 | 26.69% | 10.4079 | 10.3 | 10.2 | 0 | E130 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 3.1415e-14 |  | 0 | 0 | 0 | 0
[15 empty] | E140 | 8 | 8 | 7.027 | 6.1547 | 8.0856 | 8.1097 | 8.2063 | 6.1547 | 8.2063 | 24.98% | 8.2142 | 8.2 | 7.6 | 0 | E140 | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | -2.7533e-16 | 0 |  | 0 | 0 | 0 | 0
[15 empty] | E150 | 141 | 141 | 167.979 | 149.4725 | 134.0026 | 140.8714 | 139.4441 | 134.0026 | 167.979 | 24.06% | 141.2189 | 141.1 | 141.9 | 0 | E150 | 0 | 0 | 0 | 2.0516 | 0.00057016 | 0 | 0.00687 | 0 | 2.0516 |  | -0.0044111 | 0 | 0.2 | 0
[15 empty] | E160 | 129 | 129 | 146.726 | 137.456 | 121.3436 | 129.1114 | 128.2687 | 121.3436 | 146.726 | 19.63% | 129.316 | 129.2 | 128.9 | 0 | E160 | 1 | 0 | 0 | 0 | 0.00054522 | 0 | -0.00534 | -0.00534 | 1 |  | 0.039573 | 0 | -0.1 | 0
[15 empty] | E165 | 149 | 149 | 181.387 | 160.6096 | 142.712 | 149.3587 | 147.9512 | 142.712 | 181.387 | 25.94% | 149.1144 | 149.4 | 149.9 | 0 | E165 | 1 | 0 | 0 | 0.87925 | 0.0010962 | 0 | -0.01082 | -0.01082 | 1 |  | 0.045435 | 0 | 0.1 | 0
[15 empty] | E170 | 73 | 73 | 68.706 | 79.1325 | 67.7064 | 73.1606 | 73.002 | 67.7064 | 79.1325 | 15.54% | 73.5141 | 73.2 | 73.6 | 0 | E170 | 1 | 0 | 0 | -0.58617 | 0.00076678 | 0 | 0.01152 | -0.58617 | 1 |  | 0.1157 | 0 | 0.2 | 0
[15 empty] | E180 | 117 | 118 | 135.132 | 188.1594 | 106.4247 | 118.487 | 118.1294 | 106.4247 | 188.1594 | 69.1% | 118.281 | 118.6 | 118.2 | 0 | E180 | 1 | 0 | 0 | -29.6014 | 0.0061807 | 0 | -0.00076 | -29.6014 | 1 |  | 0.67126 | 0 | -0.7 | 0
[15 empty] | E185 | 109 | 139 | 171.245 | 215.4162 | 129.1418 | 139.2451 | 138.8308 | 109 | 215.4162 | 76.62% | 138.8945 | 139.4 | 139 | 0 | E185 | 2 | 0 | 0 | -27.5498 | 0.012727 | 0 | 0.01946 | -27.5498 | 2 |  | 0.72237 | 0 | -0.6 | 0
[15 empty] | E190 | 18 | 18 | 14.517 | 23.7397 | 16.4646 | 18.0237 | 18.1676 | 14.517 | 23.7397 | 51.07% | 18.0594 | 18 | 18.2 | 0 | E190 | 3 | 0 | 0 | -3.2239 | 0.0048306 | 0 | 0.046846 | -3.2239 | 3 |  | 0.11557 | 0 | 0.2 | 0
[15 empty] | E195 | 23 | 23 | 18.314 | 27.5498 | 21.2685 | 22.6256 | 22.7915 | 18.314 | 27.5498 | 40.69% | 22.6987 | 22.6 | 22.6 | 0 | E195 | 3 | 0 | 0 | -2.9308 | 0.023067 | 0 | 0.0055 | -2.9308 | 3 |  | 0.1294 | 0 | 0 | 0
[15 empty] | E200 | 154 | 153 | 192.674 | 181.1254 | 142.9847 | 154.56 | 154.56 | 142.9847 | 192.674 | 32.17% | 154.4636 | 154.6 | 154.6 | 0 | E200 | 1 | 0 | -0.024 | -2.0516 | 0.0013081 | 0 | 0 | -2.0516 | 1 |  | 0.082262 | 0 | 0 | 0
Zone Loads: Total, Sensible, and Latent
COP: Mean, and (Max-Min)/Mean
Mean COP | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 2.39 | 2.389 | 2.4304 | 2.4064 | 2.4031 | 2.4017 | 2.4184 | 2.389 | 2.4304 | 1.733% | 2.3889 | 2.39 | 2.39 | 0
E110 | 3.38 | 3.342 | 3.4589 | 3.4146 | 3.3994 | 3.4087 | 3.4271 | 3.342 | 3.4589 | 3.459% | 3.3795 | 3.38 | 3.38 | 0
E120 | 3.59 | 3.59 | 3.6139 | 3.623 | 3.606 | 3.6054 | 3.6313 | 3.59 | 3.6313 | 1.15% | 3.5865 | 3.59 | 3.59 | 0
E130 | 1.91 | 1.909 | 1.9752 | 1.953 | 1.903 | 1.9198 | 1.9163 | 1.903 | 1.9752 | 3.822% | 1.8895 | 1.91 | 1.91 | 0
E140 | 2.77 | 2.734 | 2.9151 | 2.854 | 2.7701 | 2.7974 | 2.7996 | 2.734 | 2.9151 | 6.585% | 2.7502 | 2.77 | 2.77 | 0
E150 | 3.62 | 3.63 | 3.6675 | 3.7 | 3.6525 | 3.6496 | 3.6734 | 3.62 | 3.7 | 2.205% | 3.6273 | 3.63 | 3.63 | 0
E160 | 3.84 | 3.84 | 3.8658 | 3.95 | 3.8589 | 3.8452 | 3.8599 | 3.84 | 3.95 | 2.87% | 3.8329 | 3.84 | 3.84 | 0
E165 | 2.92 | 2.92 | 2.9514 | 2.9853 | 2.9399 | 2.9257 | 2.9449 | 2.92 | 2.9853 | 2.228% | 2.9295 | 2.93 | 2.93 | 0
E170 | 3.38 | 3.39 | 3.4423 | 3.477 | 3.3937 | 3.3944 | 3.4033 | 3.38 | 3.477 | 2.881% | 3.3672 | 3.39 | 3.39 | 0
E180 | 4.04 | 4.04 | 4.0842 | 4.026 | 4.0416 | 4.0472 | 4.055 | 4.026 | 4.0842 | 1.44% | 4.0423 | 4.04 | 4.04 | 0
E185 | 2.85 | 2.85 | 2.8744 | 2.823 | 2.8512 | 2.8512 | 2.8574 | 2.823 | 2.8744 | 1.805% | 2.8458 | 2.85 | 2.85 | 0
E190 | 3.41 | 3.41 | 3.4865 | 3.457 | 3.395 | 3.4096 | 3.4048 | 3.395 | 3.4865 | 2.701% | 3.3865 | 3.41 | 3.41 | 0
E195 | 2.31 | 2.31 | 2.3598 | 2.337 | 2.3041 | 2.3158 | 2.3054 | 2.3041 | 2.3598 | 2.428% | 2.2944 | 2.31 | 2.31 | 0
E200 | 3.62 | 3.61 | 3.6677 | 3.708 | 3.6447 | 3.6102 | 3.6102 | 3.61 | 3.708 | 2.707% | 3.6206 | 3.62 | 3.62 | 0
(Max - Min)/Mean COP | [7 empty] | Statistics, All Results
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
| EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
E100 | 0 | 0.00083717 | 0.0015062 | 0.0012467 | 0.0031826 | 0 | 0 | 0 | 0.0031826 |  | 0 | 0 | 0.00012552 | #DIV/0!
E110 | 0 | 0.010473 | 0.0017378 | 0.0011714 | 0.0025513 | 0 | 0.010592 | 0 | 0.010592 |  | 0 | 0 | 0.00038462 | #DIV/0!
E120 | 0 | 0.0036212 | 0.00079758 | 0.0011041 | 0.0025503 | 0 | 0.012271 | 0 | 0.012271 |  | 0 | 0 | 0.00030641 | #DIV/0!
E130 | 0 | 0.03824 | 0.012602 | 0.0087046 | 0.0043691 | 0 | 0.17198 | 0 | 0.17198 |  | 0 | 0 | -5.2356e-05 | #DIV/0!
E140 | 0 | 0.055962 | 0.010989 | 0.018921 | 0.003545 | 0 | 0.20433 | 0 | 0.20433 |  | 0 | 0 | 3.6101e-05 | #DIV/0!
E150 | 0.0027624 | 0.0027548 | 0.0014674 | 0.0048649 | 0.0052381 | 0 | 0.0092759 | 0 | 0.0092759 |  | 0 | 0 | 0.00096419 | #DIV/0!
E160 | 0.0026042 | 0.0052083 | 0.0010614 | 0.0032911 | 0.0057024 | 0 | 0.010193 | 0 | 0.010193 |  | 0 | 0 | 0.00026042 | #DIV/0!
E165 | 0.010274 | 0.0034247 | 0.0012002 | 0.0026798 | 0.006025 | 0 | 0.0084429 | 0 | 0.010274 |  | 0 | 0 | 0.00030717 | #DIV/0!
E170 | 0 | 0.0058997 | 0.0021466 | 0.0040265 | 0.0081135 | 0 | 0.043444 | 0 | 0.043444 |  | 0 | 0 | 0.00026549 | #DIV/0!
E180 | 0.0049505 | 0.0024752 | 0.0023307 | 0.009687 | 0.010241 | 0 | 0.011687 | 0 | 0.011687 |  | 0 | 0 | 4.9505e-05 | #DIV/0!
E185 | 0.0070175 | 0.0035088 | 0.0023597 | 0.010273 | 0.011693 | 0 | 0.0091078 | 0 | 0.011693 |  | 0 | 0 | 0.00017544 | #DIV/0!
E190 | 0 | 0.02346 | 0.0071705 | 0.018802 | 0.040402 | 0 | 0.10066 | 0 | 0.10066 |  | 0 | 0 | -8.7977e-05 | #DIV/0!
E195 | 0 | 0.017316 | 0.0078108 | 0.016688 | 0.079144 | 0 | 0.08606 | 0 | 0.08606 |  | 0 | 0 | 0.00012987 | #DIV/0!
E200 | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.0060171 | 0 | 0 | -1.2839e-05 | 0.0060171 |  | 0 | 0 | 8.2873e-05 | #DIV/0!
results5-3.xls q:a185..p220; 10/15/02
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
[15 empty] | Mean IDB (°C) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6346 | 22.1999 | 22.6346 | 1.958% | 22.2 | 22.2 | 22.216 | 0
[15 empty] | E110 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.1999 | 22.2 | 22.5242 | 22.1999 | 22.5242 | 1.461% | 22.2 | 22.2 | 22.214 | 0
[15 empty] | E120 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 27.0785 | 1.418% | 26.7 | 26.7 | 26.712 | 0
[15 empty] | E130 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 21.6377 | 22.2 | 2.533% | 22.2 | 22.2 | 22.187 | 0
[15 empty] | E140 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 21.5097 | 22.2 | 3.11% | 22.2 | 22.2 | 22.185 | 0
[15 empty] | E150 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1772 | 22.2 | 22.6771 | 22.1772 | 22.6771 | 2.252% | 22.2 | 22.2 | 22.216 | 0
[15 empty] | E160 | 26.7 | 26.7 | 26.8 | 26.7222 | 26.6723 | 26.7 | 26.9948 | 26.6723 | 26.9948 | 1.208% | 26.7 | 26.7 | 26.714 | 0
[15 empty] | E165 | 23.3 | 23.3 | 23.4 | 23.4444 | 23.28 | 23.3 | 23.7805 | 23.28 | 23.7805 | 2.148% | 23.3 | 23.3 | 23.317 | 0
[15 empty] | E170 | 22.2 | 22.2 | 22.2 | 22.2222 | 22.1809 | 22.2 | 22.1169 | 22.1169 | 22.2222 | 0.4746% | 22.2 | 22.2 | 22.199 | 0
[15 empty] | E180 | 22.2 | 22.2 | 22.3 | 22.2778 | 22.157 | 22.2 | 22.3344 | 22.157 | 22.3344 | 0.7991% | 22.2 | 22.2 | 22.205 | 0
[15 empty] | E185 | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1672 | 22.2 | 22.3682 | 22.1672 | 22.3682 | 0.9053% | 22.2 | 22.2 | 22.206 | 0
[15 empty] | E190 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.1945 | 22.2 | 21.9469 | 21.9469 | 22.2 | 1.14% | 22.2 | 22.2 | 22.194 | 0
[15 empty] | E195 | 22.2 | 22.2 | 22.1 | 22.1111 | 22.1956 | 22.2 | 22.0113 | 22.0113 | 22.2 | 0.8501% | 22.2 | 22.2 | 22.195 | 0
[15 empty] | E200 | 26.7 | 26.7 | 26.8 | 26.7778 | 26.6624 | 26.7339 | 26.7339 | 26.6624 | 26.8 | 0.5154% | 26.7 | 26.7 | 26.713 | 0
[15 empty] | (Max - Min)/Mean IDB (°C) | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 0 | 0 | 0 | 0 | 7.6728e-07 | 0 | 0.049482 | 0 | 0.049482 |  | 0 | 0 | 0.0017105 | #DIV/0!
[15 empty] | E110 | 0 | 0 | 0 | 0 | 3.9213e-07 | 0 | 0.047948 | 0 | 0.047948 |  | 0 | 0 | 0.0018907 | #DIV/0!
[15 empty] | E120 | 0 | 0 | 0 | 0 | 2.5833e-09 | 0 | 0.077183 | 0 | 0.077183 |  | 0 | 0 | 0.0017221 | #DIV/0!
[15 empty] | E130 | 0 | 0 | 0 | 0 | 2.8008e-09 | 0 | 0.056383 | 0 | 0.056383 |  | 0 | 0 | 0.0013521 | #DIV/0!
[15 empty] | E140 | 0 | 0 | 0 | 0 | 1.0566e-09 | 0 | 0.069271 | 0 | 0.069271 |  | 0 | 0 | 0.0015326 | #DIV/0!
[15 empty] | E150 | 0 | 0 | 0 | 0 | 9.1726e-05 | 0 | 0.053799 | 0 | 0.053799 |  | 0 | 0 | 0.0017105 | #DIV/0!
[15 empty] | E160 | 0 | 0 | 0 | 0 | 0.00019269 | 0 | 0.045194 | 0 | 0.045194 |  | 0 | 0 | 0.0015722 | #DIV/0!
[15 empty] | E165 | 0 | 0 | 0 | 0 | 0.00027951 | 0 | 0.051303 | 0 | 0.051303 |  | 0 | 0 | 0.0015439 | #DIV/0!
[15 empty] | E170 | 0 | 0 | 0 | 0 | 7.1143e-05 | 0 | 0.049736 | 0 | 0.049736 |  | 0 | 0 | 0.0013064 | #DIV/0!
[15 empty] | E180 | 0 | 0 | 0 | 0 | 0.00014949 | 0 | 0.034924 | 0 | 0.034924 |  | 0 | 0 | 0.00081063 | #DIV/0!
[15 empty] | E185 | 0 | 0 | 0 | 0 | 0.00022693 | 0 | 0.021459 | 0 | 0.021459 |  | 0 | 0 | 0.00072053 | #DIV/0!
[15 empty] | E190 | 0 | 0 | 0 | 0 | 1.2134e-05 | 0 | 0.02825 | 0 | 0.02825 |  | 0 | 0 | 0.00072092 | #DIV/0!
[15 empty] | E195 | 0 | 0 | 0 | 0 | 1.7277e-05 | 0 | 0.022716 | 0 | 0.022716 |  | 0 | 0 | 0.00063077 | #DIV/0!
[15 empty] | E200 | 0 | 0 | 0 | 0 | 8.3697e-05 | 0 | 0 | 0 | 8.3697e-05 |  | 0 | 0 | 0 | #DIV/0!
Humidity Ratio: Mean and (Max-Min)/Mean
[15 empty] | Mean Humidity Ratio | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 0.0075 | 0.00691 | 0.0076 | 0.0074 | 0.0074522 | 0.0075036 | 0.0075088 | 0.00691 | 0.0076 | 9.29% | 0.0074274 | 0.00734 | 0.007339 | 0
[15 empty] | E110 | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065611 | 0.0065938 | 0.0066309 | 0.0064 | 0.0070296 | 9.659% | 0.0065187 | 0.0064 | 0.006411 | 0
[15 empty] | E120 | 0.008 | 0.007 | 0.0078 | 0.0078 | 0.008011 | 0.0079506 | 0.0079517 | 0.007 | 0.008011 | 12.83% | 0.0078783 | 0.00786 | 0.007873 | 0
[15 empty] | E130 | 0.0075 | 0.00691 | 0.0076 | 0.0073 | 0.0074578 | 0.0075036 | 0.0075194 | 0.00691 | 0.0076 | 9.29% | 0.0074274 | 0.00734 | 0.007339 | 0
[15 empty] | E140 | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065668 | 0.0065938 | 0.0065941 | 0.0064 | 0.0070601 | 10.13% | 0.0065187 | 0.0064 | 0.006402 | 0
[15 empty] | E150 | 0.0083 | 0.00853 | 0.0082 | 0.0083 | 0.0083955 | 0.0083236 | 0.0085152 | 0.0082 | 0.00853 | 4.011% | 0.0082272 | 0.0082 | 0.00821 | 0
[15 empty] | E160 | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.01024 | 0.010069 | 0.010236 | 0.009701 | 0.01024 | 5.409% | 0.009969 | 0.00994 | 0.009946 | 0
[15 empty] | E165 | 0.0093 | 0.00985 | 0.0090039 | 0.0092 | 0.0093667 | 0.0093021 | 0.0095112 | 0.0090039 | 0.00985 | 9.128% | 0.0092694 | 0.0092 | 0.009208 | 0
[15 empty] | E170 | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.01055 | 0.010471 | 0.010525 | 0.010471 | 0.0107 | 2.211% | 0.010367 | 0.01045 | 0.010451 | 0
[15 empty] | E180 | 0.0164 | 0.0164 | 0.016614 | 0.0164 | 0.016161 | 0.01631 | 0.016404 | 0.016161 | 0.016614 | 2.796% | 0.01619 | 0.01623 | 0.01623 | 0
[15 empty] | E185 | 0.0162 | 0.0171 | 0.016441 | 0.0162 | 0.016049 | 0.016151 | 0.016279 | 0.016049 | 0.0171 | 6.545% | 0.016056 | 0.01605 | 0.016059 | 0
[15 empty] | E190 | 0.016 | 0.0161 | 0.016254 | 0.0159 | 0.015867 | 0.015921 | 0.015707 | 0.015707 | 0.016254 | 3.465% | 0.015796 | 0.0159 | 0.015891 | 0
[15 empty] | E195 | 0.0156 | 0.0164 | 0.015764 | 0.0155 | 0.015464 | 0.01547 | 0.015326 | 0.015326 | 0.0164 | 6.988% | 0.015368 | 0.01544 | 0.015439 | 0
[15 empty] | E200 | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.011419 | 0.011281 | 0.011281 | 0.010933 | 0.0115 | 5.096% | 0.011129 | 0.01109 | 0.011099 | 0
[15 empty] | (Max - Min)/Mean Humidity Ratio | [7 empty] | Statistics, All Results
[16 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | (Max-Min) |  | Analytical |  | your
[16 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | /Analytical | TUD | HTAL1 | HTAL2 | program
[15 empty] | E100 | 0 | 0.021708 | 0 | 0 | 4.0271e-14 | 0 | 0 | 0 | 0.021708 |  | 0 | 0 | 0 | #DIV/0!
[15 empty] | E110 | 0 | 0.021676 | 0.014226 | 0 | 4.4154e-14 | 0 | 0 | 0 | 0.021676 |  | 0 | 0 | 0 | #DIV/0!
[15 empty] | E120 | 0 | 0 | 0 | 0 | 2.88e-14 | 0 | 0 | 0 | 2.88e-14 |  | 0 | 0 | 0 | #DIV/0!
[15 empty] | E130 | 0 | 0.01013 | 0 | 0 | 1.006e-13 | 0 | 0 | 0 | 0.01013 |  | 0 | 0 | 0 | #DIV/0!
[15 empty] | E140 | 0 | 0.011561 | 0.014164 | 0 | 8.374e-14 | 0 | 0 | 0 | 0.014164 |  | 0 | 0 | 0 | #DIV/0!
[15 empty] | E150 | 0.012048 | 0 | 0 | 0 | 0.010954 | 0 | 0.013153 | 0 | 0.013153 |  | 0 | 0 | 0.00036541 | #DIV/0!
[15 empty] | E160 | 0.019608 | 0 | 0.010308 | 0.010101 | 0.011333 | 0 | 0.010747 | 0 | 0.019608 |  | 0 | 0 | 0.00040217 | #DIV/0!
[15 empty] | E165 | 0.010753 | 0.0010152 | 0.011106 | 0 | 0.011171 | 0 | 0.012512 | 0 | 0.012512 |  | 0 | 0 | 0.0003258 | #DIV/0!
[15 empty] | E170 | 0 | 0 | 0.0095289 | 0 | 0.011126 | 0 | 0.023752 | 0 | 0.023752 |  | 0 | 0 | 0.00057411 | #DIV/0!
[15 empty] | E180 | 0.018293 | 0 | 0.012038 | 0.012195 | 0.0097718 | 0 | 0.040234 | 0 | 0.040234 |  | 0 | 0 | 0.00092421 | #DIV/0!
[15 empty] | E185 | 0.012346 | 0.005848 | 0.018247 | 0.012346 | 0.012009 | 0 | 0.024571 | 0 | 0.024571 |  | 0 | 0 | 0.00080951 | #DIV/0!
[15 empty] | E190 | 0 | 0 | 0.018457 | 0.018868 | 0.024976 | 0 | 0.031196 | 0 | 0.031196 |  | 0 | 0 | 0.00075514 | #DIV/0!
[15 empty] | E195 | 0 | 0.0060976 | 0.01903 | 0.019355 | 0.039296 | 0 | 0.024142 | 0 | 0.039296 |  | 0 | 0 | 0.00064771 | #DIV/0!
[15 empty] | E200 | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.010952 | 0 | 0 | 0 | 0.017544 |  | 0 | 0 | 0 | #DIV/0!
results5-3.xls q:bc233..br304; 10/15/02
Sensitivities for COP and Coil Loads
[45 empty] | Sensitivities for Space Cooling Electricity Consumption | [14 empty] | Sensitivities for COP and Coil Loads
[45 empty] | Delta Qtot (kWh,e) | [7 empty] | Statistics, All Results | [6 empty] | Delta COP (kWh,t) | [7 empty] | Statistics, All Results
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program
[45 empty] | E110-E100 | -454 | -441 | -459.621 | -454 | -450.8529 | -455.3055 | -449.9711 | -459.621 | -441 | 4.099% | -454.3131 | -453.6 | -453.2 | 0 | E110-E100 | 0.99 | 0.953 | 1.0285 | 1.0082 | 0.99634 | 1.0069 | 1.0087 | 0.953 | 1.0285 | 7.622% | 0.99059 | 0.99 | 0.99 | 0
[45 empty] | E120-E110 | -65 | -77 | -50.092 | -62 | -62.6934 | -59.6584 | -60.3021 | -77 | -50.092 | 42.34% | -63.5575 | -66.2 | -66.4 | 0 | E120-E110 | 0.21 | 0.248 | 0.155 | 0.20837 | 0.2066 | 0.19677 | 0.20416 | 0.155 | 0.248 | 44.92% | 0.20704 | 0.21 | 0.21 | 0
[45 empty] | E120-E100 | -519 | -518 | -509.713 | -516 | -513.5463 | -514.9639 | -510.2732 | -519 | -509.713 | 1.793% | -517.8706 | -519.8 | -519.6 | 0 | E120-E100 | 1.2 | 1.201 | 1.1835 | 1.2166 | 1.2029 | 1.2037 | 1.2129 | 1.1835 | 1.2166 | 2.763% | 1.1976 | 1.2 | 1.2 | 0
[45 empty] | E130-E100 | -1421 | -1421 | -1415.398 | -1413 | -1412.0645 | -1413.5415 | -1401.8208 | -1421 | -1401.8208 | 1.351% | -1419.9663 | -1421.3 | -1421.1 | 0 | E130-E100 | -0.48 | -0.48 | -0.4552 | -0.45341 | -0.50009 | -0.48198 | -0.50212 | -0.50212 | -0.45341 | 9.754% | -0.49937 | -0.48 | -0.48 | 0
[45 empty] | E140-E130 | -42 | -40 | -40.411 | -40 | -40.3501 | -40.9605 | -41.4733 | -42 | -40 | 4.809% | -41.5864 | -41 | -41.2 | 0 | E140-E130 | 0.86 | 0.825 | 0.9399 | 0.901 | 0.86717 | 0.87767 | 0.88334 | 0.825 | 0.9399 | 13.35% | 0.86071 | 0.86 | 0.86 | 0
[45 empty] | E140-E110 | -1009 | -1020 | -996.188 | -999 | -1001.5617 | -999.1966 | -993.323 | -1020 | -993.323 | 2.649% | -1007.2396 | -1008.7 | -1009.1 | 0 | E140-E110 | -0.61 | -0.608 | -0.5438 | -0.56063 | -0.62926 | -0.61124 | -0.6275 | -0.62926 | -0.5438 | 13.58% | -0.62925 | -0.61 | -0.61 | 0
[45 empty] | E150-E110 | 131 | 118 | 141.228 | 118 | 128.2886 | 132.0944 | 129.6472 | 118 | 141.228 | 17.83% | 130.2551 | 129.3 | 129.1 | 0 | E150-E110 | 0.24 | 0.288 | 0.2086 | 0.28537 | 0.2531 | 0.24097 | 0.24631 | 0.2086 | 0.288 | 32.04% | 0.24783 | 0.25 | 0.25 | 0
[45 empty] | E160-E150 | -68 | -68 | -64.794 | -76 | -65.3881 | -62.3216 | -58.7295 | -76 | -58.7295 | 26.15% | -66.05 | -67.2 | -67.6 | 0 | E160-E150 | 0.22 | 0.21 | 0.1983 | 0.25 | 0.20639 | 0.19555 | 0.18654 | 0.18654 | 0.25 | 30.86% | 0.20563 | 0.21 | 0.21 | 0
[45 empty] | E165-E160 | 362 | 362 | 361.817 | 363 | 359.356 | 362.977 | 357.0433 | 357.0433 | 363 | 1.667% | 357.3902 | 360.4 | 360.7 | 0 | E165-E160 | -0.92 | -0.92 | -0.9144 | -0.96474 | -0.91897 | -0.91948 | -0.91505 | -0.96474 | -0.9144 | 5.572% | -0.90343 | -0.91 | -0.91 | 0
[45 empty] | E170-E150 | -570 | -569 | -573.348 | -563 | -562.1205 | -563.1461 | -555.7842 | -573.348 | -555.7842 | 3.107% | -565.3727 | -568.8 | -568.7 | 0 | E170-E150 | -0.24 | -0.24 | -0.2252 | -0.223 | -0.25878 | -0.25525 | -0.27013 | -0.27013 | -0.223 | 18.12% | -0.26014 | -0.24 | -0.24 | 0
[45 empty] | E180-E150 | -125 | -125 | -125.315 | -103 | -115.294 | -117.7844 | -111.5753 | -125.315 | -103 | 18.02% | -123.824 | -124.2 | -124.6 | 0 | E180-E150 | 0.42 | 0.41 | 0.4167 | 0.326 | 0.3891 | 0.39757 | 0.38162 | 0.326 | 0.42 | 22.65% | 0.41502 | 0.41 | 0.41 | 0
[45 empty] | E180-E170 | 445 | 444 | 448.033 | 460 | 446.8265 | 445.3617 | 444.2089 | 444 | 460 | 3.624% | 441.5487 | 444.6 | 444.1 | 0 | E180-E170 | 0.66 | 0.65 | 0.6419 | 0.549 | 0.64788 | 0.65282 | 0.65175 | 0.549 | 0.66 | 16.44% | 0.67516 | 0.65 | 0.65 | 0
[45 empty] | E185-E180 | 461 | 461 | 464.046 | 467 | 458.2115 | 460.255 | 458.3596 | 458.2115 | 467 | 1.902% | 461.9737 | 461.1 | 461 | 0 | E185-E180 | -1.19 | -1.19 | -1.2098 | -1.203 | -1.1904 | -1.196 | -1.1976 | -1.2098 | -1.19 | 1.655% | -1.1965 | -1.19 | -1.19 | 0
[45 empty] | E190-E180 | -919 | -918 | -916.89 | -920 | -918.1623 | -917.2731 | -914.9174 | -920 | -914.9174 | 0.554% | -917.493 | -918.2 | -917.7 | 0 | E190-E180 | -0.63 | -0.63 | -0.5977 | -0.569 | -0.64659 | -0.63762 | -0.65027 | -0.65027 | -0.569 | 12.39% | -0.65583 | -0.63 | -0.63 | 0
[45 empty] | E190-E140 | 96 | 95 | 95.211 | 94 | 96.394 | 96.2334 | 96.4774 | 94 | 96.4774 | 2.576% | 96.1777 | 95.6 | 95.9 | 0 | E190-E140 | 0.64 | 0.676 | 0.5714 | 0.603 | 0.62487 | 0.61216 | 0.60515 | 0.5714 | 0.676 | 16.44% | 0.63627 | 0.64 | 0.64 | 0
[45 empty] | E195-E190 | 86 | 86 | 84.7 | 86 | 85.546 | 85.7346 | 86.4597 | 84.7 | 86.4597 | 2.023% | 86.9875 | 85.9 | 85.8 | 0 | E195-E190 | -1.1 | -1.1 | -1.1267 | -1.12 | -1.0909 | -1.0938 | -1.0994 | -1.1267 | -1.0909 | 3.276% | -1.0921 | -1.1 | -1.1 | 0
[45 empty] | E195-E185 | -1294 | -1293 | -1296.236 | -1301 | -1290.8277 | -1291.7935 | -1286.8173 | -1301 | -1286.8173 | 1.097% | -1292.4792 | -1293.4 | -1292.9 | 0 | E195-E185 | -0.54 | -0.54 | -0.5146 | -0.48603 | -0.54708 | -0.53547 | -0.55209 | -0.55209 | -0.48603 | 11.98% | -0.55141 | -0.54 | -0.54 | 0
[45 empty] | E195-E130 | 140 | 141 | 139.5 | 140 | 141.5899 | 141.0075 | 141.4638 | 139.5 | 141.5899 | 1.476% | 141.5788 | 140.5 | 140.5 | 0 | E195-E130 | 0.4 | 0.401 | 0.3846 | 0.384 | 0.40112 | 0.39602 | 0.3891 | 0.384 | 0.40112 | 4.227% | 0.40487 | 0.4 | 0.4 | 0
[45 empty] | E200-E100 | -54 | -66 | -52.603 | -79 | -54.8104 | -42.2735 | -31.9443 | -79 | -31.9443 | 85.97% | -54.7376 | -53.4 | -53.5 | 0 | E200-E100 | 1.23 | 1.221 | 1.2373 | 1.3016 | 1.2417 | 1.2084 | 1.1918 | 1.1918 | 1.3016 | 8.915% | 1.2317 | 1.23 | 1.23 | 0
[45 empty] | Del Qcomp (kWh,e) | [7 empty] | Statistics, All Results | [6 empty] | Del Q coil,t (kWh,t) | [7 empty] | Statistics, All Results
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program
[45 empty] | E110-E100 | -430 | -419 | -441.592 | -428 |  | -431.8474 | -426.8936 | -441.592 | -419 | 5.243% | -430.9138 | -429.8 | -429.5 | 0 | E110-E100 | -35 | -34 | -37.89 | -38.3939 | -34.0099 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.51% | -35.1161 | -35.4 | -35.1 | 0
[45 empty] | E120-E110 | -49 | -59 | -15.798 | -45 |  | -43.4717 | -43.903 | -59 | -15.798 | 91.78% | -47.0715 | -50.1 | -50.2 | 0 | E120-E110 | -16 | -17 | -40.1 | -16.4127 | -16.3058 | -16.1818 | -16.4257 | -40.1 | -16 | 147.5% | -16.3418 | -16.2 | -16.8 | 0
[45 empty] | E120-E100 | -479 | -478 | -457.39 | -473 |  | -475.319 | -470.7965 | -479 | -457.39 | 4.521% | -477.9853 | -479.9 | -479.7 | 0 | E120-E100 | -51 | -51 | -77.99 | -54.8066 | -50.3157 | -51.3072 | -51.1386 | -77.99 | -50.3157 | 53.78% | -51.4579 | -51.6 | -51.9 | 0
[45 empty] | E130-E100 | -1224 | -1224 | -1214.26 | -1218 |  | -1217.5188 | -1207.8769 | -1224 | -1207.8769 | 1.318% | -1223.5648 | -1224.6 | -1224.6 | 0 | E130-E100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.7334 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2 | 0
[45 empty] | E140-E130 | -38 | -37 | -38.399 | -37 |  | -37.8005 | -38.2753 | -38.399 | -37 | 3.647% | -38.3628 | -37.9 | -37.9 | 0 | E140-E130 | -21 | -21 | -20.248 | -20.5158 | -20.1438 | -21.3105 | -21.2052 | -21.3105 | -20.1438 | 5.455% | -21.387 | -21.4 | -21.9 | 0
[45 empty] | E140-E110 | -832 | -842 | -811.067 | -827 |  | -823.472 | -819.2586 | -842 | -811.067 | 3.722% | -831.0138 | -832.7 | -833 | 0 | E140-E110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.8672 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568 | 0
[45 empty] | E150-E110 | 111 | 100 | 141.228 | 99 |  | 112.7146 | 110.9181 | 99 | 141.228 | 38.04% | 111.0199 | 110 | 109.8 | 0 | E150-E110 | 752 | 751 | 739.2 | 771.9812 | 745.6367 | 752.3846 | 751.7923 | 739.2 | 771.9812 | 4.358% | 752.2836 | 752.4 | 753 | 0
[45 empty] | E160-E150 | -50 | -50 | -44.419 | -56 |  | -45.0374 | -42.3919 | -56 | -42.3919 | 28.03% | -48.5466 | -49.8 | -50.1 | 0 | E160-E150 | -16 | -17 | -26.402 | -19.0504 | -17.8067 | -16.9277 | -16.1469 | -26.402 | -16 | 61.25% | -16.9825 | -17.1 | -18.4 | 0
[45 empty] | E165-E160 | 333 | 332 | 328.567 | 330 |  | 333.2246 | 328.108 | 328.108 | 333.2246 | 1.558% | 328.3094 | 330.8 | 331.1 | 0 | E165-E160 | 37 | 38 | 51.08 | 40.4455 | 37.3585 | 37.0003 | 36.2193 | 36.2193 | 51.08 | 40.77% | 36.4531 | 37 | 38 | 0
[45 empty] | E170-E150 | -469 | -469 | -468.135 | -459 |  | -463.6356 | -458.1666 | -469 | -458.1666 | 2.325% | -465.9883 | -469.2 | -469.1 | 0 | E170-E150 | -2284 | -2285 | -2316.723 | -2291.0317 | -2283.9004 | -2285.3107 | -2283.394 | -2316.723 | -2283.394 | 1.458% | -2285.1847 | -2285.5 | -2285.8 | 0
[45 empty] | E180-E150 | -91 | -91 | -92.832 | -70 |  | -84.887 | -80.3105 | -92.832 | -70 | 25.14% | -90.836 | -91.2 | -91.5 | 0 | E180-E150 | -22 | -22 | -32.796 | 7.034 | -27.5505 | -22.3843 | -20.9286 | -32.796 | 7.034 | 178.9% | -22.2623 | -22.5 | -24.5 | 0
[45 empty] | E180-E170 | 378 | 378 | 375.303 | 389 |  | 378.7486 | 377.8561 | 375.303 | 389 | 3.651% | 375.1523 | 378 | 377.6 | 0 | E180-E170 | 2262 | 2263 | 2283.927 | 2298.0657 | 2256.3499 | 2262.9264 | 2262.4654 | 2256.3499 | 2298.0657 | 1.843% | 2262.9224 | 2263 | 2261.3 | 0
[45 empty] | E185-E180 | 431 | 431 | 428.419 | 432 |  | 429.7507 | 427.9509 | 427.9509 | 432 | 0.938% | 431.6779 | 430.6 | 430.5 | 0 | E185-E180 | 12 | 40 | 54.91 | 48.0657 | 40.7328 | 39.9168 | 39.8433 | 12 | 54.91 | 107.7% | 39.858 | 40 | 40.1 | 0
[45 empty] | E190-E180 | -771 | -770 | -774.839 | -774 |  | -769.6356 | -767.9826 | -774.839 | -767.9826 | 0.8908% | -769.6508 | -770.4 | -770 | 0 | E190-E180 | -3917 | -3918 | -3937.377 | -3956.0375 | -3906.9631 | -3917.4227 | -3916.4296 | -3956.0375 | -3906.9631 | 1.253% | -3917.7372 | -3917.6 | -3916.1 | 0
[45 empty] | E190-E140 | 81 | 81 | 84.624 | 82 |  | 81.6639 | 81.8837 | 81 | 84.624 | 4.444% | 81.5469 | 81.1 | 81.3 | 0 | E190-E140 | 380 | 379 | 377.077 | 383.939 | 377.9903 | 379.514 | 379.106 | 377.077 | 383.939 | 1.808% | 379.5607 | 379.4 | 380.4 | 0
[45 empty] | E195-E190 | 79 | 79 | 79.444 | 79 |  | 78.9721 | 79.6337 | 78.9721 | 79.6337 | 0.8254% | 80.1527 | 79.2 | 79.1 | 0 | E195-E190 | 24 | 24 | 22.633 | 23.1536 | 22.8387 | 23.7619 | 23.6687 | 22.633 | 24 | 5.733% | 23.8465 | 23.9 | 23.5 | 0
[45 empty] | E195-E185 | -1123 | -1122 | -1123.814 | -1127 |  | -1120.4142 | -1116.2999 | -1127 | -1116.2999 | 0.9544% | -1121.176 | -1121.8 | -1121.4 | 0 | E195-E185 | -3905 | -3934 | -3969.654 | -3980.9496 | -3924.8572 | -3933.5775 | -3932.6042 | -3980.9496 | -3905 | 1.931% | -3933.7487 | -3933.7 | -3932.7 | 0
[45 empty] | E195-E130 | 122 | 123 | 125.669 | 124 |  | 122.8356 | 123.242 | 122 | 125.669 | 2.975% | 123.3368 | 122.4 | 122.5 | 0 | E195-E130 | 383 | 382 | 379.462 | 386.5768 | 380.6852 | 381.9655 | 381.5695 | 379.462 | 386.5768 | 1.862% | 382.0203 | 381.9 | 382 | 0
[45 empty] | E200-E100 | -69 | -79 | -58.431 | -93 |  | -58.3094 | -49.8691 | -93 | -49.8691 | 61.59% | -70.0317 | -68.8 | -68.9 | 0 | E200-E100 | 1698 | 1636 | 1692.73 | 1728.0188 | 1687.1961 | 1697.8282 | 1699.6157 | 1636 | 1728.0188 | 5.421% | 1697.4409 | 1697.4 | 1697.4 | 0
[45 empty] | Del Q IDfan (kWh,e) | [7 empty] | Statistics, All Results | [6 empty] | Del Q coil,s (kWh,t) | [7 empty] | Statistics, All Results
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program
[45 empty] | E110-E100 | -16 | -15 | -12.268 | -19 | -15.9921 | -15.9627 | -15.7035 | -19 | -12.268 | 42.28% | -15.9226 | -16.2 | -16.1 | 0 | E110-E100 | -35 | -34 | -37.89 | -38.3939 | -34.0099 | -35.1254 | -34.7129 | -38.3939 | -34 | 12.51% | -35.1161 | -35.4 | -35.1 | 0
[45 empty] | E120-E110 | -11 | -12 | -23.336 | -12 | -11.1547 | -11.0148 | -11.1592 | -23.336 | -11 | 110% | -11.2183 | -11 | -11 | 0 | E120-E110 | -16 | -17 | -40.1 | -16.4127 | -16.3058 | -16.1818 | -16.4257 | -40.1 | -16 | 147.5% | -16.3418 | -16.2 | -16.8 | 0
[45 empty] | E120-E100 | -27 | -27 | -35.604 | -31 | -27.1468 | -26.9774 | -26.8627 | -35.604 | -26.8627 | 32.21% | -27.1409 | -27.2 | -27.1 | 0 | E120-E100 | -51 | -51 | -77.99 | -54.8066 | -50.3157 | -51.3072 | -51.1386 | -77.99 | -50.3157 | 53.78% | -51.4579 | -51.6 | -51.9 | 0
[45 empty] | E130-E100 | -134 | -134 | -136.869 | -133 | -133.3733 | -133.3883 | -131.9736 | -136.869 | -131.9736 | 3.663% | -133.646 | -133.8 | -133.7 | 0 | E130-E100 | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.7334 | -3580.7513 | -3578.1796 | -3625.692 | -3578.1796 | 1.327% | -3581.0058 | -3581.1 | -3581.2 | 0
[45 empty] | E140-E130 | -2 | -2 | -1.369 | -2 | -2.1259 | -2.1503 | -2.1761 | -2.1761 | -1.369 | 36.79% | -2.1936 | -2.2 | -2.2 | 0 | E140-E130 | -21 | -21 | -20.248 | -20.5158 | -20.1438 | -21.3105 | -21.2052 | -21.3105 | -20.1438 | 5.455% | -21.387 | -21.4 | -21.9 | 0
[45 empty] | E140-E110 | -120 | -121 | -125.97 | -116 | -119.5071 | -119.5759 | -118.4462 | -125.97 | -116 | 8.314% | -119.917 | -119.8 | -119.8 | 0 | E140-E110 | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.8672 | -3566.9364 | -3564.6719 | -3608.05 | -3560.9613 | 1.32% | -3567.2767 | -3567.1 | -3568 | 0
[45 empty] | E150-E110 | 13 | 12 | 0 | 14 | 12.757 | 13.1873 | 12.7446 | 0 | 14 | 107% | 13.0891 | 13.2 | 13.2 | 0 | E150-E110 | 13 | 12 | 0 | 30.4807 | 6.4394 | 13.1846 | 12.5854 | 0 | 30.4807 | 232.9% | 13.088 | 13.2 | 13.7 | 0
[45 empty] | E160-E150 | -12 | -12 | -13.865 | -15 | -11.9691 | -11.7613 | -11.1173 | -15 | -11.1173 | 32.6% | -11.9106 | -11.9 | -11.9 | 0 | E160-E150 | -17 | -17 | -26.402 | -16.9988 | -17.8067 | -16.9277 | -16.1348 | -26.402 | -16.1348 | 60.3% | -17.0265 | -17.1 | -18.2 | 0
[45 empty] | E165-E160 | 20 | 21 | 22.626 | 24 | 20.2354 | 20.246 | 19.6897 | 19.6897 | 24 | 21.78% | 19.7887 | 20.1 | 20.1 | 0 | E165-E160 | 37 | 37 | 51.08 | 39.5662 | 37.3579 | 37.0003 | 36.2248 | 36.2248 | 51.08 | 40.76% | 36.4472 | 37 | 37.8 | 0
[45 empty] | E170-E150 | -68 | -68 | -71.595 | -73 | -67.3106 | -67.7141 | -66.4261 | -73 | -66.4261 | 9.721% | -67.6284 | -67.9 | -67.9 | 0 | E170-E150 | -2285 | -2285 | -2316.723 | -2288.3939 | -2283.904 | -2285.3107 | -2283.3986 | -2316.723 | -2283.3986 | 1.458% | -2285.3048 | -2285.5 | -2285.9 | 0
[45 empty] | E180-E150 | -23 | -22 | -22.104 | -24 | -21.8861 | -22.3857 | -21.2749 | -24 | -21.2749 | 12.14% | -22.4474 | -22.5 | -22.6 | 0 | E180-E150 | -2241 | -2240 | -2250.396 | -2179.3669 | -2245.146 | -2239.9843 | -2238.5215 | -2250.396 | -2179.3669 | 3.17% | -2240.5379 | -2240.1 | -2241.3 | 0
[45 empty] | E180-E170 | 45 | 46 | 49.491 | 49 | 45.4245 | 45.3284 | 45.1513 | 45 | 49.491 | 9.94% | 45.181 | 45.4 | 45.3 | 0 | E180-E170 | 44 | 45 | 66.327 | 109.027 | 38.758 | 45.3264 | 44.8771 | 38.758 | 109.027 | 157% | 44.7669 | 45.4 | 44.6 | 0
[45 empty] | E185-E180 | 21 | 20 | 24.243 | 25 | 20.6754 | 20.7574 | 20.6923 | 20 | 25 | 24.25% | 20.6154 | 20.8 | 20.8 | 0 | E185-E180 | 11 | 40 | 54.91 | 46.0141 | 40.7262 | 39.9168 | 39.8232 | 11 | 54.91 | 110.3% | 39.8069 | 40 | 40 | 0
[45 empty] | E190-E180 | -100 | -101 | -96.662 | -98 | -100.4513 | -100.4635 | -99.9852 | -101 | -96.662 | 4.312% | -100.6027 | -100.6 | -100.5 | 0 | E190-E180 | -1329 | -1330 | -1350.177 | -1394.49 | -1319.7742 | -1330.2227 | -1329.2766 | -1394.49 | -1319.7742 | 5.618% | -1329.9815 | -1330.4 | -1329.8 | 0
[45 empty] | E190-E140 | 10 | 10 | 7.204 | 8 | 9.9268 | 9.9142 | 9.9306 | 7.204 | 10 | 28.08% | 9.9559 | 9.9 | 9.9 | 0 | E190-E140 | 10 | 10 | 7.477 | 17.585 | 8.3865 | 9.914 | 9.4592 | 7.477 | 17.585 | 102.7% | 9.8452 | 9.8 | 10.6 | 0
[45 empty] | E195-E190 | 5 | 5 | 3.577 | 4 | 4.5989 | 4.6017 | 4.6449 | 3.577 | 5 | 30.6% | 4.6509 | 4.6 | 4.6 | 0 | E195-E190 | 24 | 24 | 22.633 | 22.8605 | 22.8205 | 23.7619 | 23.71 | 22.633 | 24 | 5.736% | 23.8326 | 23.9 | 23.7 | 0
[45 empty] | E195-E185 | -116 | -116 | -117.328 | -119 | -116.5278 | -116.6191 | -116.0326 | -119 | -116 | 2.574% | -116.5672 | -116.8 | -116.7 | 0 | E195-E185 | -1316 | -1346 | -1382.454 | -1417.6436 | -1337.68 | -1346.3775 | -1345.3897 | -1417.6436 | -1316 | 7.552% | -1345.9558 | -1346.5 | -1346.1 | 0
[45 empty] | E195-E130 | 13 | 13 | 9.412 | 10 | 12.3997 | 12.3655 | 12.3994 | 9.412 | 13 | 28.9% | 12.4132 | 12.3 | 12.3 | 0 | E195-E130 | 13 | 13 | 9.862 | 19.9297 | 11.0631 | 12.3655 | 11.964 | 9.862 | 19.9297 | 81.91% | 12.2909 | 12.3 | 12.4 | 0
[45 empty] | E200-E100 | 10 | 9 | 3.966 | 10 | 9.9058 | 10.9119 | 12.1975 | 3.966 | 12.1975 | 79.09% | 10.4073 | 10.5 | 10.6 | 0 | E200-E100 | 476 | 415 | 471.706 | 508.7925 | 466.2125 | 476.8042 | 478.5917 | 415 | 508.7925 | 19.69% | 476.3346 | 476.4 | 476.4 | 0
[45 empty] | Del Q ODfan (kWh,e) | [7 empty] | Statistics, All Results | [6 empty] | Del Qcoil,lat (kWh,t) | [7 empty] | Statistics, All Results
[46 empty] | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your |  | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  |  | Abs(Max- | Analytical |  |  | your
[46 empty] | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program |  | EDF | EDF | CIEMAT | NREL | GARD | TUD | TUD | Min | Max | Min)/Analy. | TUD | HTAL1 | HTAL2 | program
[45 empty] | E110-E100 | -8 | -7 | -5.761 | -7 |  | -7.4954 | -7.374 | -8 | -5.761 | 29.95% | -7.4767 | -7.5 | -7.5 | 0 | E110-E100 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0447e-14 | -3.0447e-14 | 0 |  | 0 | 0 | 0 | 0
[45 empty] | E120-E110 | -5 | -6 | -10.958 | -5 |  | -5.172 | -5.24 | -10.958 | -5 | 113.1% | -5.2677 | -5.2 | -5.2 | 0 | E120-E110 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1191e-15 | 0 | 1.1191e-15 |  | 0 | 0 | 0 | 0
[45 empty] | E120-E100 | -13 | -13 | -16.719 | -12 |  | -12.6674 | -12.6139 | -16.719 | -12 | 37.03% | -12.7444 | -12.7 | -12.7 | 0 | E120-E100 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9328e-14 | -2.9328e-14 | 0 |  | 0 | 0 | 0 | 0
[45 empty] | E130-E100 | -63 | -63 | -64.269 | -62 |  | -62.6344 | -61.9703 | -64.269 | -61.9703 | 3.663% | -62.7555 | -62.8 | -62.8 | 0 | E130-E100 | 0 | 0 | 0 | 0 | 0 | 0 | -1.7231e-15 | -1.7231e-15 | 0 |  | 0 | 0 | 0 | 0
[45 empty] | E140-E130 | -1 | -1 | -0.643 | -1 |  | -1.0097 | -1.0218 | -1.0218 | -0.643 | 36.78% | -1.03 | -1 | -1 | 0 | E140-E130 | 0 | 0 | 0 | 0 | 0 | 0 | -3.169e-14 | -3.169e-14 | 0 |  | 0 | 0 | 0 | 0
[45 empty] | E140-E110 | -56 | -57 | -59.151 | -56 |  | -56.1487 | -55.6182 | -59.151 | -55.6182 | 6.274% | -56.3088 | -56.3 | -56.3 | 0 | E140-E110 | 0 | 0 | 0 | 0 | 0 | 0 | -2.9665e-15 | -2.9665e-15 | 0 |  | 0 | 0 | 0 | 0
[45 empty] | E150-E110 | 6 | 5 | 0 | 5 |  | 6.1925 | 5.9844 | 0 | 6.1925 | 100.8% | 6.1462 | 6.2 | 6.1 | 0 | E150-E110 | 739 | 739 | 739.2 | 741.5006 | 739.1972 | 739.2 | 739.2069 | 739 | 741.5006 | 0.3383% | 739.1956 | 739.2 | 739.4 | 0
[45 empty] | E160-E150 | -5 | -5 | -6.51 | -5 |  | -5.5228 | -5.2203 | -6.51 | -5 | 27% | -5.5928 | -5.6 | -5.5 | 0 | E160-E150 | 1 | 0 | 0 | -2.0516 | -2.4939e-05 | 0 | -0.01221 | -2.0516 | 1 |  | 0.043984 | 0 | -0.3 | 0
[45 empty] | E165-E160 | 9 | 9 | 10.624 | 9 |  | 9.5064 | 9.2456 | 9 | 10.624 | 17.48% | 9.2921 | 9.4 | 9.4 | 0 | E165-E160 | 0 | 0 | 0 | 0.87925 | 0.00055101 | 0 | -0.00548 | -0.00548 | 0.87925 |  | 0.005862 | 0 | 0.2 | 0
[45 empty] | E170-E150 | -32 | -32 | -33.618 | -31 |  | -31.7964 | -31.1915 | -33.618 | -31 | 8.244% | -31.756 | -31.9 | -31.8 | 0 | E170-E150 | 1 | 0 | 0 | -2.6377 | 0.0035566 | 0 | 0.00465 | -2.6377 | 1 |  | 0.12011 | 0 | 0 | 0
[45 empty] | E180-E150 | -10 | -10 | -10.379 | -9 |  | -10.5117 | -9.99 | -10.5117 | -9 | 14.34% | -10.5405 | -10.6 | -10.5 | 0 | E180-E150 | 2219 | 2218 | 2217.6 | 2186.4009 | 2217.5955 | 2217.6 | 2217.5924 | 2186.4009 | 2219 | 1.47% | 2218.2757 | 2217.6 | 2216.7 | 0
[45 empty] | E180-E170 | 22 | 22 | 23.239 | 22 |  | 21.2847 | 21.2015 | 21.2015 | 23.239 | 9.604% | 21.2154 | 21.3 | 21.3 | 0 | E180-E170 | 2218 | 2218 | 2217.6 | 2189.0387 | 2217.592 | 2217.6 | 2217.5877 | 2189.0387 | 2218 | 1.306% | 2218.1556 | 2217.6 | 2216.7 | 0
[45 empty] | E185-E180 | 9 | 9 | 11.384 | 10 |  | 9.7468 | 9.7164 | 9 | 11.384 | 24.63% | 9.6803 | 9.7 | 9.7 | 0 | E185-E180 | 1 | 0 | 0 | 2.0516 | 0.0065461 | 0 | 0.02022 | 0 | 2.0516 |  | 0.051109 | 0 | 0.1 | 0
[45 empty] | E190-E180 | -48 | -47 | -45.389 | -48 |  | -47.1741 | -46.9496 | -48 | -45.389 | 5.527% | -47.2395 | -47.2 | -47.2 | 0 | E190-E180 | -2588 | -2587 | -2587.2 | -2561.5475 | -2587.1889 | -2587.2 | -2587.1524 | -2588 | -2561.5475 | 1.022% | -2587.7557 | -2587.2 | -2586.3 | 0
[45 empty] | E190-E140 | 4 | 5 | 3.383 | 4 |  | 4.6553 | 4.6631 | 3.383 | 5 | 34.59% | 4.6749 | 4.7 | 4.7 | 0 | E190-E140 | 370 | 370 | 369.6 | 366.354 | 369.6039 | 369.6 | 369.6468 | 366.354 | 370 | 0.9862% | 369.7156 | 369.6 | 369.8 | 0
[45 empty] | E195-E190 | 3 | 2 | 1.679 | 3 |  | 2.1608 | 2.1811 | 1.679 | 3 | 60.49% | 2.1839 | 2.1 | 2.1 | 0 | E195-E190 | 0 | 0 | 0 | 0.29308 | 0.018237 | 0 | -0.041346 | -0.041346 | 0.29308 |  | 0.013833 | 0 | -0.2 | 0
[45 empty] | E195-E185 | -54 | -54 | -55.094 | -55 |  | -54.7601 | -54.4849 | -55.094 | -54 | 1.999% | -54.7359 | -54.8 | -54.8 | 0 | E195-E185 | -2589 | -2587 | -2587.2 | -2563.306 | -2587.1772 | -2587.2 | -2587.214 | -2589 | -2563.306 | 0.9929% | -2587.793 | -2587.2 | -2586.6 | 0
[45 empty] | E195-E130 | 6 | 6 | 4.419 | 6 |  | 5.8064 | 5.8223 | 4.419 | 6 | 27.12% | 5.8288 | 5.8 | 5.8 | 0 | E195-E130 | 370 | 370 | 369.6 | 366.6471 | 369.6221 | 369.6 | 369.6055 | 366.6471 | 370 | 0.9068% | 369.7294 | 369.6 | 369.6 | 0
[45 empty] | E200-E100 | 5 | 4 | 1.862 | 4 |  | 5.124 | 5.7274 | 1.862 | 5.7274 | 79.1% | 4.8869 | 5 | 5 | 0 | E200-E100 | 1222 | 1221 | 1221 | 1219.2263 | 1220.9837 | 1221.024 | 1221.024 | 1219.2263 | 1222 | 0.2271% | 1221.1063 | 1221 | 1221 | 0
[47 empty] | results5-3.xls q:ck491..cz580; 10/15/02 | [12 empty] | results5-3.xls q:db491..dq580; 10/15/02

## R
HTAL1 = analytical solution, adiabatic env
HTAL2 = numerical model, near-adiab except E200
Space Cooling Electricity Consumption
[27 empty] | Total (kWh,e) |  |  |  | Compressor (kWh,e) |  |  |  | Supply Fan (kWh,e) |  |  |  | Condenser Fan (kWh,e)
[30 empty] | (Max-Min) |  |  |  | (Max-Min) |  |  |  | (Max-Min) |  |  |  | (Max-Min)
[27 empty] | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
[26 empty] | E100 | 1530.548 | 1530.8 | 1530.6 | 0.01646% | 1318.8515 | 1319 | 1318.9 | 0.01126% | 144.0538 | 144.1 | 144 | 0.06942% | 67.6427 | 67.6 | 67.6 | 0.06311%
[26 empty] | E110 | 1076.2349 | 1077.2 | 1077.4 | 0.1082% | 887.9378 | 889.2 | 889.4 | 0.1645% | 128.1312 | 127.9 | 127.9 | 0.1807% | 60.166 | 60.1 | 60.1 | 0.1097%
[26 empty] | E120 | 1012.6774 | 1011 | 1011 | 0.1658% | 840.8662 | 839.1 | 839.2 | 0.2103% | 116.9129 | 116.9 | 116.9 | 0.01107% | 54.8982 | 54.9 | 54.9 | 0.003191%
[26 empty] | E130 | 110.5818 | 109.5 | 109.5 | 0.9847% | 95.2867 | 94.4 | 94.3 | 1.042% | 10.4079 | 10.3 | 10.3 | 1.044% | 4.8872 | 4.8 | 4.8 | 1.805%
[26 empty] | E140 | 68.9953 | 68.5 | 68.3 | 1.014% | 56.924 | 56.5 | 56.4 | 0.9256% | 8.2142 | 8.1 | 8.1 | 1.404% | 3.8571 | 3.8 | 3.8 | 1.496%
[26 empty] | E150 | 1206.49 | 1206.5 | 1206.5 | 0.0008284% | 998.9576 | 999.2 | 999.2 | 0.02426% | 141.2203 | 141.1 | 141.1 | 0.0852% | 66.3121 | 66.3 | 66.2 | 0.1692%
[26 empty] | E160 | 1140.44 | 1139.3 | 1138.9 | 0.1351% | 950.4111 | 949.4 | 949.1 | 0.1381% | 129.3096 | 129.2 | 129.2 | 0.08482% | 60.7193 | 60.7 | 60.7 | 0.03179%
[26 empty] | E165 | 1497.8302 | 1499.7 | 1499.6 | 0.1247% | 1278.7205 | 1280.2 | 1280.2 | 0.1156% | 149.0983 | 149.3 | 149.3 | 0.1351% | 70.0114 | 70.1 | 70.1 | 0.1265%
[26 empty] | E170 | 641.1173 | 637.7 | 637.8 | 0.5349% | 532.9693 | 530 | 530.1 | 0.5592% | 73.5918 | 73.2 | 73.2 | 0.5343% | 34.5562 | 34.4 | 34.4 | 0.4533%
[26 empty] | E180 | 1082.666 | 1082.3 | 1081.9 | 0.07078% | 908.1216 | 908 | 907.7 | 0.04644% | 118.7728 | 118.6 | 118.5 | 0.23% | 55.7716 | 55.7 | 55.7 | 0.1285%
[26 empty] | E185 | 1544.6397 | 1543.4 | 1542.9 | 0.1127% | 1339.7996 | 1338.6 | 1338.2 | 0.1195% | 139.3882 | 139.4 | 139.3 | 0.07176% | 65.4519 | 65.4 | 65.4 | 0.07929%
[26 empty] | E190 | 165.173 | 164.1 | 164.2 | 0.6523% | 138.4708 | 137.6 | 137.7 | 0.6314% | 18.1701 | 18 | 18 | 0.9422% | 8.5321 | 8.5 | 8.5 | 0.3767%
[26 empty] | E195 | 252.1605 | 250 | 250 | 0.8617% | 218.6235 | 216.8 | 216.8 | 0.8388% | 22.821 | 22.6 | 22.6 | 0.9748% | 10.716 | 10.6 | 10.6 | 1.09%
[26 empty] | E200 | 1475.8104 | 1477.4 | 1477.1 | 0.1076% | 1248.8198 | 1250.2 | 1250 | 0.1104% | 154.4611 | 154.6 | 154.6 | 0.08987% | 72.5296 | 72.6 | 72.6 | 0.09705%
results.xls r:am06..be81; 05/18/01
Coil Loads: Total, Sensible, and Latent
[27 empty] | Total (kWh,thermal) |  |  |  | Sensible (kWh,thermal) |  |  |  | Latent (kWh,thermal)
[30 empty] | (Max-Min) |  |  |  | (Max-Min) |  |  |  | (Max-Min)
[27 empty] | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
[26 empty] | E100 | 3800.3599 | 3800.4 | 3800.4 | 0.001056% | 3800.3599 | 3800.4 | 3800.4 | 0.001056% | 0 | 0 | 0
[26 empty] | E110 | 3765.2438 | 3765 | 3765.3 | 0.007968% | 3765.2438 | 3765 | 3765.3 | 0.007968% | 0 | 0 | 0
[26 empty] | E120 | 3748.902 | 3748.8 | 3748.5 | 0.01072% | 3748.902 | 3748.8 | 3748.5 | 0.01072% | 0 | 0 | 0
[26 empty] | E130 | 219.3541 | 219.3 | 219.2 | 0.07027% | 219.3541 | 219.3 | 219.2 | 0.07027% | 0 | 0 | 0
[26 empty] | E140 | 197.9671 | 197.9 | 197.3 | 0.3374% | 197.9671 | 197.9 | 197.3 | 0.3374% | 0 | 0 | 0
[26 empty] | E150 | 4517.5274 | 4517.4 | 4518.3 | 0.01992% | 3778.3318 | 3778.2 | 3779 | 0.02117% | 739.1956 | 739.2 | 739.4 | 0.02765%
[26 empty] | E160 | 4500.5449 | 4500.3 | 4499.9 | 0.01433% | 3761.3053 | 3761.1 | 3760.8 | 0.01344% | 739.2396 | 739.2 | 739.1 | 0.01888%
[26 empty] | E165 | 4536.998 | 4537.3 | 4537.9 | 0.01988% | 3797.7525 | 3798.1 | 3798.6 | 0.02231% | 739.2454 | 739.2 | 739.3 | 0.01353%
[26 empty] | E170 | 2232.3427 | 2231.9 | 2232.5 | 0.02688% | 1493.027 | 1492.7 | 1493.1 | 0.02679% | 739.3157 | 739.2 | 739.4 | 0.02705%
[26 empty] | E180 | 4495.2651 | 4494.9 | 4493.8 | 0.0326% | 1537.7939 | 1538.1 | 1537.7 | 0.02601% | 2957.4713 | 2956.8 | 2956.1 | 0.04638%
[26 empty] | E185 | 4535.1231 | 4534.9 | 4533.9 | 0.02697% | 1577.6007 | 1578.1 | 1577.7 | 0.03164% | 2957.5224 | 2956.8 | 2956.2 | 0.04472%
[26 empty] | E190 | 577.5279 | 577.3 | 577.7 | 0.06926% | 207.8123 | 207.7 | 207.9 | 0.09624% | 369.7156 | 369.6 | 369.8 | 0.0541%
[26 empty] | E195 | 601.3744 | 601.2 | 601.2 | 0.029% | 231.645 | 231.6 | 231.6 | 0.01941% | 369.7294 | 369.6 | 369.6 | 0.03501%
[26 empty] | E200 | 5497.8008 | 5497.8 | 5497.8 | 1.411e-05% | 4276.6945 | 4276.8 | 4276.8 | 0.002466% | 1221.1063 | 1221 | 1221 | 0.008703%
Zone Loads: Total, Sensible, and Latent
[27 empty] | Total (kWh,thermal) |  |  |  | Sensible (kWh,thermal) |  |  |  | Latent (kWh,thermal)
[30 empty] | (Max-Min) |  |  |  | (Max-Min) |  |  |  | (Max-Min)
[27 empty] | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
[26 empty] | E100 | 3656.3062 | 3656.3 | 3656.3 | 0.0001705% | 3656.3062 | 3656.3 | 3656.3 | 0.0001705% | 0 | 0 | 0
[26 empty] | E110 | 3637.1129 | 3637.1 | 3637.1 | 0.0003545% | 3637.1129 | 3637.1 | 3637.1 | 0.0003545% | 0 | 0 | 0
[26 empty] | E120 | 3631.9893 | 3631.9 | 3631.9 | 0.002459% | 3631.9893 | 3631.9 | 3631.9 | 0.002459% | 0 | 0 | 0
[26 empty] | E130 | 208.9462 | 209 | 209 | 0.02573% | 208.9462 | 209 | 209 | 0.02573% | 0 | 0 | 0
[26 empty] | E140 | 189.7529 | 189.7 | 189.7 | 0.02788% | 189.7529 | 189.7 | 189.7 | 0.02788% | 0 | 0 | 0
[26 empty] | E150 | 4376.3129 | 4376.3 | 4376.3 | 0.0002946% | 3637.1129 | 3637.1 | 3637.1 | 0.0003545% | 739.2 | 739.2 | 739.2 | 0%
[26 empty] | E160 | 4371.1893 | 4371.1 | 4371.1 | 0.002043% | 3631.9893 | 3631.9 | 3631.9 | 0.002459% | 739.2 | 739.2 | 739.2 | 0%
[26 empty] | E165 | 4387.8381 | 4387.9 | 4387.9 | 0.001411% | 3648.6381 | 3648.7 | 3648.7 | 0.001696% | 739.2 | 739.2 | 739.2 | 0%
[26 empty] | E170 | 2158.7129 | 2158.7 | 2158.7 | 0.0005972% | 1419.5129 | 1419.5 | 1419.5 | 0.0009083% | 739.2 | 739.2 | 739.2 | 0%
[26 empty] | E180 | 4376.3129 | 4376.3 | 4376.3 | 0.0002946% | 1419.5129 | 1419.5 | 1419.5 | 0.0009083% | 2956.8 | 2956.8 | 2956.8 | 0%
[26 empty] | E185 | 4395.5062 | 4395.5 | 4395.5 | 0.0001418% | 1438.7062 | 1438.7 | 1438.7 | 0.0004333% | 2956.8 | 2956.8 | 2956.8 | 0%
[26 empty] | E190 | 559.3529 | 559.3 | 559.3 | 0.009457% | 189.7529 | 189.7 | 189.7 | 0.02788% | 369.6 | 369.6 | 369.6 | 0%
[26 empty] | E195 | 578.5462 | 578.6 | 578.6 | 0.009293% | 208.9462 | 209 | 209 | 0.02573% | 369.6 | 369.6 | 369.6 | 0%
[26 empty] | E200 | 5343.2549 | 5343.2 | 5343.2 | 0.001028% | 4122.2309 | 4122.2 | 4122.2 | 0.0007499% | 1221.024 | 1221 | 1221 | 0.001966%
Fan Heat and Latent Loads Check
[27 empty] | Sensible Coil - Zone Load |  |  |  | Latent Coil-Zone Load (kWh,th)
[27 empty] | (Fan Heat) (kWh,th) |  |  | (Max-Min) | (Should = 0) |  |  | (Max-Min)
[27 empty] | TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
[26 empty] | E100 | 144.0536 | 144.1 | 144.1 | 0.03218% | 0 | 0 | 0
[26 empty] | E110 | 128.1309 | 127.9 | 128.2 | 0.2342% | 0 | 0 | 0
[26 empty] | E120 | 116.9127 | 116.9 | 116.6 | 0.2677% | 0 | 0 | 0
[26 empty] | E130 | 10.4079 | 10.3 | 10.2 | 2.018% | 0 | 0 | 0
[26 empty] | E140 | 8.2142 | 8.2 | 7.6 | 7.673% | 0 | 0 | 0
[26 empty] | E150 | 141.2189 | 141.1 | 141.9 | 0.5657% | -0.0044111 | 0 | 0.2
[26 empty] | E160 | 129.316 | 129.2 | 128.9 | 0.3222% | 0.039573 | 0 | -0.1
[26 empty] | E165 | 149.1144 | 149.4 | 149.9 | 0.5256% | 0.045435 | 0 | 0.1
[26 empty] | E170 | 73.5141 | 73.2 | 73.6 | 0.5447% | 0.1157 | 0 | 0.2
[26 empty] | E180 | 118.281 | 118.6 | 118.2 | 0.338% | 0.67126 | 0 | -0.7
[26 empty] | E185 | 138.8945 | 139.4 | 139 | 0.3634% | 0.72237 | 0 | -0.6
[26 empty] | E190 | 18.0594 | 18 | 18.2 | 1.106% | 0.11557 | 0 | 0.2
[26 empty] | E195 | 22.6987 | 22.6 | 22.6 | 0.4362% | 0.1294 | 0 | 0
[26 empty] | E200 | 154.4636 | 154.6 | 154.6 | 0.08825% | 0.082262 | 0 | 0
COP: Mean, and (Max-Mean)/Mean
| Mean COP |  |  |  | (Max - Min)/Mean COP
|  |  |  | (Max-Min) |  |  |  | (Max-Min)
| TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
E100 | 2.3889 | 2.39 | 2.39 | 0.04658% | 0 | 0 | 0.00012552
E110 | 3.3795 | 3.38 | 3.38 | 0.01543% | 0 | 0 | 0.00038462
E120 | 3.5865 | 3.59 | 3.59 | 0.09693% | 0 | 0 | 0.00030641
E130 | 1.8895 | 1.91 | 1.91 | 1.076% | 0 | 0 | -5.2356e-05
E140 | 2.7502 | 2.77 | 2.77 | 0.7155% | 0 | 0 | 3.6101e-05
E150 | 3.6273 | 3.63 | 3.63 | 0.07426% | 0 | 0 | 0.00096419
E160 | 3.8329 | 3.84 | 3.84 | 0.184% | 0 | 0 | 0.00026042
E165 | 2.9295 | 2.93 | 2.93 | 0.01693% | 0 | 0 | 0.00030717
E170 | 3.3672 | 3.39 | 3.39 | 0.675% | 0 | 0 | 0.00026549
E180 | 4.0423 | 4.04 | 4.04 | 0.05764% | 0 | 0 | 4.9505e-05
E185 | 2.8458 | 2.85 | 2.85 | 0.1475% | 0 | 0 | 0.00017544
E190 | 3.3865 | 3.41 | 3.41 | 0.6908% | 0 | 0 | -8.7977e-05
E195 | 2.2944 | 2.31 | 2.31 | 0.6775% | 0 | 0 | 0.00012987
E200 | 3.6206 | 3.62 | 3.62 | 0.01696% | 0 | 0 | 8.2873e-05
results.xls r:a85..k141; 05/18/01
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
| Mean IDB (°C) |  |  |  | (Max - Min)/Mean IDB (°C)
|  |  |  | (Max-Min) |  |  |  | (Max-Min)
| TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
E100 | 22.2 | 22.2 | 22.216 | 0.07205% | 0 | 0 | 0.0017105
E110 | 22.2 | 22.2 | 22.214 | 0.06305% | 0 | 0 | 0.0018907
E120 | 26.7 | 26.7 | 26.712 | 0.04494% | 0 | 0 | 0.0017221
E130 | 22.2 | 22.2 | 22.187 | 0.05857% | 0 | 0 | 0.0013521
E140 | 22.2 | 22.2 | 22.185 | 0.06758% | 0 | 0 | 0.0015326
E150 | 22.2 | 22.2 | 22.216 | 0.07205% | 0 | 0 | 0.0017105
E160 | 26.7 | 26.7 | 26.714 | 0.05243% | 0 | 0 | 0.0015722
E165 | 23.3 | 23.3 | 23.317 | 0.07294% | 0 | 0 | 0.0015439
E170 | 22.2 | 22.2 | 22.199 | 0.004505% | 0 | 0 | 0.0013064
E180 | 22.2 | 22.2 | 22.205 | 0.02252% | 0 | 0 | 0.00081063
E185 | 22.2 | 22.2 | 22.206 | 0.02702% | 0 | 0 | 0.00072053
E190 | 22.2 | 22.2 | 22.194 | 0.02703% | 0 | 0 | 0.00072092
E195 | 22.2 | 22.2 | 22.195 | 0.02252% | 0 | 0 | 0.00063077
E200 | 26.7 | 26.7 | 26.713 | 0.04868% | 0 | 0 | 0
Humidity Ratio: Mean and (Max-Min)/Mean
| Mean Humidity Ratio |  |  |  | (Max - Min)/Mean Hum. Ratio
|  |  |  | (Max-Min) |  |  |  | (Max-Min)
| TUD | HTAL1 | HTAL2 | /Mean | TUD | HTAL1 | HTAL2 | /Mean
E100 | 0.0074274 | 0.00734 | 0.007339 | 1.2% | 0 | 0 | 0
E110 | 0.0065187 | 0.0064 | 0.006411 | 1.842% | 0 | 0 | 0
E120 | 0.0078783 | 0.00786 | 0.007873 | 0.2323% | 0 | 0 | 0
E130 | 0.0074274 | 0.00734 | 0.007339 | 1.2% | 0 | 0 | 0
E140 | 0.0065187 | 0.0064 | 0.006402 | 1.843% | 0 | 0 | 0
E150 | 0.0082272 | 0.0082 | 0.00821 | 0.3316% | 0 | 0 | 0.00036541
E160 | 0.009969 | 0.00994 | 0.009946 | 0.2912% | 0 | 0 | 0.00040217
E165 | 0.0092694 | 0.0092 | 0.009208 | 0.7523% | 0 | 0 | 0.0003258
E170 | 0.010367 | 0.01045 | 0.010451 | 0.8073% | 0 | 0 | 0.00057411
E180 | 0.01619 | 0.01623 | 0.01623 | 0.2463% | 0 | 0 | 0.00092421
E185 | 0.016056 | 0.01605 | 0.016059 | 0.05606% | 0 | 0 | 0.00080951
E190 | 0.015796 | 0.0159 | 0.015891 | 0.6526% | 0 | 0 | 0.00075514
E195 | 0.015368 | 0.01544 | 0.015439 | 0.4688% | 0 | 0 | 0.00064771
E200 | 0.011129 | 0.01109 | 0.011099 | 0.3523% | 0 | 0 | 0
Sensitivities for Space Cooling Electricity Consumption, COP and Coil Loads
[10 empty] | Del Qtot (kWh,e) |  |  |  | Del Qcomp (kWh,e) |  |  |  | Del Q IDfan (kWh,e) |  |  |  | Del Q ODfan (kWh,e)
[13 empty] | Abs(Max- |  |  |  | Abs(Max- |  |  |  | Abs(Max- |  |  |  | Abs(Max-
[10 empty] | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean
[9 empty] | E110-E100 | -454.3131 | -453.6 | -453.2 | 0.2453% | -430.9138 | -429.8 | -429.5 | 0.3287% | -15.9226 | -16.2 | -16.1 | 1.725% | -7.4767 | -7.5 | -7.5 | 0.3107%
[9 empty] | E120-E110 | -63.5575 | -66.2 | -66.4 | 4.347% | -47.0715 | -50.1 | -50.2 | 6.369% | -11.2183 | -11 | -11 | 1.971% | -5.2677 | -5.2 | -5.2 | 1.296%
[9 empty] | E120-E100 | -517.8706 | -519.8 | -519.6 | 0.3717% | -477.9853 | -479.9 | -479.7 | 0.3996% | -27.1409 | -27.2 | -27.1 | 0.3684% | -12.7444 | -12.7 | -12.7 | 0.3494%
[9 empty] | E130-E100 | -1419.9663 | -1421.3 | -1421.1 | 0.09387% | -1223.5648 | -1224.6 | -1224.6 | 0.08456% | -133.646 | -133.8 | -133.7 | 0.1152% | -62.7555 | -62.8 | -62.8 | 0.07087%
[9 empty] | E140-E130 | -41.5864 | -41 | -41.2 | 1.421% | -38.3628 | -37.9 | -37.9 | 1.216% | -2.1936 | -2.2 | -2.2 | 0.2904% | -1.03 | -1 | -1 | 2.975%
[9 empty] | E140-E110 | -1007.2396 | -1008.7 | -1009.1 | 0.1845% | -831.0138 | -832.7 | -833 | 0.2387% | -119.917 | -119.8 | -119.8 | 0.09759% | -56.3088 | -56.3 | -56.3 | 0.01568%
[9 empty] | E150-E110 | 130.2551 | 129.3 | 129.1 | 0.8916% | 111.0199 | 110 | 109.8 | 1.106% | 13.0891 | 13.2 | 13.2 | 0.8428% | 6.1462 | 6.2 | 6.1 | 1.626%
[9 empty] | E160-E150 | -66.05 | -67.2 | -67.6 | 2.315% | -48.5466 | -49.8 | -50.1 | 3.139% | -11.9106 | -11.9 | -11.9 | 0.08943% | -5.5928 | -5.6 | -5.5 | 1.797%
[9 empty] | E165-E160 | 357.3902 | 360.4 | 360.7 | 0.9207% | 328.3094 | 330.8 | 331.1 | 0.8455% | 19.7887 | 20.1 | 20.1 | 1.557% | 9.2921 | 9.4 | 9.4 | 1.152%
[9 empty] | E170-E150 | -565.3727 | -568.8 | -568.7 | 0.6038% | -465.9883 | -469.2 | -469.1 | 0.6861% | -67.6284 | -67.9 | -67.9 | 0.4005% | -31.756 | -31.9 | -31.8 | 0.4527%
[9 empty] | E180-E150 | -123.824 | -124.2 | -124.6 | 0.6248% | -90.836 | -91.2 | -91.5 | 0.7282% | -22.4474 | -22.5 | -22.6 | 0.6776% | -10.5405 | -10.6 | -10.5 | 0.9482%
[9 empty] | E180-E170 | 441.5487 | 444.6 | 444.1 | 0.6881% | 375.1523 | 378 | 377.6 | 0.7555% | 45.181 | 45.4 | 45.3 | 0.4835% | 21.2154 | 21.3 | 21.3 | 0.3976%
[9 empty] | E185-E180 | 461.9737 | 461.1 | 461 | 0.211% | 431.6779 | 430.6 | 430.5 | 0.2734% | 20.6154 | 20.8 | 20.8 | 0.89% | 9.6803 | 9.7 | 9.7 | 0.2034%
[9 empty] | E190-E180 | -917.493 | -918.2 | -917.7 | 0.07703% | -769.6508 | -770.4 | -770 | 0.09729% | -100.6027 | -100.6 | -100.5 | 0.1021% | -47.2395 | -47.2 | -47.2 | 0.08371%
[9 empty] | E190-E140 | 96.1777 | 95.6 | 95.9 | 0.6024% | 81.5469 | 81.1 | 81.3 | 0.5495% | 9.9559 | 9.9 | 9.9 | 0.5635% | 4.6749 | 4.7 | 4.7 | 0.5341%
[9 empty] | E195-E190 | 86.9875 | 85.9 | 85.8 | 1.377% | 80.1527 | 79.2 | 79.1 | 1.324% | 4.6509 | 4.6 | 4.6 | 1.102% | 2.1839 | 2.1 | 2.1 | 3.942%
[9 empty] | E195-E185 | -1292.4792 | -1293.4 | -1292.9 | 0.07122% | -1121.176 | -1121.8 | -1121.4 | 0.05564% | -116.5672 | -116.8 | -116.7 | 0.1995% | -54.7359 | -54.8 | -54.8 | 0.117%
[9 empty] | E195-E130 | 141.5788 | 140.5 | 140.5 | 0.7658% | 123.3368 | 122.4 | 122.5 | 0.7632% | 12.4132 | 12.3 | 12.3 | 0.9172% | 5.8288 | 5.8 | 5.8 | 0.4955%
[9 empty] | E200-E100 | -54.7376 | -53.4 | -53.5 | 2.483% | -70.0317 | -68.8 | -68.9 | 1.779% | 10.4073 | 10.5 | 10.6 | 1.835% | 4.8869 | 5 | 5 | 2.279%
Sensitivities for COP and Coil Loads
[10 empty] | Delta COP (kWh,t) |  |  |  | Del Q coil,t (kWh,t) |  |  |  | Del Q coil,s (kWh,t) |  |  |  | Del Qcoil,lat (kWh,t)
[13 empty] | Abs(Max- |  |  |  | Abs(Max- |  |  |  | Abs(Max- |  |  |  | Abs(Max-
[10 empty] | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean | TUD | HTAL1 | HTAL2 | Min)/Mean
[9 empty] | E110-E100 | 0.99059 | 0.99 | 0.99 | 0.05974% | -35.1161 | -35.4 | -35.1 | 0.8521% | -35.1161 | -35.4 | -35.1 | 0.8521% | 0 | 0 | 0
[9 empty] | E120-E110 | 0.20704 | 0.21 | 0.21 | 1.415% | -16.3418 | -16.2 | -16.8 | 3.648% | -16.3418 | -16.2 | -16.8 | 3.648% | 0 | 0 | 0
[9 empty] | E120-E100 | 1.1976 | 1.2 | 1.2 | 0.1973% | -51.4579 | -51.6 | -51.9 | 0.8559% | -51.4579 | -51.6 | -51.9 | 0.8559% | 0 | 0 | 0
[9 empty] | E130-E100 | -0.49937 | -0.48 | -0.48 | 3.982% | -3581.0058 | -3581.1 | -3581.2 | 0.005423% | -3581.0058 | -3581.1 | -3581.2 | 0.005423% | 0 | 0 | 0
[9 empty] | E140-E130 | 0.86071 | 0.86 | 0.86 | 0.08261% | -21.387 | -21.4 | -21.9 | 2.379% | -21.387 | -21.4 | -21.9 | 2.379% | 0 | 0 | 0
[9 empty] | E140-E110 | -0.62925 | -0.61 | -0.61 | 3.123% | -3567.2767 | -3567.1 | -3568 | 0.02523% | -3567.2767 | -3567.1 | -3568 | 0.02523% | 0 | 0 | 0
[9 empty] | E150-E110 | 0.24783 | 0.25 | 0.25 | 0.8719% | 752.2836 | 752.4 | 753 | 0.0952% | 13.088 | 13.2 | 13.7 | 4.591% | 739.1956 | 739.2 | 739.4 | 0.02765%
[9 empty] | E160-E150 | 0.20563 | 0.21 | 0.21 | 2.094% | -16.9825 | -17.1 | -18.4 | 8.103% | -17.0265 | -17.1 | -18.2 | 6.728% | 0.043984 | 0 | -0.3 | 403.1%
[9 empty] | E165-E160 | -0.90343 | -0.91 | -0.91 | 0.7233% | 36.4531 | 37 | 38 | 4.164% | 36.4472 | 37 | 37.8 | 3.648% | 0.005862 | 0 | 0.2 | 291.5%
[9 empty] | E170-E150 | -0.26014 | -0.24 | -0.24 | 8.161% | -2285.1847 | -2285.5 | -2285.8 | 0.02692% | -2285.3048 | -2285.5 | -2285.9 | 0.02604% | 0.12011 | 0 | 0 | 300%
[9 empty] | E180-E150 | 0.41502 | 0.41 | 0.41 | 1.22% | -22.2623 | -22.5 | -24.5 | 9.692% | -2240.5379 | -2240.1 | -2241.3 | 0.05356% | 2218.2757 | 2217.6 | 2216.7 | 0.07106%
[9 empty] | E180-E170 | 0.67516 | 0.65 | 0.65 | 3.821% | 2262.9224 | 2263 | 2261.3 | 0.07514% | 44.7669 | 45.4 | 44.6 | 1.781% | 2218.1556 | 2217.6 | 2216.7 | 0.06564%
[9 empty] | E185-E180 | -1.1965 | -1.19 | -1.19 | 0.5477% | 39.858 | 40 | 40.1 | 0.6052% | 39.8069 | 40 | 40 | 0.4836% | 0.051109 | 0 | 0.1 | 198.5%
[9 empty] | E190-E180 | -0.65583 | -0.63 | -0.63 | 4.045% | -3917.7372 | -3917.6 | -3916.1 | 0.0418% | -1329.9815 | -1330.4 | -1329.8 | 0.04511% | -2587.7557 | -2587.2 | -2586.3 | 0.05627%
[9 empty] | E190-E140 | 0.63627 | 0.64 | 0.64 | 0.5843% | 379.5607 | 379.4 | 380.4 | 0.2633% | 9.8452 | 9.8 | 10.6 | 7.935% | 369.7156 | 369.6 | 369.8 | 0.0541%
[9 empty] | E195-E190 | -1.0921 | -1.1 | -1.1 | 0.7189% | 23.8465 | 23.9 | 23.5 | 1.684% | 23.8326 | 23.9 | 23.7 | 0.84% | 0.013833 | 0 | -0.2 | 344.6%
[9 empty] | E195-E185 | -0.55141 | -0.54 | -0.54 | 2.099% | -3933.7487 | -3933.7 | -3932.7 | 0.02666% | -1345.9558 | -1346.5 | -1346.1 | 0.04043% | -2587.793 | -2587.2 | -2586.6 | 0.04611%
[9 empty] | E195-E130 | 0.40487 | 0.4 | 0.4 | 1.212% | 382.0203 | 381.9 | 382 | 0.03149% | 12.2909 | 12.3 | 12.4 | 0.8851% | 369.7294 | 369.6 | 369.6 | 0.03501%
[9 empty] | E200-E100 | 1.2317 | 1.23 | 1.23 | 0.1403% | 1697.4409 | 1697.4 | 1697.4 | 0.00241% | 476.3346 | 476.4 | 476.4 | 0.01372% | 1221.1063 | 1221 | 1221 | 0.008703%
i220401a.xls r:s145..ak192; 05/18/01
Sensitivities for COP and Coil Loads
[43 empty] | i220600a.wk3 q:cl491..cz580; 06/05/00 | i220600a.wk3 q:db491..dp580; 06/05/00

## Data-TempHum
Indoor Drybulb Temperature: Mean and (Max-Min)/Mean
Mean IDB (°C)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1999 | 22.2 | 22.6346 | 22.2 | 22.2 | 22.216 | 0
CE110 as100 lo ODB | 22.2 | 22.2 | 22.3 | 22.2778 | 22.1999 | 22.2 | 22.5242 | 22.2 | 22.2 | 22.214 | 0
CE120 as100 hiIDB | 26.7 | 26.7 | 26.8 | 26.7222 | 26.7 | 26.7 | 27.0785 | 26.7 | 26.7 | 26.712 | 0
CE130 as100 lo PLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.6377 | 22.2 | 22.2 | 22.187 | 0
CE140 as130 lo ODB | 22.2 | 22.2 | 22.1 | 22.1111 | 22.2 | 22.2 | 21.5097 | 22.2 | 22.2 | 22.185 | 0
CE150 as110 hiSHR | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1772 | 22.2 | 22.6771 | 22.2 | 22.2 | 22.216 | 0
CE160 as150 hiIDB | 26.7 | 26.7 | 26.8 | 26.7222 | 26.6723 | 26.7 | 26.9948 | 26.7 | 26.7 | 26.714 | 0
CE165 as150 mIDB mODB | 23.3 | 23.3 | 23.4 | 23.4444 | 23.28 | 23.3 | 23.7805 | 23.3 | 23.3 | 23.317 | 0
CE170 as150 mSHR mPLR | 22.2 | 22.2 | 22.2 | 22.2222 | 22.1809 | 22.2 | 22.1169 | 22.2 | 22.2 | 22.199 | 0
CE180 as150 loSHR | 22.2 | 22.2 | 22.3 | 22.2778 | 22.157 | 22.2 | 22.3344 | 22.2 | 22.2 | 22.205 | 0
CE185 loSHR hiODB | 22.2 | 22.2 | 22.3 | 22.3333 | 22.1672 | 22.2 | 22.3682 | 22.2 | 22.2 | 22.206 | 0
CE190 as180 loPLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.1945 | 22.2 | 21.9469 | 22.2 | 22.2 | 22.194 | 0
CE195 as185 loPLR | 22.2 | 22.2 | 22.1 | 22.1111 | 22.1956 | 22.2 | 22.0113 | 22.2 | 22.2 | 22.195 | 0
CE200 ARI PLR=1 hiSHR | 26.7 | 26.7 | 26.8 | 26.7778 | 26.6624 | 26.7339 | 26.7339 | 26.7 | 26.7 | 26.713 | 0
(Max - Min)/Mean IDB (°C)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 7.6728e-07 | 0 | 0.049482 | 0 | 0 | 0.0017105 | #DIV/0!
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 3.9213e-07 | 0 | 0.047948 | 0 | 0 | 0.0018907 | #DIV/0!
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 2.5833e-09 | 0 | 0.077183 | 0 | 0 | 0.0017221 | #DIV/0!
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 2.8008e-09 | 0 | 0.056383 | 0 | 0 | 0.0013521 | #DIV/0!
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 1.0566e-09 | 0 | 0.069271 | 0 | 0 | 0.0015326 | #DIV/0!
CE150 as110 hiSHR | 0 | 0 | 0 | 0 | 9.1726e-05 | 0 | 0.053799 | 0 | 0 | 0.0017105 | #DIV/0!
CE160 as150 hiIDB | 0 | 0 | 0 | 0 | 0.00019269 | 0 | 0.045194 | 0 | 0 | 0.0015722 | #DIV/0!
CE165 as150 mIDB mODB | 0 | 0 | 0 | 0 | 0.00027951 | 0 | 0.051303 | 0 | 0 | 0.0015439 | #DIV/0!
CE170 as150 mSHR mPLR | 0 | 0 | 0 | 0 | 7.1143e-05 | 0 | 0.049736 | 0 | 0 | 0.0013064 | #DIV/0!
CE180 as150 loSHR | 0 | 0 | 0 | 0 | 0.00014949 | 0 | 0.034924 | 0 | 0 | 0.00081063 | #DIV/0!
CE185 loSHR hiODB | 0 | 0 | 0 | 0 | 0.00022693 | 0 | 0.021459 | 0 | 0 | 0.00072053 | #DIV/0!
CE190 as180 loPLR | 0 | 0 | 0 | 0 | 1.2134e-05 | 0 | 0.02825 | 0 | 0 | 0.00072092 | #DIV/0!
CE195 as185 loPLR | 0 | 0 | 0 | 0 | 1.7277e-05 | 0 | 0.022716 | 0 | 0 | 0.00063077 | #DIV/0!
CE200 ARI PLR=1 hiSHR | 0 | 0 | 0 | 0 | 8.3697e-05 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
Humidity Ratio: Mean and (Max-Min)/Mean
Mean Humidity Ratio
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0.0075 | 0.00691 | 0.0076 | 0.0074 | 0.0074522 | 0.0075036 | 0.0075088 | 0.0074274 | 0.00734 | 0.007339 | 0
CE110 as100 lo ODB | 0.0066 | 0.00692 | 0.0070296 | 0.0064 | 0.0065611 | 0.0065938 | 0.0066309 | 0.0065187 | 0.0064 | 0.006411 | 0
CE120 as100 hiIDB | 0.008 | 0.007 | 0.0078 | 0.0078 | 0.008011 | 0.0079506 | 0.0079517 | 0.0078783 | 0.00786 | 0.007873 | 0
CE130 as100 lo PLR | 0.0075 | 0.00691 | 0.0076 | 0.0073 | 0.0074578 | 0.0075036 | 0.0075194 | 0.0074274 | 0.00734 | 0.007339 | 0
CE140 as130 lo ODB | 0.0065 | 0.00692 | 0.0070601 | 0.0064 | 0.0065668 | 0.0065938 | 0.0065941 | 0.0065187 | 0.0064 | 0.006402 | 0
CE150 as110 hiSHR | 0.0083 | 0.00853 | 0.0082 | 0.0083 | 0.0083955 | 0.0083236 | 0.0085152 | 0.0082272 | 0.0082 | 0.00821 | 0
CE160 as150 hiIDB | 0.0102 | 0.0101 | 0.009701 | 0.0099 | 0.01024 | 0.010069 | 0.010236 | 0.009969 | 0.00994 | 0.009946 | 0
CE165 as150 mIDB mODB | 0.0093 | 0.00985 | 0.0090039 | 0.0092 | 0.0093667 | 0.0093021 | 0.0095112 | 0.0092694 | 0.0092 | 0.009208 | 0
CE170 as150 mSHR mPLR | 0.0106 | 0.0107 | 0.010494 | 0.0105 | 0.01055 | 0.010471 | 0.010525 | 0.010367 | 0.01045 | 0.010451 | 0
CE180 as150 loSHR | 0.0164 | 0.0164 | 0.016614 | 0.0164 | 0.016161 | 0.01631 | 0.016404 | 0.01619 | 0.01623 | 0.01623 | 0
CE185 loSHR hiODB | 0.0162 | 0.0171 | 0.016441 | 0.0162 | 0.016049 | 0.016151 | 0.016279 | 0.016056 | 0.01605 | 0.016059 | 0
CE190 as180 loPLR | 0.016 | 0.0161 | 0.016254 | 0.0159 | 0.015867 | 0.015921 | 0.015707 | 0.015796 | 0.0159 | 0.015891 | 0
CE195 as185 loPLR | 0.0156 | 0.0164 | 0.015764 | 0.0155 | 0.015464 | 0.01547 | 0.015326 | 0.015368 | 0.01544 | 0.015439 | 0
CE200 ARI PLR=1 hiSHR | 0.0114 | 0.0115 | 0.010933 | 0.0111 | 0.011419 | 0.011281 | 0.011281 | 0.011129 | 0.01109 | 0.011099 | 0
(Max - Min)/Mean Humidity Ratio
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0.021708 | 0 | 0 | 4.0271e-14 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE110 as100 lo ODB | 0 | 0.021676 | 0.014226 | 0 | 4.4154e-14 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 2.88e-14 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE130 as100 lo PLR | 0 | 0.01013 | 0 | 0 | 1.006e-13 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE140 as130 lo ODB | 0 | 0.011561 | 0.014164 | 0 | 8.374e-14 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
CE150 as110 hiSHR | 0.012048 | 0 | 0 | 0 | 0.010954 | 0 | 0.013153 | 0 | 0 | 0.00036541 | #DIV/0!
CE160 as150 hiIDB | 0.019608 | 0 | 0.010308 | 0.010101 | 0.011333 | 0 | 0.010747 | 0 | 0 | 0.00040217 | #DIV/0!
CE165 as150 mIDB mODB | 0.010753 | 0.0010152 | 0.011106 | 0 | 0.011171 | 0 | 0.012512 | 0 | 0 | 0.0003258 | #DIV/0!
CE170 as150 mSHR mPLR | 0 | 0 | 0.0095289 | 0 | 0.011126 | 0 | 0.023752 | 0 | 0 | 0.00057411 | #DIV/0!
CE180 as150 loSHR | 0.018293 | 0 | 0.012038 | 0.012195 | 0.0097718 | 0 | 0.040234 | 0 | 0 | 0.00092421 | #DIV/0!
CE185 loSHR hiODB | 0.012346 | 0.005848 | 0.018247 | 0.012346 | 0.012009 | 0 | 0.024571 | 0 | 0 | 0.00080951 | #DIV/0!
CE190 as180 loPLR | 0 | 0 | 0.018457 | 0.018868 | 0.024976 | 0 | 0.031196 | 0 | 0 | 0.00075514 | #DIV/0!
CE195 as185 loPLR | 0 | 0.0060976 | 0.01903 | 0.019355 | 0.039296 | 0 | 0.024142 | 0 | 0 | 0.00064771 | #DIV/0!
CE200 ARI PLR=1 hiSHR | 0.017544 | 0 | 0.0091467 | 0.009009 | 0.010952 | 0 | 0 | 0 | 0 | 0 | #DIV/0!

## Data-COP
COP: Mean, and (Max-Min)/Mean
Mean COP
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | 0 | Analytical | 0 | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 2.39 | 2.389 | 2.4304 | 2.4064 | 2.4031 | 2.4017 | 2.4184 | 2.3889 | 2.39 | 2.39 | 0
CE110 as100 lo ODB | 3.38 | 3.342 | 3.4589 | 3.4146 | 3.3994 | 3.4087 | 3.4271 | 3.3795 | 3.38 | 3.38 | 0
CE120 as100 hiIDB | 3.59 | 3.59 | 3.6139 | 3.623 | 3.606 | 3.6054 | 3.6313 | 3.5865 | 3.59 | 3.59 | 0
CE130 as100 lo PLR | 1.91 | 1.909 | 1.9752 | 1.953 | 1.903 | 1.9198 | 1.9163 | 1.8895 | 1.91 | 1.91 | 0
CE140 as130 lo ODB | 2.77 | 2.734 | 2.9151 | 2.854 | 2.7701 | 2.7974 | 2.7996 | 2.7502 | 2.77 | 2.77 | 0
CE150 as110 hiSHR | 3.62 | 3.63 | 3.6675 | 3.7 | 3.6525 | 3.6496 | 3.6734 | 3.6273 | 3.63 | 3.63 | 0
CE160 as150 hiIDB | 3.84 | 3.84 | 3.8658 | 3.95 | 3.8589 | 3.8452 | 3.8599 | 3.8329 | 3.84 | 3.84 | 0
CE165 as150 mIDB mODB | 2.92 | 2.92 | 2.9514 | 2.9853 | 2.9399 | 2.9257 | 2.9449 | 2.9295 | 2.93 | 2.93 | 0
CE170 as150 mSHR mPLR | 3.38 | 3.39 | 3.4423 | 3.477 | 3.3937 | 3.3944 | 3.4033 | 3.3672 | 3.39 | 3.39 | 0
CE180 as150 loSHR | 4.04 | 4.04 | 4.0842 | 4.026 | 4.0416 | 4.0472 | 4.055 | 4.0423 | 4.04 | 4.04 | 0
CE185 loSHR hiODB | 2.85 | 2.85 | 2.8744 | 2.823 | 2.8512 | 2.8512 | 2.8574 | 2.8458 | 2.85 | 2.85 | 0
CE190 as180 loPLR | 3.41 | 3.41 | 3.4865 | 3.457 | 3.395 | 3.4096 | 3.4048 | 3.3865 | 3.41 | 3.41 | 0
CE195 as185 loPLR | 2.31 | 2.31 | 2.3598 | 2.337 | 2.3041 | 2.3158 | 2.3054 | 2.2944 | 2.31 | 2.31 | 0
CE200 ARI PLR=1 hiSHR | 3.62 | 3.61 | 3.6677 | 3.708 | 3.6447 | 3.6102 | 3.6102 | 3.6206 | 3.62 | 3.62 | 0
(Max - Min)/Mean COP
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0.00083717 | 0.0015062 | 0.0012467 | 0.0031826 | 0 | 0 | 0 | 0 | 0.00012552 | #DIV/0!
CE110 as100 lo ODB | 0 | 0.010473 | 0.0017378 | 0.0011714 | 0.0025513 | 0 | 0.010592 | 0 | 0 | 0.00038462 | #DIV/0!
CE120 as100 hiIDB | 0 | 0.0036212 | 0.00079758 | 0.0011041 | 0.0025503 | 0 | 0.012271 | 0 | 0 | 0.00030641 | #DIV/0!
CE130 as100 lo PLR | 0 | 0.03824 | 0.012602 | 0.0087046 | 0.0043691 | 0 | 0.17198 | 0 | 0 | -5.2356e-05 | #DIV/0!
CE140 as130 lo ODB | 0 | 0.055962 | 0.010989 | 0.018921 | 0.003545 | 0 | 0.20433 | 0 | 0 | 3.6101e-05 | #DIV/0!
CE150 as110 hiSHR | 0.0027624 | 0.0027548 | 0.0014674 | 0.0048649 | 0.0052381 | 0 | 0.0092759 | 0 | 0 | 0.00096419 | #DIV/0!
CE160 as150 hiIDB | 0.0026042 | 0.0052083 | 0.0010614 | 0.0032911 | 0.0057024 | 0 | 0.010193 | 0 | 0 | 0.00026042 | #DIV/0!
CE165 as150 mIDB mODB | 0.010274 | 0.0034247 | 0.0012002 | 0.0026798 | 0.006025 | 0 | 0.0084429 | 0 | 0 | 0.00030717 | #DIV/0!
CE170 as150 mSHR mPLR | 0 | 0.0058997 | 0.0021466 | 0.0040265 | 0.0081135 | 0 | 0.043444 | 0 | 0 | 0.00026549 | #DIV/0!
CE180 as150 loSHR | 0.0049505 | 0.0024752 | 0.0023307 | 0.009687 | 0.010241 | 0 | 0.011687 | 0 | 0 | 4.9505e-05 | #DIV/0!
CE185 loSHR hiODB | 0.0070175 | 0.0035088 | 0.0023597 | 0.010273 | 0.011693 | 0 | 0.0091078 | 0 | 0 | 0.00017544 | #DIV/0!
CE190 as180 loPLR | 0 | 0.02346 | 0.0071705 | 0.018802 | 0.040402 | 0 | 0.10066 | 0 | 0 | -8.7977e-05 | #DIV/0!
CE195 as185 loPLR | 0 | 0.017316 | 0.0078108 | 0.016688 | 0.079144 | 0 | 0.08606 | 0 | 0 | 0.00012987 | #DIV/0!
CE200 ARI PLR=1 hiSHR | 0.0055249 | 0 | -1.2839e-05 | 0.0051241 | 0.0060171 | 0 | 0 | 0 | 0 | 8.2873e-05 | #DIV/0!

## Data-Electr
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 1531 | 1530 | 1520.817 | 1519 | 1520.1842 | 1522.2661 | 1511.9369 | 1530.548 | 1530.8 | 1530.6 | 0
CE110 as100 lo ODB | 1077 | 1089 | 1061.196 | 1065 | 1069.3313 | 1066.9607 | 1061.9658 | 1076.2349 | 1077.2 | 1077.4 | 0
CE120 as100 hiIDB | 1012 | 1012 | 1011.104 | 1003 | 1006.6379 | 1007.3023 | 1001.6637 | 1012.6774 | 1011 | 1011 | 0
CE130 as100 lo PLR | 110 | 109 | 105.419 | 106 | 108.1197 | 108.7246 | 110.1161 | 110.5818 | 109.5 | 109.5 | 0
CE140 as130 lo ODB | 68 | 69 | 65.008 | 66 | 67.7696 | 67.7641 | 68.6428 | 68.9953 | 68.5 | 68.3 | 0
CE150 as110 hiSHR | 1208 | 1207 | 1202.424 | 1183 | 1197.6199 | 1199.055 | 1191.613 | 1206.49 | 1206.5 | 1206.5 | 0
CE160 as150 hiIDB | 1140 | 1139 | 1137.63 | 1107 | 1132.2318 | 1136.7334 | 1132.8835 | 1140.44 | 1139.3 | 1138.9 | 0
CE165 as150 mIDB mODB | 1502 | 1501 | 1499.447 | 1470 | 1491.5878 | 1499.7105 | 1489.9268 | 1497.8302 | 1499.7 | 1499.6 | 0
CE170 as150 mSHR mPLR | 638 | 638 | 629.076 | 620 | 635.4994 | 635.909 | 635.8287 | 641.1173 | 637.7 | 637.8 | 0
CE180 as150 loSHR | 1083 | 1082 | 1077.109 | 1080 | 1082.3259 | 1081.2706 | 1080.0377 | 1082.666 | 1082.3 | 1081.9 | 0
CE185 loSHR hiODB | 1544 | 1543 | 1541.155 | 1547 | 1540.5373 | 1541.5256 | 1538.3972 | 1544.6397 | 1543.4 | 1542.9 | 0
CE190 as180 loPLR | 164 | 164 | 160.219 | 160 | 164.1636 | 163.9975 | 165.1202 | 165.173 | 164.1 | 164.2 | 0
CE195 as185 loPLR | 250 | 250 | 244.919 | 246 | 249.7096 | 249.7321 | 251.5799 | 252.1605 | 250 | 250 | 0
CE200 ARI PLR=1 hiSHR | 1477 | 1464 | 1468.214 | 1440 | 1465.3737 | 1479.9926 | 1479.9926 | 1475.8104 | 1477.4 | 1477.1 | 0
Energy Consumption, Compressor (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 1319 | 1318 | 1307.458 | 1311 | 0 | 1311.1661 | 1302.7258 | 1318.8515 | 1319 | 1318.9 | 0
CE110 as100 lo ODB | 889 | 899 | 865.866 | 883 | 0 | 879.3187 | 875.8322 | 887.9378 | 889.2 | 889.4 | 0
CE120 as100 hiIDB | 840 | 840 | 850.068 | 838 | 0 | 835.847 | 831.9292 | 840.8662 | 839.1 | 839.2 | 0
CE130 as100 lo PLR | 95 | 94 | 93.198 | 93 | 0 | 93.6472 | 94.8489 | 95.2867 | 94.4 | 94.3 | 0
CE140 as130 lo ODB | 57 | 57 | 54.799 | 56 | 0 | 55.8468 | 56.5735 | 56.924 | 56.5 | 56.4 | 0
CE150 as110 hiSHR | 1000 | 999 | 1007.094 | 982 | 0 | 992.0333 | 986.7503 | 998.9576 | 999.2 | 999.2 | 0
CE160 as150 hiIDB | 950 | 949 | 962.675 | 926 | 0 | 946.9958 | 944.3585 | 950.4111 | 949.4 | 949.1 | 0
CE165 as150 mIDB mODB | 1283 | 1281 | 1291.242 | 1256 | 0 | 1280.2205 | 1272.4664 | 1278.7205 | 1280.2 | 1280.2 | 0
CE170 as150 mSHR mPLR | 531 | 530 | 538.959 | 523 | 0 | 528.3976 | 528.5837 | 532.9693 | 530 | 530.1 | 0
CE180 as150 loSHR | 909 | 908 | 914.262 | 912 | 0 | 907.1462 | 906.4398 | 908.1216 | 908 | 907.7 | 0
CE185 loSHR hiODB | 1340 | 1339 | 1342.681 | 1344 | 0 | 1336.897 | 1334.3908 | 1339.7996 | 1338.6 | 1338.2 | 0
CE190 as180 loPLR | 138 | 138 | 139.423 | 138 | 0 | 137.5107 | 138.4572 | 138.4708 | 137.6 | 137.7 | 0
CE195 as185 loPLR | 217 | 217 | 218.867 | 217 | 0 | 216.4828 | 218.0909 | 218.6235 | 216.8 | 216.8 | 0
CE200 ARI PLR=1 hiSHR | 1250 | 1239 | 1249.027 | 1218 | 0 | 1252.8566 | 1252.8566 | 1248.8198 | 1250.2 | 1250 | 0
Energy Consumption, Supply Fan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 144 | 144 | 145.185 | 141 | 143.5848 | 143.6481 | 142.3625 | 144.0538 | 144.1 | 144 | 0
CE110 as100 lo ODB | 128 | 129 | 132.917 | 122 | 127.5927 | 127.6854 | 126.659 | 128.1312 | 127.9 | 127.9 | 0
CE120 as100 hiIDB | 117 | 117 | 109.581 | 110 | 116.438 | 116.6706 | 115.4998 | 116.9129 | 116.9 | 116.9 | 0
CE130 as100 lo PLR | 10 | 10 | 8.316 | 8 | 10.2115 | 10.2598 | 10.3889 | 10.4079 | 10.3 | 10.3 | 0
CE140 as130 lo ODB | 8 | 8 | 6.947 | 6 | 8.0856 | 8.1094 | 8.2128 | 8.2142 | 8.1 | 8.1 | 0
CE150 as110 hiSHR | 141 | 141 | 132.917 | 136 | 140.3497 | 140.8727 | 139.4036 | 141.2203 | 141.1 | 141.1 | 0
CE160 as150 hiIDB | 129 | 129 | 119.052 | 121 | 128.3806 | 129.1114 | 128.2863 | 129.3096 | 129.2 | 129.2 | 0
CE165 as150 mIDB mODB | 149 | 150 | 141.678 | 145 | 148.616 | 149.3574 | 147.976 | 149.0983 | 149.3 | 149.3 | 0
CE170 as150 mSHR mPLR | 73 | 73 | 61.322 | 63 | 73.0391 | 73.1586 | 72.9774 | 73.5918 | 73.2 | 73.2 | 0
CE180 as150 loSHR | 118 | 119 | 110.813 | 112 | 118.4636 | 118.487 | 118.1287 | 118.7728 | 118.6 | 118.5 | 0
CE185 loSHR hiODB | 139 | 139 | 135.056 | 137 | 139.139 | 139.2444 | 138.821 | 139.3882 | 139.4 | 139.3 | 0
CE190 as180 loPLR | 18 | 18 | 14.151 | 14 | 18.0123 | 18.0236 | 18.1435 | 18.1701 | 18 | 18 | 0
CE195 as185 loPLR | 23 | 23 | 17.728 | 18 | 22.6112 | 22.6253 | 22.7884 | 22.821 | 22.6 | 22.6 | 0
CE200 ARI PLR=1 hiSHR | 154 | 153 | 149.151 | 151 | 153.4905 | 154.56 | 154.56 | 154.4611 | 154.6 | 154.6 | 0
Energy Consumption, Condenser Fan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 68 | 68 | 68.174 | 67 | 0 | 67.452 | 66.8486 | 67.6427 | 67.6 | 67.6 | 0
CE110 as100 lo ODB | 60 | 61 | 62.413 | 60 | 0 | 59.9566 | 59.4747 | 60.166 | 60.1 | 60.1 | 0
CE120 as100 hiIDB | 55 | 55 | 51.455 | 55 | 0 | 54.7846 | 54.2347 | 54.8982 | 54.9 | 54.9 | 0
CE130 as100 lo PLR | 5 | 5 | 3.905 | 5 | 0 | 4.8176 | 4.8783 | 4.8872 | 4.8 | 4.8 | 0
CE140 as130 lo ODB | 4 | 4 | 3.262 | 4 | 0 | 3.8079 | 3.8565 | 3.8571 | 3.8 | 3.8 | 0
CE150 as110 hiSHR | 66 | 66 | 62.413 | 65 | 0 | 66.1491 | 65.4591 | 66.3121 | 66.3 | 66.2 | 0
CE160 as150 hiIDB | 61 | 61 | 55.903 | 60 | 0 | 60.6262 | 60.2388 | 60.7193 | 60.7 | 60.7 | 0
CE165 as150 mIDB mODB | 70 | 70 | 66.527 | 69 | 0 | 70.1326 | 69.4843 | 70.0114 | 70.1 | 70.1 | 0
CE170 as150 mSHR mPLR | 34 | 34 | 28.795 | 34 | 0 | 34.3527 | 34.2676 | 34.5562 | 34.4 | 34.4 | 0
CE180 as150 loSHR | 56 | 56 | 52.034 | 56 | 0 | 55.6374 | 55.4691 | 55.7716 | 55.7 | 55.7 | 0
CE185 loSHR hiODB | 65 | 65 | 63.418 | 66 | 0 | 65.3842 | 65.1855 | 65.4519 | 65.4 | 65.4 | 0
CE190 as180 loPLR | 8 | 9 | 6.645 | 8 | 0 | 8.4632 | 8.5195 | 8.5321 | 8.5 | 8.5 | 0
CE195 as185 loPLR | 11 | 11 | 8.324 | 11 | 0 | 10.6241 | 10.7006 | 10.716 | 10.6 | 10.6 | 0
CE200 ARI PLR=1 hiSHR | 73 | 72 | 70.036 | 71 | 0 | 72.576 | 72.576 | 72.5296 | 72.6 | 72.6 | 0

## Data-Loads
Zone Loads: Total, Sensible, and Latent
Zone Load, Total (kWh,thermal)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 3656 | 3656 | 3654.42 | 3655.3341 | 3653.1097 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 0
CE110 as100 lo ODB | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.0919 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 0
CE120 as100 hiIDB | 3632 | 3632 | 3630.472 | 3631.5944 | 3629.9408 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 0
CE130 as100 lo PLR | 209 | 209 | 207.344 | 207.5029 | 205.7496 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 0
CE140 as130 lo ODB | 190 | 190 | 188.503 | 188.4525 | 187.7318 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 0
CE150 as110 hiSHR | 4376 | 4376 | 4374.801 | 4376.0258 | 4374.3181 | 4376.1245 | 4375.5775 | 4376.3129 | 4376.3 | 4376.3 | 0
CE160 as150 hiIDB | 4371 | 4371 | 4369.652 | 4371.0434 | 4369.1704 | 4370.9568 | 4370.6181 | 4371.1893 | 4371.1 | 4371.1 | 0
CE165 as150 mIDB mODB | 4388 | 4388 | 4386.071 | 4387.456 | 4385.1599 | 4387.7098 | 4387.1605 | 4387.8381 | 4387.9 | 4387.9 | 0
CE170 as150 mSHR mPLR | 2159 | 2159 | 2157.351 | 2157.9719 | 2156.7137 | 2158.5245 | 2158.621 | 2158.7129 | 2158.7 | 2158.7 | 0
CE180 as150 loSHR | 4376 | 4376 | 4374.852 | 4376.0258 | 4374.3398 | 4376.1245 | 4375.9707 | 4376.3129 | 4376.3 | 4376.3 | 0
CE185 loSHR hiODB | 4396 | 4396 | 4393.649 | 4394.7831 | 4392.349 | 4395.2832 | 4395.0925 | 4395.5062 | 4395.5 | 4395.5 | 0
CE190 as180 loPLR | 557 | 559 | 558.09 | 558.0305 | 557.3382 | 559.1652 | 559.4558 | 559.3529 | 559.3 | 559.3 | 0
CE195 as185 loPLR | 576 | 579 | 576.926 | 577.0809 | 575.3548 | 578.3252 | 578.542 | 578.5462 | 578.6 | 578.6 | 0
CE200 ARI PLR=1 hiSHR | 5343 | 5283 | 5341.526 | 5342.9074 | 5340.9046 | 5343.0048 | 5343.0048 | 5343.2549 | 5343.2 | 5343.2 | 0
Zone Load, Sensible (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 3656 | 3656 | 3654.42 | 3655.3341 | 3653.1097 | 3656.0832 | 3655.5859 | 3656.3062 | 3656.3 | 3656.3 | 0
CE110 as100 lo ODB | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.0919 | 3636.9245 | 3636.5534 | 3637.1129 | 3637.1 | 3637.1 | 0
CE120 as100 hiIDB | 3632 | 3632 | 3630.472 | 3631.5944 | 3629.9408 | 3631.7568 | 3631.3216 | 3631.9893 | 3631.9 | 3631.9 | 0
CE130 as100 lo PLR | 209 | 209 | 207.344 | 207.5029 | 205.7496 | 208.7252 | 209.371 | 208.9462 | 209 | 209 | 0
CE140 as130 lo ODB | 190 | 190 | 188.503 | 188.4525 | 187.7318 | 189.5652 | 190.358 | 189.7529 | 189.7 | 189.7 | 0
CE150 as110 hiSHR | 3637 | 3637 | 3635.601 | 3636.5768 | 3635.1214 | 3636.9245 | 3636.3775 | 3637.1129 | 3637.1 | 3637.1 | 0
CE160 as150 hiIDB | 3632 | 3632 | 3630.452 | 3631.5944 | 3629.9738 | 3631.7568 | 3631.4181 | 3631.9893 | 3631.9 | 3631.9 | 0
CE165 as150 mIDB mODB | 3649 | 3649 | 3646.871 | 3648.007 | 3645.9633 | 3648.5098 | 3647.9605 | 3648.6381 | 3648.7 | 3648.7 | 0
CE170 as150 mSHR mPLR | 1420 | 1420 | 1418.151 | 1418.5229 | 1417.5137 | 1419.3245 | 1419.421 | 1419.5129 | 1419.5 | 1419.5 | 0
CE180 as150 loSHR | 1420 | 1420 | 1418.052 | 1418.5229 | 1417.5533 | 1419.3245 | 1419.1707 | 1419.5129 | 1419.5 | 1419.5 | 0
CE185 loSHR hiODB | 1439 | 1439 | 1436.849 | 1437.2802 | 1435.5625 | 1438.4832 | 1438.2925 | 1438.7062 | 1438.7 | 1438.7 | 0
CE190 as180 loPLR | 190 | 190 | 188.49 | 188.4525 | 187.7391 | 189.5652 | 189.8558 | 189.7529 | 189.7 | 189.7 | 0
CE195 as185 loPLR | 209 | 209 | 207.326 | 207.5029 | 205.7557 | 208.7252 | 208.942 | 208.9462 | 209 | 209 | 0
CE200 ARI PLR=1 hiSHR | 4122 | 4062 | 4120.502 | 4121.6295 | 4119.9223 | 4121.9808 | 4121.9808 | 4122.2309 | 4122.2 | 4122.2 | 0
Zone Load, Latent (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CE150 as110 hiSHR | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 0
CE160 as150 hiIDB | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 0
CE165 as150 mIDB mODB | 739 | 739 | 739.2 | 739.449 | 739.1966 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 0
CE170 as150 mSHR mPLR | 739 | 739 | 739.2 | 739.449 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 739.2 | 0
CE180 as150 loSHR | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 0
CE185 loSHR hiODB | 2957 | 2957 | 2956.8 | 2957.5029 | 2956.7866 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 2956.8 | 0
CE190 as180 loPLR | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 0
CE195 as185 loPLR | 367 | 370 | 369.6 | 369.578 | 369.5991 | 369.6 | 369.6 | 369.6 | 369.6 | 369.6 | 0
CE200 ARI PLR=1 hiSHR | 1221 | 1221 | 1221.024 | 1221.2778 | 1220.9824 | 1221.024 | 1221.024 | 1221.024 | 1221 | 1221 | 0
Latent Coil - Zone Load, (Should be 0) (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | 0 | 0 | 0 | 0
CE150 as110 hiSHR | 0 | 0 | 0 | 2.0516 | 0.00057016 | 0 | 0.00687 | -0.0044111 | 0 | 0.2 | 0
CE160 as150 hiIDB | 1 | 0 | 0 | 0 | 0.00054522 | 0 | -0.00534 | 0.039573 | 0 | -0.1 | 0
CE165 as150 mIDB mODB | 1 | 0 | 0 | 0.87925 | 0.0010962 | 0 | -0.01082 | 0.045435 | 0 | 0.1 | 0
CE170 as150 mSHR mPLR | 1 | 0 | 0 | -0.58617 | 0.00076678 | 0 | 0.01152 | 0.1157 | 0 | 0.2 | 0
CE180 as150 loSHR | 1 | 0 | 0 | -29.6014 | 0.0061807 | 0 | -0.00076 | 0.67126 | 0 | -0.7 | 0
CE185 loSHR hiODB | 2 | 0 | 0 | -27.5498 | 0.012727 | 0 | 0.01946 | 0.72237 | 0 | -0.6 | 0
CE190 as180 loPLR | 3 | 0 | 0 | -3.2239 | 0.0048306 | 0 | 0.046846 | 0.11557 | 0 | 0.2 | 0
CE195 as185 loPLR | 3 | 0 | 0 | -2.9308 | 0.023067 | 0 | 0.0055 | 0.1294 | 0 | 0 | 0
CE200 ARI PLR=1 hiSHR | 1 | 0 | -0.024 | -2.0516 | 0.0013081 | 0 | 0 | 0.082262 | 0 | 0 | 0
Coil Loads: Total, Sensible, and Latent
Coil Load, Total (kWh,thermal)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 3800 | 3800 | 3841.47 | 3793.9625 | 3796.6945 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 0
CE110 as100 lo ODB | 3765 | 3766 | 3803.58 | 3755.5686 | 3762.6846 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 0
CE120 as100 hiIDB | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.3788 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 0
CE130 as100 lo PLR | 219 | 219 | 215.778 | 215.1231 | 215.9611 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 0
CE140 as130 lo ODB | 198 | 198 | 195.53 | 194.6073 | 195.8173 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 0
CE150 as110 hiSHR | 4517 | 4517 | 4542.78 | 4527.5498 | 4508.3212 | 4516.9958 | 4515.0285 | 4517.5274 | 4517.4 | 4518.3 | 0
CE160 as150 hiIDB | 4501 | 4500 | 4516.378 | 4508.4994 | 4490.5145 | 4500.0682 | 4498.8816 | 4500.5449 | 4500.3 | 4499.9 | 0
CE165 as150 mIDB mODB | 4538 | 4538 | 4567.458 | 4548.9449 | 4527.873 | 4537.0685 | 4535.1008 | 4536.998 | 4537.3 | 4537.9 | 0
CE170 as150 mSHR mPLR | 2233 | 2232 | 2226.057 | 2236.5182 | 2224.4208 | 2231.6851 | 2231.6345 | 2232.3427 | 2231.9 | 2232.5 | 0
CE180 as150 loSHR | 4495 | 4495 | 4509.984 | 4534.5838 | 4480.7708 | 4494.6115 | 4494.0999 | 4495.2651 | 4494.9 | 4493.8 | 0
CE185 loSHR hiODB | 4507 | 4535 | 4564.894 | 4582.6495 | 4521.5036 | 4534.5283 | 4533.9432 | 4535.1231 | 4534.9 | 4533.9 | 0
CE190 as180 loPLR | 578 | 577 | 572.607 | 578.5463 | 573.8077 | 577.1889 | 577.6703 | 577.5279 | 577.3 | 577.7 | 0
CE195 as185 loPLR | 602 | 601 | 595.24 | 601.6999 | 596.6464 | 600.9508 | 601.339 | 601.3744 | 601.2 | 601.2 | 0
CE200 ARI PLR=1 hiSHR | 5498 | 5436 | 5534.2 | 5521.9812 | 5483.8906 | 5497.5648 | 5497.5648 | 5497.8008 | 5497.8 | 5497.8 | 0
Coil Load, Sensible (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 3800 | 3800 | 3841.47 | 3793.9625 | 3796.6945 | 3799.7366 | 3797.9491 | 3800.3599 | 3800.4 | 3800.4 | 0
CE110 as100 lo ODB | 3765 | 3766 | 3803.58 | 3755.5686 | 3762.6846 | 3764.6112 | 3763.2362 | 3765.2438 | 3765 | 3765.3 | 0
CE120 as100 hiIDB | 3749 | 3749 | 3763.48 | 3739.1559 | 3746.3788 | 3748.4294 | 3746.8105 | 3748.902 | 3748.8 | 3748.5 | 0
CE130 as100 lo PLR | 219 | 219 | 215.778 | 215.1231 | 215.9611 | 218.9853 | 219.7695 | 219.3541 | 219.3 | 219.2 | 0
CE140 as130 lo ODB | 198 | 198 | 195.53 | 194.6073 | 195.8173 | 197.6748 | 198.5643 | 197.9671 | 197.9 | 197.3 | 0
CE150 as110 hiSHR | 3778 | 3778 | 3803.58 | 3786.0492 | 3769.124 | 3777.7958 | 3775.8216 | 3778.3318 | 3778.2 | 3779 | 0
CE160 as150 hiIDB | 3761 | 3761 | 3777.178 | 3769.0504 | 3751.3173 | 3760.8682 | 3759.6868 | 3761.3053 | 3761.1 | 3760.8 | 0
CE165 as150 mIDB mODB | 3798 | 3798 | 3828.258 | 3808.6166 | 3788.6753 | 3797.8685 | 3795.9117 | 3797.7525 | 3798.1 | 3798.6 | 0
CE170 as150 mSHR mPLR | 1493 | 1493 | 1486.857 | 1497.6553 | 1485.2201 | 1492.4851 | 1492.423 | 1493.027 | 1492.7 | 1493.1 | 0
CE180 as150 loSHR | 1537 | 1538 | 1553.184 | 1606.6823 | 1523.978 | 1537.8115 | 1537.3001 | 1537.7939 | 1538.1 | 1537.7 | 0
CE185 loSHR hiODB | 1548 | 1578 | 1608.094 | 1652.6964 | 1564.7043 | 1577.7283 | 1577.1233 | 1577.6007 | 1578.1 | 1577.7 | 0
CE190 as180 loPLR | 208 | 208 | 203.007 | 212.1923 | 204.2038 | 207.5889 | 208.0235 | 207.8123 | 207.7 | 207.9 | 0
CE195 as185 loPLR | 232 | 232 | 225.64 | 235.0528 | 227.0242 | 231.3508 | 231.7335 | 231.645 | 231.6 | 231.6 | 0
CE200 ARI PLR=1 hiSHR | 4276 | 4215 | 4313.176 | 4302.755 | 4262.9069 | 4276.5408 | 4276.5408 | 4276.6945 | 4276.8 | 4276.8 | 0
Coil Load, Latent (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 0 | 0 | 0 | 0 | 0 | 0 | 3.3138e-14 | 0 | 0 | 0 | 0
CE110 as100 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | 2.6912e-15 | 0 | 0 | 0 | 0
CE120 as100 hiIDB | 0 | 0 | 0 | 0 | 0 | 0 | 3.8103e-15 | 0 | 0 | 0 | 0
CE130 as100 lo PLR | 0 | 0 | 0 | 0 | 0 | 0 | 3.1415e-14 | 0 | 0 | 0 | 0
CE140 as130 lo ODB | 0 | 0 | 0 | 0 | 0 | 0 | -2.7533e-16 | 0 | 0 | 0 | 0
CE150 as110 hiSHR | 739 | 739 | 739.2 | 741.5006 | 739.1972 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 0
CE160 as150 hiIDB | 740 | 739 | 739.2 | 739.449 | 739.1972 | 739.2 | 739.1947 | 739.2396 | 739.2 | 739.1 | 0
CE165 as150 mIDB mODB | 740 | 739 | 739.2 | 740.3283 | 739.1977 | 739.2 | 739.1892 | 739.2454 | 739.2 | 739.3 | 0
CE170 as150 mSHR mPLR | 740 | 739 | 739.2 | 738.8628 | 739.2008 | 739.2 | 739.2115 | 739.3157 | 739.2 | 739.4 | 0
CE180 as150 loSHR | 2958 | 2957 | 2956.8 | 2927.9015 | 2956.7927 | 2956.8 | 2956.7992 | 2957.4713 | 2956.8 | 2956.1 | 0
CE185 loSHR hiODB | 2959 | 2957 | 2956.8 | 2929.9531 | 2956.7993 | 2956.8 | 2956.8195 | 2957.5224 | 2956.8 | 2956.2 | 0
CE190 as180 loPLR | 370 | 370 | 369.6 | 366.354 | 369.6039 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 0
CE195 as185 loPLR | 370 | 370 | 369.6 | 366.6471 | 369.6221 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 0
CE200 ARI PLR=1 hiSHR | 1222 | 1221 | 1221 | 1219.2263 | 1220.9837 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 0
Sensible Coil - Zone Load, (Fan Heat) (kWh,thermal)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re |  | Analytical |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
CE100 dry lo IDB hi ODB | 144 | 144 | 187.05 | 138.6284 | 143.5848 | 143.6534 | 142.3632 | 144.0536 | 144.1 | 144.1 | 0
CE110 as100 lo ODB | 128 | 129 | 167.979 | 118.9918 | 127.5927 | 127.6867 | 126.6828 | 128.1309 | 127.9 | 128.2 | 0
CE120 as100 hiIDB | 117 | 117 | 133.008 | 107.5615 | 116.438 | 116.6726 | 115.4889 | 116.9127 | 116.9 | 116.6 | 0
CE130 as100 lo PLR | 10 | 10 | 8.434 | 7.6202 | 10.2115 | 10.2601 | 10.3985 | 10.4079 | 10.3 | 10.2 | 0
CE140 as130 lo ODB | 8 | 8 | 7.027 | 6.1547 | 8.0856 | 8.1097 | 8.2063 | 8.2142 | 8.2 | 7.6 | 0
CE150 as110 hiSHR | 141 | 141 | 167.979 | 149.4725 | 134.0026 | 140.8714 | 139.4441 | 141.2189 | 141.1 | 141.9 | 0
CE160 as150 hiIDB | 129 | 129 | 146.726 | 137.456 | 121.3436 | 129.1114 | 128.2687 | 129.316 | 129.2 | 128.9 | 0
CE165 as150 mIDB mODB | 149 | 149 | 181.387 | 160.6096 | 142.712 | 149.3587 | 147.9512 | 149.1144 | 149.4 | 149.9 | 0
CE170 as150 mSHR mPLR | 73 | 73 | 68.706 | 79.1325 | 67.7064 | 73.1606 | 73.002 | 73.5141 | 73.2 | 73.6 | 0
CE180 as150 loSHR | 117 | 118 | 135.132 | 188.1594 | 106.4247 | 118.487 | 118.1294 | 118.281 | 118.6 | 118.2 | 0
CE185 loSHR hiODB | 109 | 139 | 171.245 | 215.4162 | 129.1418 | 139.2451 | 138.8308 | 138.8945 | 139.4 | 139 | 0
CE190 as180 loPLR | 18 | 18 | 14.517 | 23.7397 | 16.4646 | 18.0237 | 18.1676 | 18.0594 | 18 | 18.2 | 0
CE195 as185 loPLR | 23 | 23 | 18.314 | 27.5498 | 21.2685 | 22.6256 | 22.7915 | 22.6987 | 22.6 | 22.6 | 0
CE200 ARI PLR=1 hiSHR | 154 | 153 | 192.674 | 181.1254 | 142.9847 | 154.56 | 154.56 | 154.4636 | 154.6 | 154.6 | 0

## Data-Delta
Sensitivities for Space Cooling Electricity Consumption
Delta Qtot (kWh,e)
0 | CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical | 0 | 0 | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -454 | -441 | -459.621 | -454 | -450.8529 | -455.3055 | -449.9711 | -454.3131 | -453.6 | -453.2 | 0
E120-110 IDB | -65 | -77 | -50.092 | -62 | -62.6934 | -59.6584 | -60.3021 | -63.5575 | -66.2 | -66.4 | 0
E120-100 IDB+ODB | -519 | -518 | -509.713 | -516 | -513.5463 | -514.9639 | -510.2732 | -517.8706 | -519.8 | -519.6 | 0
E130-100 PLR | -1421 | -1421 | -1415.398 | -1413 | -1412.0645 | -1413.5415 | -1401.8208 | -1419.9663 | -1421.3 | -1421.1 | 0
E140-130 ODB @loPLR | -42 | -40 | -40.411 | -40 | -40.3501 | -40.9605 | -41.4733 | -41.5864 | -41 | -41.2 | 0
E140-110 PLR @loODB | -1009 | -1020 | -996.188 | -999 | -1001.5617 | -999.1966 | -993.323 | -1007.2396 | -1008.7 | -1009.1 | 0
E150-110 hiSHR v. dry | 131 | 118 | 141.228 | 118 | 128.2886 | 132.0944 | 129.6472 | 130.2551 | 129.3 | 129.1 | 0
E160-150 IDB @hiSHR | -68 | -68 | -64.794 | -76 | -65.3881 | -62.3216 | -58.7295 | -66.05 | -67.2 | -67.6 | 0
E165-160 IDB+ODB @hiSH | 362 | 362 | 361.817 | 363 | 359.356 | 362.977 | 357.0433 | 357.3902 | 360.4 | 360.7 | 0
E170-150 sens x 0.39 | -570 | -569 | -573.348 | -563 | -562.1205 | -563.1461 | -555.7842 | -565.3727 | -568.8 | -568.7 | 0
E180-150 SHR | -125 | -125 | -125.315 | -103 | -115.294 | -117.7844 | -111.5753 | -123.824 | -124.2 | -124.6 | 0
E180-170 lat x 4 | 445 | 444 | 448.033 | 460 | 446.8265 | 445.3617 | 444.2089 | 441.5487 | 444.6 | 444.1 | 0
E185-180 ODB @loSHR | 461 | 461 | 464.046 | 467 | 458.2115 | 460.255 | 458.3596 | 461.9737 | 461.1 | 461 | 0
E190-180 PLR @loSHR | -919 | -918 | -916.89 | -920 | -918.1623 | -917.2731 | -914.9174 | -917.493 | -918.2 | -917.7 | 0
E190-140 lat @loPLR | 96 | 95 | 95.211 | 94 | 96.394 | 96.2334 | 96.4774 | 96.1777 | 95.6 | 95.9 | 0
E195-190 ODB @loPLloSH | 86 | 86 | 84.7 | 86 | 85.546 | 85.7346 | 86.4597 | 86.9875 | 85.9 | 85.8 | 0
E195-185 PLR @loSHR | -1294 | -1293 | -1296.236 | -1301 | -1290.8277 | -1291.7935 | -1286.8173 | -1292.4792 | -1293.4 | -1292.9 | 0
E195-130 lat @loPLR | 140 | 141 | 139.5 | 140 | 141.5899 | 141.0075 | 141.4638 | 141.5788 | 140.5 | 140.5 | 0
E200-100 ARI v dry | -54 | -66 | -52.603 | -79 | -54.8104 | -42.2735 | -31.9443 | -54.7376 | -53.4 | -53.5 | 0
Del Qcomp (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -430 | -419 | -441.592 | -428 | 0 | -431.8474 | -426.8936 | -430.9138 | -429.8 | -429.5 | 0
E120-110 IDB | -49 | -59 | -15.798 | -45 | 0 | -43.4717 | -43.903 | -47.0715 | -50.1 | -50.2 | 0
E120-100 IDB+ODB | -479 | -478 | -457.39 | -473 | 0 | -475.319 | -470.7965 | -477.9853 | -479.9 | -479.7 | 0
E130-100 PLR | -1224 | -1224 | -1214.26 | -1218 | 0 | -1217.5188 | -1207.8769 | -1223.5648 | -1224.6 | -1224.6 | 0
E140-130 ODB @loPLR | -38 | -37 | -38.399 | -37 | 0 | -37.8005 | -38.2753 | -38.3628 | -37.9 | -37.9 | 0
E140-110 PLR @loODB | -832 | -842 | -811.067 | -827 | 0 | -823.472 | -819.2586 | -831.0138 | -832.7 | -833 | 0
E150-110 hiSHR v. dry | 111 | 100 | 141.228 | 99 | 0 | 112.7146 | 110.9181 | 111.0199 | 110 | 109.8 | 0
E160-150 IDB @hiSHR | -50 | -50 | -44.419 | -56 | 0 | -45.0374 | -42.3919 | -48.5466 | -49.8 | -50.1 | 0
E165-160 IDB+ODB @hiSH | 333 | 332 | 328.567 | 330 | 0 | 333.2246 | 328.108 | 328.3094 | 330.8 | 331.1 | 0
E170-150 sens x 0.39 | -469 | -469 | -468.135 | -459 | 0 | -463.6356 | -458.1666 | -465.9883 | -469.2 | -469.1 | 0
E180-150 SHR | -91 | -91 | -92.832 | -70 | 0 | -84.887 | -80.3105 | -90.836 | -91.2 | -91.5 | 0
E180-170 lat x 4 | 378 | 378 | 375.303 | 389 | 0 | 378.7486 | 377.8561 | 375.1523 | 378 | 377.6 | 0
E185-180 ODB @loSHR | 431 | 431 | 428.419 | 432 | 0 | 429.7507 | 427.9509 | 431.6779 | 430.6 | 430.5 | 0
E190-180 PLR @loSHR | -771 | -770 | -774.839 | -774 | 0 | -769.6356 | -767.9826 | -769.6508 | -770.4 | -770 | 0
E190-140 lat @loPLR | 81 | 81 | 84.624 | 82 | 0 | 81.6639 | 81.8837 | 81.5469 | 81.1 | 81.3 | 0
E195-190 ODB @loPLloSH | 79 | 79 | 79.444 | 79 | 0 | 78.9721 | 79.6337 | 80.1527 | 79.2 | 79.1 | 0
E195-185 PLR @loSHR | -1123 | -1122 | -1123.814 | -1127 | 0 | -1120.4142 | -1116.2999 | -1121.176 | -1121.8 | -1121.4 | 0
E195-130 lat @loPLR | 122 | 123 | 125.669 | 124 | 0 | 122.8356 | 123.242 | 123.3368 | 122.4 | 122.5 | 0
E200-100 ARI v dry | -69 | -79 | -58.431 | -93 | 0 | -58.3094 | -49.8691 | -70.0317 | -68.8 | -68.9 | 0
Del Q IDfan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -16 | -15 | -12.268 | -19 | -15.9921 | -15.9627 | -15.7035 | -15.9226 | -16.2 | -16.1 | 0
E120-110 IDB | -11 | -12 | -23.336 | -12 | -11.1547 | -11.0148 | -11.1592 | -11.2183 | -11 | -11 | 0
E120-100 IDB+ODB | -27 | -27 | -35.604 | -31 | -27.1468 | -26.9774 | -26.8627 | -27.1409 | -27.2 | -27.1 | 0
E130-100 PLR | -134 | -134 | -136.869 | -133 | -133.3733 | -133.3883 | -131.9736 | -133.646 | -133.8 | -133.7 | 0
E140-130 ODB @loPLR | -2 | -2 | -1.369 | -2 | -2.1259 | -2.1503 | -2.1761 | -2.1936 | -2.2 | -2.2 | 0
E140-110 PLR @loODB | -120 | -121 | -125.97 | -116 | -119.5071 | -119.5759 | -118.4462 | -119.917 | -119.8 | -119.8 | 0
E150-110 hiSHR v. dry | 13 | 12 | 0 | 14 | 12.757 | 13.1873 | 12.7446 | 13.0891 | 13.2 | 13.2 | 0
E160-150 IDB @hiSHR | -12 | -12 | -13.865 | -15 | -11.9691 | -11.7613 | -11.1173 | -11.9106 | -11.9 | -11.9 | 0
E165-160 IDB+ODB @hiSH | 20 | 21 | 22.626 | 24 | 20.2354 | 20.246 | 19.6897 | 19.7887 | 20.1 | 20.1 | 0
E170-150 sens x 0.39 | -68 | -68 | -71.595 | -73 | -67.3106 | -67.7141 | -66.4261 | -67.6284 | -67.9 | -67.9 | 0
E180-150 SHR | -23 | -22 | -22.104 | -24 | -21.8861 | -22.3857 | -21.2749 | -22.4474 | -22.5 | -22.6 | 0
E180-170 lat x 4 | 45 | 46 | 49.491 | 49 | 45.4245 | 45.3284 | 45.1513 | 45.181 | 45.4 | 45.3 | 0
E185-180 ODB @loSHR | 21 | 20 | 24.243 | 25 | 20.6754 | 20.7574 | 20.6923 | 20.6154 | 20.8 | 20.8 | 0
E190-180 PLR @loSHR | -100 | -101 | -96.662 | -98 | -100.4513 | -100.4635 | -99.9852 | -100.6027 | -100.6 | -100.5 | 0
E190-140 lat @loPLR | 10 | 10 | 7.204 | 8 | 9.9268 | 9.9142 | 9.9306 | 9.9559 | 9.9 | 9.9 | 0
E195-190 ODB @loPLloSH | 5 | 5 | 3.577 | 4 | 4.5989 | 4.6017 | 4.6449 | 4.6509 | 4.6 | 4.6 | 0
E195-185 PLR @loSHR | -116 | -116 | -117.328 | -119 | -116.5278 | -116.6191 | -116.0326 | -116.5672 | -116.8 | -116.7 | 0
E195-130 lat @loPLR | 13 | 13 | 9.412 | 10 | 12.3997 | 12.3655 | 12.3994 | 12.4132 | 12.3 | 12.3 | 0
E200-100 ARI v dry | 10 | 9 | 3.966 | 10 | 9.9058 | 10.9119 | 12.1975 | 10.4073 | 10.5 | 10.6 | 0
Del Q ODfan (kWh,e)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -8 | -7 | -5.761 | -7 | 0 | -7.4954 | -7.374 | -7.4767 | -7.5 | -7.5 | 0
E120-110 IDB | -5 | -6 | -10.958 | -5 | 0 | -5.172 | -5.24 | -5.2677 | -5.2 | -5.2 | 0
E120-100 IDB+ODB | -13 | -13 | -16.719 | -12 | 0 | -12.6674 | -12.6139 | -12.7444 | -12.7 | -12.7 | 0
E130-100 PLR | -63 | -63 | -64.269 | -62 | 0 | -62.6344 | -61.9703 | -62.7555 | -62.8 | -62.8 | 0
E140-130 ODB @loPLR | -1 | -1 | -0.643 | -1 | 0 | -1.0097 | -1.0218 | -1.03 | -1 | -1 | 0
E140-110 PLR @loODB | -56 | -57 | -59.151 | -56 | 0 | -56.1487 | -55.6182 | -56.3088 | -56.3 | -56.3 | 0
E150-110 hiSHR v. dry | 6 | 5 | 0 | 5 | 0 | 6.1925 | 5.9844 | 6.1462 | 6.2 | 6.1 | 0
E160-150 IDB @hiSHR | -5 | -5 | -6.51 | -5 | 0 | -5.5228 | -5.2203 | -5.5928 | -5.6 | -5.5 | 0
E165-160 IDB+ODB @hiSH | 9 | 9 | 10.624 | 9 | 0 | 9.5064 | 9.2456 | 9.2921 | 9.4 | 9.4 | 0
E170-150 sens x 0.39 | -32 | -32 | -33.618 | -31 | 0 | -31.7964 | -31.1915 | -31.756 | -31.9 | -31.8 | 0
E180-150 SHR | -10 | -10 | -10.379 | -9 | 0 | -10.5117 | -9.99 | -10.5405 | -10.6 | -10.5 | 0
E180-170 lat x 4 | 22 | 22 | 23.239 | 22 | 0 | 21.2847 | 21.2015 | 21.2154 | 21.3 | 21.3 | 0
E185-180 ODB @loSHR | 9 | 9 | 11.384 | 10 | 0 | 9.7468 | 9.7164 | 9.6803 | 9.7 | 9.7 | 0
E190-180 PLR @loSHR | -48 | -47 | -45.389 | -48 | 0 | -47.1741 | -46.9496 | -47.2395 | -47.2 | -47.2 | 0
E190-140 lat @loPLR | 4 | 5 | 3.383 | 4 | 0 | 4.6553 | 4.6631 | 4.6749 | 4.7 | 4.7 | 0
E195-190 ODB @loPLloSH | 3 | 2 | 1.679 | 3 | 0 | 2.1608 | 2.1811 | 2.1839 | 2.1 | 2.1 | 0
E195-185 PLR @loSHR | -54 | -54 | -55.094 | -55 | 0 | -54.7601 | -54.4849 | -54.7359 | -54.8 | -54.8 | 0
E195-130 lat @loPLR | 6 | 6 | 4.419 | 6 | 0 | 5.8064 | 5.8223 | 5.8288 | 5.8 | 5.8 | 0
E200-100 ARI v dry | 5 | 4 | 1.862 | 4 | 0 | 5.124 | 5.7274 | 4.8869 | 5 | 5 | 0
Sensitivities for COP and Coil Loads
Delta COP (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | 0.99 | 0.953 | 1.0285 | 1.0082 | 0.99634 | 1.0069 | 1.0087 | 0.99059 | 0.99 | 0.99 | 0
E120-110 IDB | 0.21 | 0.248 | 0.155 | 0.20837 | 0.2066 | 0.19677 | 0.20416 | 0.20704 | 0.21 | 0.21 | 0
E120-100 IDB+ODB | 1.2 | 1.201 | 1.1835 | 1.2166 | 1.2029 | 1.2037 | 1.2129 | 1.1976 | 1.2 | 1.2 | 0
E130-100 PLR | -0.48 | -0.48 | -0.4552 | -0.45341 | -0.50009 | -0.48198 | -0.50212 | -0.49937 | -0.48 | -0.48 | 0
E140-130 ODB @loPLR | 0.86 | 0.825 | 0.9399 | 0.901 | 0.86717 | 0.87767 | 0.88334 | 0.86071 | 0.86 | 0.86 | 0
E140-110 PLR @loODB | -0.61 | -0.608 | -0.5438 | -0.56063 | -0.62926 | -0.61124 | -0.6275 | -0.62925 | -0.61 | -0.61 | 0
E150-110 hiSHR v. dry | 0.24 | 0.288 | 0.2086 | 0.28537 | 0.2531 | 0.24097 | 0.24631 | 0.24783 | 0.25 | 0.25 | 0
E160-150 IDB @hiSHR | 0.22 | 0.21 | 0.1983 | 0.25 | 0.20639 | 0.19555 | 0.18654 | 0.20563 | 0.21 | 0.21 | 0
E165-160 IDB+ODB @hiSH | -0.92 | -0.92 | -0.9144 | -0.96474 | -0.91897 | -0.91948 | -0.91505 | -0.90343 | -0.91 | -0.91 | 0
E170-150 sens x 0.39 | -0.24 | -0.24 | -0.2252 | -0.223 | -0.25878 | -0.25525 | -0.27013 | -0.26014 | -0.24 | -0.24 | 0
E180-150 SHR | 0.42 | 0.41 | 0.4167 | 0.326 | 0.3891 | 0.39757 | 0.38162 | 0.41502 | 0.41 | 0.41 | 0
E180-170 lat x 4 | 0.66 | 0.65 | 0.6419 | 0.549 | 0.64788 | 0.65282 | 0.65175 | 0.67516 | 0.65 | 0.65 | 0
E185-180 ODB @loSHR | -1.19 | -1.19 | -1.2098 | -1.203 | -1.1904 | -1.196 | -1.1976 | -1.1965 | -1.19 | -1.19 | 0
E190-180 PLR @loSHR | -0.63 | -0.63 | -0.5977 | -0.569 | -0.64659 | -0.63762 | -0.65027 | -0.65583 | -0.63 | -0.63 | 0
E190-140 lat @loPLR | 0.64 | 0.676 | 0.5714 | 0.603 | 0.62487 | 0.61216 | 0.60515 | 0.63627 | 0.64 | 0.64 | 0
E195-190 ODB @loPLloSH | -1.1 | -1.1 | -1.1267 | -1.12 | -1.0909 | -1.0938 | -1.0994 | -1.0921 | -1.1 | -1.1 | 0
E195-185 PLR @loSHR | -0.54 | -0.54 | -0.5146 | -0.48603 | -0.54708 | -0.53547 | -0.55209 | -0.55141 | -0.54 | -0.54 | 0
E195-130 lat @loPLR | 0.4 | 0.401 | 0.3846 | 0.384 | 0.40112 | 0.39602 | 0.3891 | 0.40487 | 0.4 | 0.4 | 0
E200-100 ARI v dry | 1.23 | 1.221 | 1.2373 | 1.3016 | 1.2417 | 1.2084 | 1.1918 | 1.2317 | 1.23 | 1.23 | 0
Del Q coil,t (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -35 | -34 | -37.89 | -38.3939 | -34.0099 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | 0
E120-110 IDB | -16 | -17 | -40.1 | -16.4127 | -16.3058 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | 0
E120-100 IDB+ODB | -51 | -51 | -77.99 | -54.8066 | -50.3157 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | 0
E130-100 PLR | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.7334 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | 0
E140-130 ODB @loPLR | -21 | -21 | -20.248 | -20.5158 | -20.1438 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | 0
E140-110 PLR @loODB | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.8672 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | 0
E150-110 hiSHR v. dry | 752 | 751 | 739.2 | 771.9812 | 745.6367 | 752.3846 | 751.7923 | 752.2836 | 752.4 | 753 | 0
E160-150 IDB @hiSHR | -16 | -17 | -26.402 | -19.0504 | -17.8067 | -16.9277 | -16.1469 | -16.9825 | -17.1 | -18.4 | 0
E165-160 IDB+ODB @hiSH | 37 | 38 | 51.08 | 40.4455 | 37.3585 | 37.0003 | 36.2193 | 36.4531 | 37 | 38 | 0
E170-150 sens x 0.39 | -2284 | -2285 | -2316.723 | -2291.0317 | -2283.9004 | -2285.3107 | -2283.394 | -2285.1847 | -2285.5 | -2285.8 | 0
E180-150 SHR | -22 | -22 | -32.796 | 7.034 | -27.5505 | -22.3843 | -20.9286 | -22.2623 | -22.5 | -24.5 | 0
E180-170 lat x 4 | 2262 | 2263 | 2283.927 | 2298.0657 | 2256.3499 | 2262.9264 | 2262.4654 | 2262.9224 | 2263 | 2261.3 | 0
E185-180 ODB @loSHR | 12 | 40 | 54.91 | 48.0657 | 40.7328 | 39.9168 | 39.8433 | 39.858 | 40 | 40.1 | 0
E190-180 PLR @loSHR | -3917 | -3918 | -3937.377 | -3956.0375 | -3906.9631 | -3917.4227 | -3916.4296 | -3917.7372 | -3917.6 | -3916.1 | 0
E190-140 lat @loPLR | 380 | 379 | 377.077 | 383.939 | 377.9903 | 379.514 | 379.106 | 379.5607 | 379.4 | 380.4 | 0
E195-190 ODB @loPLloSH | 24 | 24 | 22.633 | 23.1536 | 22.8387 | 23.7619 | 23.6687 | 23.8465 | 23.9 | 23.5 | 0
E195-185 PLR @loSHR | -3905 | -3934 | -3969.654 | -3980.9496 | -3924.8572 | -3933.5775 | -3932.6042 | -3933.7487 | -3933.7 | -3932.7 | 0
E195-130 lat @loPLR | 383 | 382 | 379.462 | 386.5768 | 380.6852 | 381.9655 | 381.5695 | 382.0203 | 381.9 | 382 | 0
E200-100 ARI v dry | 1698 | 1636 | 1692.73 | 1728.0188 | 1687.1961 | 1697.8282 | 1699.6157 | 1697.4409 | 1697.4 | 1697.4 | 0
Del Q coil,s (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | -35 | -34 | -37.89 | -38.3939 | -34.0099 | -35.1254 | -34.7129 | -35.1161 | -35.4 | -35.1 | 0
E120-110 IDB | -16 | -17 | -40.1 | -16.4127 | -16.3058 | -16.1818 | -16.4257 | -16.3418 | -16.2 | -16.8 | 0
E120-100 IDB+ODB | -51 | -51 | -77.99 | -54.8066 | -50.3157 | -51.3072 | -51.1386 | -51.4579 | -51.6 | -51.9 | 0
E130-100 PLR | -3581 | -3581 | -3625.692 | -3578.8394 | -3580.7334 | -3580.7513 | -3578.1796 | -3581.0058 | -3581.1 | -3581.2 | 0
E140-130 ODB @loPLR | -21 | -21 | -20.248 | -20.5158 | -20.1438 | -21.3105 | -21.2052 | -21.387 | -21.4 | -21.9 | 0
E140-110 PLR @loODB | -3567 | -3568 | -3608.05 | -3560.9613 | -3566.8672 | -3566.9364 | -3564.6719 | -3567.2767 | -3567.1 | -3568 | 0
E150-110 hiSHR v. dry | 13 | 12 | 0 | 30.4807 | 6.4394 | 13.1846 | 12.5854 | 13.088 | 13.2 | 13.7 | 0
E160-150 IDB @hiSHR | -17 | -17 | -26.402 | -16.9988 | -17.8067 | -16.9277 | -16.1348 | -17.0265 | -17.1 | -18.2 | 0
E165-160 IDB+ODB @hiSH | 37 | 37 | 51.08 | 39.5662 | 37.3579 | 37.0003 | 36.2248 | 36.4472 | 37 | 37.8 | 0
E170-150 sens x 0.39 | -2285 | -2285 | -2316.723 | -2288.3939 | -2283.904 | -2285.3107 | -2283.3986 | -2285.3048 | -2285.5 | -2285.9 | 0
E180-150 SHR | -2241 | -2240 | -2250.396 | -2179.3669 | -2245.146 | -2239.9843 | -2238.5215 | -2240.5379 | -2240.1 | -2241.3 | 0
E180-170 lat x 4 | 44 | 45 | 66.327 | 109.027 | 38.758 | 45.3264 | 44.8771 | 44.7669 | 45.4 | 44.6 | 0
E185-180 ODB @loSHR | 11 | 40 | 54.91 | 46.0141 | 40.7262 | 39.9168 | 39.8232 | 39.8069 | 40 | 40 | 0
E190-180 PLR @loSHR | -1329 | -1330 | -1350.177 | -1394.49 | -1319.7742 | -1330.2227 | -1329.2766 | -1329.9815 | -1330.4 | -1329.8 | 0
E190-140 lat @loPLR | 10 | 10 | 7.477 | 17.585 | 8.3865 | 9.914 | 9.4592 | 9.8452 | 9.8 | 10.6 | 0
E195-190 ODB @loPLloSH | 24 | 24 | 22.633 | 22.8605 | 22.8205 | 23.7619 | 23.71 | 23.8326 | 23.9 | 23.7 | 0
E195-185 PLR @loSHR | -1316 | -1346 | -1382.454 | -1417.6436 | -1337.68 | -1346.3775 | -1345.3897 | -1345.9558 | -1346.5 | -1346.1 | 0
E195-130 lat @loPLR | 13 | 13 | 9.862 | 19.9297 | 11.0631 | 12.3655 | 11.964 | 12.2909 | 12.3 | 12.4 | 0
E200-100 ARI v dry | 476 | 415 | 471.706 | 508.7925 | 466.2125 | 476.8042 | 478.5917 | 476.3346 | 476.4 | 476.4 | 0
Del Qcoil,lat (kWh,t)
| CA-SIS | CLM2000 | DOE21E | DOE21E | Energy+ | TRN-id | TRN-re | Analytical |  |  | Your
| CASIS/EDF | CLIM2000/EDF | DOE-2.1E/CIEMAT | DOE-2.1E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | TRNSYS-ideal/TUD | TRNSYS-real/TUD | Analytical/TUD | Analytical/HTAL1 | Analytical/HTAL2 | Software
E110-100 ODB | 0 | 0 | 0 | 0 | 0 | 0 | -3.0447e-14 | 0 | 0 | 0 | 0
E120-110 IDB | 0 | 0 | 0 | 0 | 0 | 0 | 1.1191e-15 | 0 | 0 | 0 | 0
E120-100 IDB+ODB | 0 | 0 | 0 | 0 | 0 | 0 | -2.9328e-14 | 0 | 0 | 0 | 0
E130-100 PLR | 0 | 0 | 0 | 0 | 0 | 0 | -1.7231e-15 | 0 | 0 | 0 | 0
E140-130 ODB @loPLR | 0 | 0 | 0 | 0 | 0 | 0 | -3.169e-14 | 0 | 0 | 0 | 0
E140-110 PLR @loODB | 0 | 0 | 0 | 0 | 0 | 0 | -2.9665e-15 | 0 | 0 | 0 | 0
E150-110 hiSHR v. dry | 739 | 739 | 739.2 | 741.5006 | 739.1972 | 739.2 | 739.2069 | 739.1956 | 739.2 | 739.4 | 0
E160-150 IDB @hiSHR | 1 | 0 | 0 | -2.0516 | -2.4939e-05 | 0 | -0.01221 | 0.043984 | 0 | -0.3 | 0
E165-160 IDB+ODB @hiSH | 0 | 0 | 0 | 0.87925 | 0.00055101 | 0 | -0.00548 | 0.005862 | 0 | 0.2 | 0
E170-150 sens x 0.39 | 1 | 0 | 0 | -2.6377 | 0.0035566 | 0 | 0.00465 | 0.12011 | 0 | 0 | 0
E180-150 SHR | 2219 | 2218 | 2217.6 | 2186.4009 | 2217.5955 | 2217.6 | 2217.5924 | 2218.2757 | 2217.6 | 2216.7 | 0
E180-170 lat x 4 | 2218 | 2218 | 2217.6 | 2189.0387 | 2217.592 | 2217.6 | 2217.5877 | 2218.1556 | 2217.6 | 2216.7 | 0
E185-180 ODB @loSHR | 1 | 0 | 0 | 2.0516 | 0.0065461 | 0 | 0.02022 | 0.051109 | 0 | 0.1 | 0
E190-180 PLR @loSHR | -2588 | -2587 | -2587.2 | -2561.5475 | -2587.1889 | -2587.2 | -2587.1524 | -2587.7557 | -2587.2 | -2586.3 | 0
E190-140 lat @loPLR | 370 | 370 | 369.6 | 366.354 | 369.6039 | 369.6 | 369.6468 | 369.7156 | 369.6 | 369.8 | 0
E195-190 ODB @loPLloSH | 0 | 0 | 0 | 0.29308 | 0.018237 | 0 | -0.041346 | 0.013833 | 0 | -0.2 | 0
E195-185 PLR @loSHR | -2589 | -2587 | -2587.2 | -2563.306 | -2587.1772 | -2587.2 | -2587.214 | -2587.793 | -2587.2 | -2586.6 | 0
E195-130 lat @loPLR | 370 | 370 | 369.6 | 366.6471 | 369.6221 | 369.6 | 369.6055 | 369.7294 | 369.6 | 369.6 | 0
E200-100 ARI v dry | 1222 | 1221 | 1221 | 1219.2263 | 1220.9837 | 1221.024 | 1221.024 | 1221.1063 | 1221 | 1221 | 0
results5-3.xls q:db491..dq580; 10/15/02