## A
E300RESULTS.XLS | [5 empty] | INSTRUCTIONS
Output spreadsheet for HVAC BESTEST | [5 empty] | Import data so that Cell A1 of E300OUT2.XLS is in A1 of Sheet "YD" (your data)
SEE CELL G1 FOR INSTRUCTIONS | [5 empty] | Check that the first value (Total consumption kWh for E300) lands in YD!B62.
Data should land in "YD" cells as tabulated below. Your data will then appear in column H of Sheet A
DO NOT INSERT ROWS ON THIS SHEET! | [5 empty] | and in rightmost column of each table on sheets Q, R, S, T, Qdata, Rdata, Sdata, and Tdata.
Gives locations in participant spreadsheets (E300OUT2.xls) | [5 empty] | Chart update of "your data" is not automated.
See E300RESULTS.DOC for spreadsheet navigation.
Address guide starts at row 56
Raw data presentation starts around row 137
Mean Data starts at row 137
June 28 hourly data starts at row 483
E500,E530 avg daily starts at row 826
Hourly Maxima consumption and loads start around row 1044
Deltas start at 1450
SHEET GUIDE:
A: Unformatted data compilation, all programs
B: TRNSYS results
C: DOE-2.2 results
D: DOE-2.1E ESTSC results
E: EnergyPlus results
F: CODYRUN results
G: HOT3000/ESP-r results
YD: Your data
I,J: Extra results data sheets
Q: Absolute sum, mean results, formatted for printout
R: Absolute Max, Min Results, formatted for printout
S: Hourly results, formatted for printout
T: Sensitivity results, formatted for printout
Qdata: Absolute sum, mean results, formatted for chart source data
Rdata: Absolute Max, Min Results, formatted for chart source data
Sdata: Hourly results, formatted for chart source data
Tdata: Sensitivity results, formatted for chart source data
Sheets after "Tdata" are Charts
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [15 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio |  | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | B62 | C62 | D62 | E62 | F62 | G62 | H62 | I62 | J62 | K62 | L62 | M62 | N62 |  | E300 | Q62 | R62 | S62 | T62 | U62 | V62 | W62 | X62 | Y62 | Z62 | AA62 | AB62 | AC62 | AD62 | AE62 | AF62 | AG62 | AH62
E310 | B63 | C63 | D63 | E63 | F63 | G63 | H63 | I63 | J63 | K63 | L63 |  |  |  | E310 | Q63 | R63 | S63 | T63 | U63 | V63 | W63 | X63 | Y63 | Z63 | AA63 | AB63
E320 | B64 | C64 | D64 | E64 | F64 | G64 | H64 | I64 | J64 | K64 | L64 |  |  |  | E320 | Q64 | R64 | S64 | T64 | U64 | V64 | W64 | X64 | Y64 | Z64 | AA64 | AB64
E330 | B65 | C65 | D65 | E65 | F65 | G65 | H65 | I65 | J65 | K65 | L65 |  |  |  | E330 | Q65 | R65 | S65 | T65 | U65 | V65 | W65 | X65 | Y65 | Z65 | AA65 | AB65
E340 | B66 | C66 | D66 | E66 | F66 | G66 | H66 | I66 | J66 | K66 | L66 |  |  |  | E340 | Q66 | R66 | S66 | T66 | U66 | V66 | W66 | X66 | Y66 | Z66 | AA66 | AB66
E350 | B67 | C67 | D67 | E67 | F67 | G67 | H67 | I67 | J67 | K67 | L67 |  |  |  | E350 | Q67 | R67 | S67 | T67 | U67 | V67 | W67 | X67 | Y67 | Z67 | AA67 | AB67
E360 | B68 | C68 | D68 | E68 | F68 | G68 | H68 | I68 | J68 | K68 | L68 |  |  |  | E360 | Q68 | R68 | S68 | T68 | U68 | V68 | W68 | X68 | Y68 | Z68 | AA68 | AB68
E400 | B69 | C69 | D69 | E69 | F69 | G69 | H69 | I69 | J69 | K69 | L69 |  |  |  | E400 | Q69 | R69 | S69 | T69 | U69 | V69 | W69 | X69 | Y69 | Z69 | AA69 | AB69
E410 | B70 | C70 | D70 | E70 | F70 | G70 | H70 | I70 | J70 | K70 | L70 |  |  |  | E410 | Q70 | R70 | S70 | T70 | U70 | V70 | W70 | X70 | Y70 | Z70 | AA70 | AB70
E420 | B71 | C71 | D71 | E71 | F71 | G71 | H71 | I71 | J71 | K71 | L71 |  |  |  | E420 | Q71 | R71 | S71 | T71 | U71 | V71 | W71 | X71 | Y71 | Z71 | AA71 | AB71
E430 | B72 | C72 | D72 | E72 | F72 | G72 | H72 | I72 | J72 | K72 | L72 |  |  |  | E430 | Q72 | R72 | S72 | T72 | U72 | V72 | W72 | X72 | Y72 | Z72 | AA72 | AB72
E440 | B73 | C73 | D73 | E73 | F73 | G73 | H73 | I73 | J73 | K73 | L73 |  |  |  | E440 | Q73 | R73 | S73 | T73 | U73 | V73 | W73 | X73 | Y73 | Z73 | AA73 | AB73
E500 | B74 | C74 | D74 | E74 | F74 | G74 | H74 | I74 | J74 | K74 | L74 |  |  |  | E500 | Q74 | R74 | S74 | T74 | U74 | V74 | W74 | X74 | Y74 | Z74 | AA74 | AB74
E500 May-Sep | B75 | C75 | D75 | E75 | F75 | G75 | H75 | I75 | J75 | K75 | L75 |  |  |  | E510 | Q75 | R75 | S75 | T75 | U75 | V75 | W75 | X75 | Y75 | Z75 | AA75 | AB75
E510 May-Sep | B76 | C76 | D76 | E76 | F76 | G76 | H76 | I76 | J76 | K76 | L76 |  |  |  | E520 | Q76 | R76 | S76 | T76 | U76 | V76 | W76 | X76 | Y76 | Z76 | AA76 | AB76
E520 | B77 | C77 | D77 | E77 | F77 | G77 | H77 | I77 | J77 | K77 | L77 |  |  |  | E522 | Q77 | R77 | S77 | T77 | U77 | V77 | W77 | X77 | Y77 | Z77 | AA77 | AB77
E522 | B78 | C78 | D78 | E78 | F78 | G78 | H78 | I78 | J78 | K78 | L78 |  |  |  | E525 | Q78 | R78 | S78 | T78 | U78 | V78 | W78 | X78 | Y78 | Z78 | AA78 | AB78
E525 | B79 | C79 | D79 | E79 | F79 | G79 | H79 | I79 | J79 | K79 | L79 |  |  |  | E530 | Q79 | R79 | S79 | T79 | U79 | V79 | W79 | X79 | Y79 | Z79 | AA79 | AB79
E530 | B80 | C80 | D80 | E80 | F80 | G80 | H80 | I80 | J80 | K80 | L80 |  |  |  | E540 | Q80 | R80 | S80 | T80 | U80 | V80 | W80 | X80 | Y80 | Z80 | AA80 | AB80
E540 | B81 | C81 | D81 | E81 | F81 | G81 | H81 | I81 | J81 | K81 | L81 |  |  |  | E545 | Q81 | R81 | S81 | T81 | U81 | V81 | W81 | X81 | Y81 | Z81 | AA81 | AB81
E545 | B82 | C82 | D82 | E82 | F82 | G82 | H82 | I82 | J82 | K82 | L82
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [11 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | B89 | C89 | D89 | E89 | F89 | G89 | H89 | I89 | J89 | K89 | L89 |  |  |  | E300 | Q89 | R89 | S89 | T89 | U89 | V89 | W89 | X89 | Y89 | Z89 | AA89 | AB89 | AC89 | AD89 | AE89 | AF89 | AG89 | AH89 | AI89 | AJ89 | AK89 | AL89 | AM89 | AN89
2 | B90 | C90 | D90 | E90 | F90 | G90 | H90 | I90 | J90 | K90 | L90 |  |  |  | E310 | Q90 | R90 | S90 | T90 | U90 | V90 | W90 | X90 | Y90 | Z90 | AA90 | AB90 | AC90 | AD90 | AE90 | AF90 | AG90 | AH90 | AI90 | AJ90 | AK90 | AL90 | AM90 | AN90
3 | B91 | C91 | D91 | E91 | F91 | G91 | H91 | I91 | J91 | K91 | L91 |  |  |  | E320 | Q91 | R91 | S91 | T91 | U91 | V91 | W91 | X91 | Y91 | Z91 | AA91 | AB91 | AC91 | AD91 | AE91 | AF91 | AG91 | AH91 | AI91 | AJ91 | AK91 | AL91 | AM91 | AN91
4 | B92 | C92 | D92 | E92 | F92 | G92 | H92 | I92 | J92 | K92 | L92 |  |  |  | E330 | Q92 | R92 | S92 | T92 | U92 | V92 | W92 | X92 | Y92 | Z92 | AA92 | AB92 | AC92 | AD92 | AE92 | AF92 | AG92 | AH92 | AI92 | AJ92 | AK92 | AL92 | AM92 | AN92
5 | B93 | C93 | D93 | E93 | F93 | G93 | H93 | I93 | J93 | K93 | L93 |  |  |  | E340 | Q93 | R93 | S93 | T93 | U93 | V93 | W93 | X93 | Y93 | Z93 | AA93 | AB93 | AC93 | AD93 | AE93 | AF93 | AG93 | AH93 | AI93 | AJ93 | AK93 | AL93 | AM93 | AN93
6 | B94 | C94 | D94 | E94 | F94 | G94 | H94 | I94 | J94 | K94 | L94 |  |  |  | E350 | Q94 | R94 | S94 | T94 | U94 | V94 | W94 | X94 | Y94 | Z94 | AA94 | AB94 | AC94 | AD94 | AE94 | AF94 | AG94 | AH94 | AI94 | AJ94 | AK94 | AL94 | AM94 | AN94
7 | B95 | C95 | D95 | E95 | F95 | G95 | H95 | I95 | J95 | K95 | L95 |  |  |  | E360 | Q95 | R95 | S95 | T95 | U95 | V95 | W95 | X95 | Y95 | Z95 | AA95 | AB95 | AC95 | AD95 | AE95 | AF95 | AG95 | AH95 | AI95 | AJ95 | AK95 | AL95 | AM95 | AN95
8 | B96 | C96 | D96 | E96 | F96 | G96 | H96 | I96 | J96 | K96 | L96 |  |  |  | E400 | Q96 | R96 | S96 | T96 | U96 | V96 | W96 | X96 | Y96 | Z96 | AA96 | AB96 | AC96 | AD96 | AE96 | AF96 | AG96 | AH96 | AI96 | AJ96 | AK96 | AL96 | AM96 | AN96
9 | B97 | C97 | D97 | E97 | F97 | G97 | H97 | I97 | J97 | K97 | L97 |  |  |  | E410 | Q97 | R97 | S97 | T97 | U97 | V97 | W97 | X97 | Y97 | Z97 | AA97 | AB97 | AC97 | AD97 | AE97 | AF97 | AG97 | AH97 | AI97 | AJ97 | AK97 | AL97 | AM97 | AN97
10 | B98 | C98 | D98 | E98 | F98 | G98 | H98 | I98 | J98 | K98 | L98 |  |  |  | E420 | Q98 | R98 | S98 | T98 | U98 | V98 | W98 | X98 | Y98 | Z98 | AA98 | AB98 | AC98 | AD98 | AE98 | AF98 | AG98 | AH98 | AI98 | AJ98 | AK98 | AL98 | AM98 | AN98
11 | B99 | C99 | D99 | E99 | F99 | G99 | H99 | I99 | J99 | K99 | L99 |  |  |  | E430 | Q99 | R99 | S99 | T99 | U99 | V99 | W99 | X99 | Y99 | Z99 | AA99 | AB99 | AC99 | AD99 | AE99 | AF99 | AG99 | AH99 | AI99 | AJ99 | AK99 | AL99 | AM99 | AN99
12 | B100 | C100 | D100 | E100 | F100 | G100 | H100 | I100 | J100 | K100 | L100 |  |  |  | E440 | Q100 | R100 | S100 | T100 | U100 | V100 | W100 | X100 | Y100 | Z100 | AA100 | AB100 | AC100 | AD100 | AE100 | AF100 | AG100 | AH100 | AI100 | AJ100 | AK100 | AL100 | AM100 | AN100
13 | B101 | C101 | D101 | E101 | F101 | G101 | H101 | I101 | J101 | K101 | L101 |  |  |  | E500 | Q101 | R101 | S101 | T101 | U101 | V101 | W101 | X101 | Y101 | Z101 | AA101 | AB101 | AC101 | AD101 | AE101 | AF101 | AG101 | AH101 | AI101 | AJ101 | AK101 | AL101 | AM101 | AN101
14 | B102 | C102 | D102 | E102 | F102 | G102 | H102 | I102 | J102 | K102 | L102 |  |  |  | E510 | Q102 | R102 | S102 | T102 | U102 | V102 | W102 | X102 | Y102 | Z102 | AA102 | AB102 | AC102 | AD102 | AE102 | AF102 | AG102 | AH102 | AI102 | AJ102 | AK102 | AL102 | AM102 | AN102
15 | B103 | C103 | D103 | E103 | F103 | G103 | H103 | I103 | J103 | K103 | L103 |  |  |  | E520 | Q103 | R103 | S103 | T103 | U103 | V103 | W103 | X103 | Y103 | Z103 | AA103 | AB103 | AC103 | AD103 | AE103 | AF103 | AG103 | AH103 | AI103 | AJ103 | AK103 | AL103 | AM103 | AN103
16 | B104 | C104 | D104 | E104 | F104 | G104 | H104 | I104 | J104 | K104 | L104 |  |  |  | E522 | Q104 | R104 | S104 | T104 | U104 | V104 | W104 | X104 | Y104 | Z104 | AA104 | AB104 | AC104 | AD104 | AE104 | AF104 | AG104 | AH104 | AI104 | AJ104 | AK104 | AL104 | AM104 | AN104
17 | B105 | C105 | D105 | E105 | F105 | G105 | H105 | I105 | J105 | K105 | L105 |  |  |  | E525 | Q105 | R105 | S105 | T105 | U105 | V105 | W105 | X105 | Y105 | Z105 | AA105 | AB105 | AC105 | AD105 | AE105 | AF105 | AG105 | AH105 | AI105 | AJ105 | AK105 | AL105 | AM105 | AN105
18 | B106 | C106 | D106 | E106 | F106 | G106 | H106 | I106 | J106 | K106 | L106 |  |  |  | E530 | Q106 | R106 | S106 | T106 | U106 | V106 | W106 | X106 | Y106 | Z106 | AA106 | AB106 | AC106 | AD106 | AE106 | AF106 | AG106 | AH106 | AI106 | AJ106 | AK106 | AL106 | AM106 | AN106
19 | B107 | C107 | D107 | E107 | F107 | G107 | H107 | I107 | J107 | K107 | L107 |  |  |  | E540 | Q107 | R107 | S107 | T107 | U107 | V107 | W107 | X107 | Y107 | Z107 | AA107 | AB107 | AC107 | AD107 | AE107 | AF107 | AG107 | AH107 | AI107 | AJ107 | AK107 | AL107 | AM107 | AN107
20 | B108 | C108 | D108 | E108 | F108 | G108 | H108 | I108 | J108 | K108 | L108 |  |  |  | E545 | Q108 | R108 | S108 | T108 | U108 | V108 | W108 | X108 | Y108 | Z108 | AA108 | AB108 | AC108 | AD108 | AE108 | AF108 | AG108 | AH108 | AI108 | AJ108 | AK108 | AL108 | AM108 | AN108
21 | B109 | C109 | D109 | E109 | F109 | G109 | H109 | I109 | J109 | K109 | L109
22 | B110 | C110 | D110 | E110 | F110 | G110 | H110 | I110 | J110 | K110 | L110
23 | B111 | C111 | D111 | E111 | F111 | G111 | H111 | I111 | J111 | K111 | L111
24 | B112 | C112 | D112 | E112 | F112 | G112 | H112 | I112 | J112 | K112 | L112
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B120 | C120 | D120 | E120 | F120 | G120 | H120 | I120 | J120 | K120 | L120
June 25 | B121 | C121 | D121 | E121 | F121 | G121 | H121 | I121 | J121 | K121 | L121
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | B129 | C129 | D129 | E129 | F129 | G129 | H129 | I129 | J129 | K129 | L129
June 25 | B130 | C130 | D130 | E130 | F130 | G130 | H130 | I130 | J130 | K130 | L130
Energy Consumption, Total (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 35633.7773 | 34750 | 34755 | 35023.7298 | 34976.411 | 35070 | 0 | 0 | 0
E310 | 39973.3798 | 39379 | 39384 | 39434.1646 | 39519.569 | 39608 | 0 | 0 | 0
E320 | 40059.657 | 38745 | 38792 | 39375.0348 | 39400.815 | 39457 | 0 | 0 | 0
E330 | 40963.3004 | 39708 | 39438 | 40468.7948 | 40535.137 | 40330 | 0 | 0 | 0
E340 | 40619.2951 | 39358 | 39265 | 40071.4206 | 40065.261 | 39947 | 0 | 0 | 0
E350 | 32236.9795 | 30547 | 30548 | 31376.2065 | 31586.592 | 31742 | 0 | 0 | 0
E360 | 55298.7917 | 54064 | 54016 | 54944.2502 | 54843.258 | 55068 | 0 | 0 | 0
E400 | 32045.1536 | 30846 | 30876 | 31265.6433 | 0 | 31413 | 0 | 0 | 0
E410 | 32078.4319 | 31668 | 31699 | 32010.5061 | 0 | 31503 | 0 | 0 | 0
E420 | 33387.0076 | 32530 | 32910 | 32978.5453 | 0 | 33208 | 0 | 0 | 0
E430 | 32538.0313 | 31932 | 31811 | 32085.518 | 0 | 31818 | 0 | 0 | 0
E440 | 33691.321 | 33032 | 32973 | 33284.8265 | 0 | 33248 | 0 | 0 | 0
E500 | 22337.887 | 22817 | 22822 | 23075.8197 | 22322.953 | 23138 | 0 | 0 | 0
E500 May-Sep | 17390.8511 | 17872 | 17870 | 18030.7145 | 17434.537 | 18051 | 0 | 0 | 0
E510 May-Sep | 34608.7754 | 35971 | 35970 | 35791.0201 | 34848.637 | 35845 | 0 | 0 | 0
E520 | 24986.582 | 25389 | 25390 | 25812.8973 | 25131.07 | 25781 | 0 | 0 | 0
E522 | 23544.1607 | 24293 | 24307 | 24385.5401 | 23619.744 | 24360 | 0 | 0 | 0
E525 | 20320.874 | 20408 | 20421 | 20781.3508 | 20241.713 | 21323 | 0 | 0 | 0
E530 | 17281.271 | 17540 | 17537 | 17993.9617 | 17442.468 | 17875 | 0 | 0 | 0
E540 | 19430.3785 | 19878 | 19874 | 20122.7341 | 19536.572 | 20164 | 0 | 0 | 0
E545 | 15687.0796 | 15802 | 15791 | 16608.6011 | 15791.081 | 16339 | 0 | 0 | 0
Energy Consumption, Compressor (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 22353.5343 | 21569 | 21573 | 24161.6379 | 21770.001 | 21876 | 0 | 0 | 0
E310 | 26339.6254 | 25813 | 25817 | 28572.0727 | 25936.821 | 26053 | 0 | 0 | 0
E320 | 26433.1374 | 25250 | 25294 | 28512.9429 | 25846.026 | 25912 | 0 | 0 | 0
E330 | 27299.7321 | 26172 | 25925 | 29606.7029 | 26927.733 | 26775 | 0 | 0 | 0
E340 | 26962.9373 | 25829 | 25745 | 29209.3287 | 26472.79 | 26400 | 0 | 0 | 0
E350 | 19316.8404 | 17802 | 17801 | 20514.1146 | 18738.055 | 18891 | 0 | 0 | 0
E360 | 40105.8399 | 38999 | 38955 | 44082.1583 | 39697.162 | 39941 | 0 | 0 | 0
E400 | 19178.9487 | 18106 | 18131 | 20403.5514 | 0 | 18629 | 0 | 0 | 0
E410 | 19204.4944 | 18823 | 18850 | 21148.4142 | 0 | 18685 | 0 | 0 | 0
E420 | 20358.5854 | 19596 | 19934 | 22116.4533 | 0 | 20214 | 0 | 0 | 0
E430 | 19598.6211 | 19059 | 18951 | 21223.4261 | 0 | 18966 | 0 | 0 | 0
E440 | 20629.1333 | 20042 | 19989 | 22422.7346 | 0 | 20249 | 0 | 0 | 0
E500 | 17854.2956 | 18473 | 18478 | 20445.2767 | 17857.852 | 18522 | 0 | 0 | 0
E500 May-Sep | 13942.1479 | 14508 | 14506 | 15999.9491 | 13988.512 | 14491 | 0 | 0 | 0
E510 May-Sep | 27747.879 | 28811 | 28810 | 31725.1666 | 27901.957 | 28721 | 0 | 0 | 0
E520 | 19521.2767 | 20121 | 20126 | 22672.1954 | 19654.972 | 20185 | 0 | 0 | 0
E522 | 18620.3108 | 19407 | 19418 | 21506.6752 | 18689.799 | 19281 | 0 | 0 | 0
E525 | 16557.8748 | 16880 | 16893 | 18589.1036 | 16506.802 | 17443 | 0 | 0 | 0
E530 | 13656.9951 | 14127 | 14124 | 15872.2483 | 13855.928 | 14172 | 0 | 0 | 0
E540 | 15020.7433 | 15680 | 15677 | 17628.9433 | 15163.82 | 15664 | 0 | 0 | 0
E545 | 12621.8685 | 12967 | 12957 | 14743.4176 | 12750.623 | 13215 | 0 | 0 | 0
Energy Consumption, Condenser Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 2400.3229 | 2301 | 2302 | Note 1 | 2326.49 | 2323 | 0 | 0 | 0
E310 | 2753.8345 | 2686 | 2687 | Note 1 | 2702.828 | 2691 | 0 | 0 | 0
E320 | 2746.5996 | 2615 | 2618 | Note 1 | 2674.869 | 2681 | 0 | 0 | 0
E330 | 2783.6483 | 2656 | 2633 | Note 1 | 2727.484 | 2693 | 0 | 0 | 0
E340 | 2776.4378 | 2649 | 2640 | Note 1 | 2712.551 | 2684 | 0 | 0 | 0
E350 | 2040.2191 | 1865 | 1867 | Note 1 | 1968.617 | 1970 | 0 | 0 | 0
E360 | 4313.0318 | 4185 | 4181 | Note 1 | 4266.176 | 4272 | 0 | 0 | 0
E400 | 1986.2848 | 1860 | 1865 | Note 1 | 0 | 1902 | 0 | 0 | 0
E410 | 1994.0175 | 1965 | 1969 | Note 1 | 0 | 1936 | 0 | 0 | 0
E420 | 2148.5022 | 2054 | 2096 | Note 1 | 0 | 2115 | 0 | 0 | 0
E430 | 2059.4903 | 1993 | 1980 | Note 1 | 0 | 1970 | 0 | 0 | 0
E440 | 2182.2678 | 2110 | 2104 | Note 1 | 0 | 2120 | 0 | 0 | 0
E500 | 1919.7698 | 1975 | 1975 | Note 1 | 1911.869 | 1976 | 0 | 0 | 0
E500 May-Sep | 1476.6547 | 1527 | 1527 | Note 1 | 1475.528 | 1524 | 0 | 0 | 0
E510 May-Sep | 2937.6766 | 3061 | 3061 | Note 1 | 2974.4 | 3050 | 0 | 0 | 0
E520 | 2340.1169 | 2394 | 2393 | Note 1 | 2344.827 | 2396 | 0 | 0 | 0
E522 | 2108.2783 | 2182 | 2182 | Note 1 | 2110.833 | 2174 | 0 | 0 | 0
E525 | 1611.2289 | 1642 | 1643 | Note 1 | 1599.203 | 1663 | 0 | 0 | 0
E530 | 1551.8309 | 1580 | 1580 | Note 1 | 1535.684 | 1585 | 0 | 0 | 0
E540 | 1888.1035 | 1940 | 1939 | Note 1 | 1872.336 | 1926 | 0 | 0 | 0
E545 | 1312.4522 | 1334 | 1333 | Note 1 | 1301.791 | 1337 | 0 | 0 | 0
Energy Consumption, ID Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E310 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E320 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E330 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E340 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E350 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E360 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0 | 0 | 0
E400 | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0 | 0 | 0
E410 | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0 | 0 | 0
E420 | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0 | 0 | 0
E430 | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0 | 0 | 0
E440 | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0 | 0 | 0
E500 | 2563.8216 | 2369 | 2369 | 2630.543 | 2553.232 | 2639 | 0 | 0 | 0
E500 May-Sep | 1972.0485 | 1837 | 1837 | 2030.7654 | 1970.497 | 2035 | 0 | 0 | 0
E510 May-Sep | 3923.2198 | 4099 | 4099 | 4065.8535 | 3972.28 | 4073 | 0 | 0 | 0
E520 | 3125.1884 | 2874 | 2871 | 3140.7019 | 3131.271 | 3200 | 0 | 0 | 0
E522 | 2815.5716 | 2704 | 2707 | 2878.8649 | 2819.112 | 2904 | 0 | 0 | 0
E525 | 2151.7702 | 1886 | 1885 | 2192.2472 | 2135.708 | 2221 | 0 | 0 | 0
E530 | 2072.4451 | 1833 | 1833 | 2121.7134 | 2050.856 | 2117 | 0 | 0 | 0
E540 | 2521.5317 | 2258 | 2258 | 2493.7908 | 2500.416 | 2573 | 0 | 0 | 0
E545 | 1752.7588 | 1501 | 1501 | 1865.1834 | 1738.667 | 1786 | 0 | 0 | 0
Coil Load, total (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 80426.8675 | 77283.4356 | 77291.9355 | 78329.9975 | 77744.589 | 78257 | 0 | 0 | 0
E310 | 99342.1316 | 97394.7852 | 97412.0781 | 97347.6609 | 97295.866 | 97261 | 0 | 0 | 0
E320 | 99791.678 | 96356.3319 | 96493.2096 | 97434.8383 | 97141.307 | 96957 | 0 | 0 | 0
E330 | 105012.8715 | 100729.9701 | 100993.467 | 103810.929 | 103712.915 | 102008 | 0 | 0 | 0
E340 | 102727.9789 | 99027.6453 | 99223.143 | 101133.5278 | 100676.21 | 99753 | 0 | 0 | 0
E350 | 69387.9976 | 63736.3536 | 63634.6479 | 66594.5472 | 66860.163 | 67389 | 0 | 0 | 0
E360 | 162974.0626 | 159807.2061 | 159853.809 | 162207.6865 | 161200.179 | 162168 | 0 | 0 | 0
E400 | 68792.8221 | 64917.5466 | 65025.1143 | 66490.4992 | 0 | 66898 | 0 | 0 | 0
E410 | 68672.8538 | 66779.6109 | 66843.5067 | 68071.4219 | 0 | 66175 | 0 | 0 | 0
E420 | 72609.3074 | 69610.9569 | 70882.1316 | 71248.0904 | 0 | 71803 | 0 | 0 | 0
E430 | 69756.312 | 67640.7387 | 67219.2609 | 68287.7544 | 0 | 67200 | 0 | 0 | 0
E440 | 73711.3635 | 71380.1085 | 71181.0936 | 72362.1012 | 0 | 72029 | 0 | 0 | 0
E500 | 63357.1063 | 65995.8615 | 65992.3443 | 65589.3563 | 63105.366 | 65614 | 0 | 0 | 0
E500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50355.6741 | 48439.57 | 50357 | 0 | 0 | 0
E510 May-Sep | 108974.3099 | 114017.9517 | 114015.3138 | 112794.8773 | 108979.013 | 112781 | 0 | 0 | 0
E520 | 63421.5444 | 66571.2168 | 66565.3548 | 66213.2769 | 63212.102 | 66146 | 0 | 0 | 0
E522 | 63389.2228 | 66373.0812 | 66371.9088 | 65893.8706 | 63157.03 | 65900 | 0 | 0 | 0
E525 | 63292.9454 | 65399.1099 | 65395.0065 | 65028.3172 | 63001.558 | 65155 | 0 | 0 | 0
E530 | 45045.848 | 46634.2617 | 46630.7445 | 46988.5521 | 44875.414 | 47002 | 0 | 0 | 0
E540 | 45112.827 | 47129.8938 | 47126.0835 | 47482.0855 | 44979.842 | 47462 | 0 | 0 | 0
E545 | 44981.3517 | 46239.7491 | 46235.9388 | 46635.6951 | 44775.11 | 46668 | 0 | 0 | 0
Coil Load, Sensible (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 56661.7484 | 55796.8608 | 55804.7745 | 55166.0635 | 55209.465 | 55191 | 0 | 0 | 0
E310 | 56256.3775 | 56300.9928 | 56312.7168 | 55065.6279 | 55185.072 | 55083 | 0 | 0 | 0
E320 | 62859.2053 | 62697.021 | 62746.848 | 61751.6548 | 62008.804 | 62734 | 0 | 0 | 0
E330 | 63083.3765 | 63311.0655 | 63327.7722 | 63074.0758 | 62649.459 | 61822 | 0 | 0 | 0
E340 | 63032.6061 | 63053.4306 | 63110.5851 | 62391.3804 | 62380.56 | 61406 | 0 | 0 | 0
E350 | 50370.8304 | 47684.439 | 47676.5253 | 48335.5891 | 48588.802 | 48768 | 0 | 0 | 0
E360 | 134976.8351 | 134919.792 | 134939.7228 | 134711.1169 | 134205.707 | 134697 | 0 | 0 | 0
E400 | 41952.3595 | 41419.1334 | 41437.0125 | 40599.2192 | 0 | 41181 | 0 | 0 | 0
E410 | 45676.6456 | 47658.6462 | 47659.8186 | 47103.2086 | 0 | 45585 | 0 | 0 | 0
E420 | 50389.8247 | 49666.0881 | 50612.2149 | 49444.6391 | 0 | 49984 | 0 | 0 | 0
E430 | 47863.3462 | 47731.335 | 47454.0624 | 46911.71 | 0 | 46143 | 0 | 0 | 0
E440 | 50876.0725 | 50592.5772 | 50492.0439 | 50001.0328 | 0 | 49785 | 0 | 0 | 0
E500 | 45043.8 | 47649.8532 | 47646.0429 | 47357.4403 | 44874.225 | 47530 | 0 | 0 | 0
E500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36365.0866 | 34448.151 | 36480 | 0 | 0 | 0
E510 May-Sep | 77489.4321 | 82305.7041 | 82303.0662 | 81315.4422 | 77498.985 | 81563 | 0 | 0 | 0
E520 | 45109.6141 | 48101.5203 | 48095.6583 | 47983.7484 | 44976.724 | 48059 | 0 | 0 | 0
E522 | 45076.0312 | 47962.2978 | 47961.4185 | 47663.109 | 44924.113 | 47795 | 0 | 0 | 0
E525 | 44979.0103 | 47217.5307 | 47213.4273 | 46796.3098 | 44775.105 | 47110 | 0 | 0 | 0
E530 | 45045.848 | 46573.59 | 46570.0728 | 46988.3103 | 44874.225 | 47002 | 0 | 0 | 0
E540 | 45111.8473 | 47022.9123 | 47019.102 | 47473.2183 | 44976.747 | 47460 | 0 | 0 | 0
E545 | 44981.3517 | 46214.2494 | 46210.4391 | 46635.6951 | 44775.105 | 46668 | 0 | 0 | 0
Coil Load, Latent (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 23765.119 | 21486.5748 | 21487.161 | 23163.9341 | 22535.143 | 23067 | 0 | 0 | 0
E310 | 43085.7541 | 41093.7924 | 41099.3613 | 42282.0331 | 42110.836 | 42178 | 0 | 0 | 0
E320 | 36932.4726 | 33659.3109 | 33746.3616 | 35683.1835 | 35132.592 | 34224 | 0 | 0 | 0
E330 | 41929.495 | 37418.9046 | 37665.6948 | 40736.8532 | 41063.373 | 40186 | 0 | 0 | 0
E340 | 39695.3729 | 35974.2147 | 36112.5579 | 38742.1474 | 38295.624 | 38346 | 0 | 0 | 0
E350 | 19017.1672 | 16051.9146 | 15958.1226 | 18258.9581 | 18271.394 | 18621 | 0 | 0 | 0
E360 | 27997.2274 | 24887.4141 | 24914.0862 | 27496.5697 | 26994.482 | 27470 | 0 | 0 | 0
E400 | 26840.4626 | 23498.4132 | 23588.1018 | 25891.28 | 0 | 25717 | 0 | 0 | 0
E410 | 22996.2083 | 19120.9647 | 19183.6881 | 20968.2133 | 0 | 20590 | 0 | 0 | 0
E420 | 22219.4827 | 19944.8688 | 20269.9167 | 21803.4513 | 0 | 21855 | 0 | 0 | 0
E430 | 21892.9657 | 19909.4037 | 19765.1985 | 21376.0444 | 0 | 21057 | 0 | 0 | 0
E440 | 22835.291 | 20787.5313 | 20689.0497 | 22361.0683 | 0 | 22244 | 0 | 0 | 0
E500 | 18313.3062 | 18346.0083 | 18346.3014 | 18231.916 | 18231.141 | 18084 | 0 | 0 | 0
E500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13990.5875 | 13991.418 | 13877 | 0 | 0 | 0
E510 May-Sep | 31484.8778 | 31712.2476 | 31712.2476 | 31479.435 | 31479.856 | 31217 | 0 | 0 | 0
E520 | 18311.9303 | 18469.6965 | 18469.6965 | 18229.5285 | 18235.133 | 18087 | 0 | 0 | 0
E522 | 18313.1916 | 18410.7834 | 18410.4903 | 18230.7617 | 18233.151 | 18104 | 0 | 0 | 0
E525 | 18313.9351 | 18181.5792 | 18181.5792 | 18232.0073 | 18226.509 | 18045 | 0 | 0 | 0
E530 | 5.6053e-13 | 60.6717 | 60.6717 | 0.24183 | 1.186 | 0 | 0 | 0 | 0
E540 | 0.97976 | 106.9815 | 106.9815 | 8.8672 | 3.09 | 2 | 0 | 0 | 0
E545 | -3.3573e-14 | 25.4997 | 25.4997 | 3.5428e-12 | 0.004 | 0 | 0 | 0 | 0
Mean COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 3.2491 | 3.2377 | 3.2374 | 3.2419 | 3.2264 | 3.23 | 0 | 0 | 0
E310 | 3.4146 | 3.4175 | 3.4175 | 3.4071 | 3.3972 | 3.38 | 0 | 0 | 0
E320 | 3.4199 | 3.458 | 3.4571 | 3.4172 | 3.406 | 3.39 | 0 | 0 | 0
E330 | 3.4907 | 3.4942 | 3.5364 | 3.5063 | 3.4973 | 3.46 | 0 | 0 | 0
E340 | 3.4543 | 3.4773 | 3.4956 | 3.4624 | 3.4495 | 3.42 | 0 | 0 | 0
E350 | 3.2489 | 3.2408 | 3.2354 | 3.2463 | 3.2289 | 3.23 | 0 | 0 | 0
E360 | 3.669 | 3.7006 | 3.7058 | 3.6797 | 3.6667 | 3.66 | 0 | 0 | 0
E400 | 3.2503 | 3.2514 | 3.2519 | 3.2588 | 0 | 3.26 | 0 | 0 | 0
E410 | 3.2395 | 3.2124 | 3.2107 | 3.2187 | 0 | 3.21 | 0 | 0 | 0
E420 | 3.2261 | 3.2153 | 3.2175 | 3.2215 | 0 | 3.21 | 0 | 0 | 0
E430 | 3.2208 | 3.213 | 3.2115 | 3.2176 | 0 | 3.21 | 0 | 0 | 0
E440 | 3.2313 | 3.2223 | 3.2219 | 3.2272 | 0 | 3.22 | 0 | 0 | 0
E500 | 3.2041 | 3.2275 | 3.2265 | 3.208 | 3.192 | 3.2 | 0 | 0 | 0
E500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1472 | 3.1324 | 3.14 | 0 | 0 | 0
E510 May-Sep | 3.5513 | 3.5774 | 3.5774 | 3.5554 | 3.5295 | 3.55 | 0 | 0 | 0
E520 | 2.9011 | 2.9567 | 2.956 | 2.9205 | 2.8733 | 2.92 | 0 | 0 | 0
E522 | 3.0581 | 3.0744 | 3.0728 | 3.0639 | 3.0363 | 3.07 | 0 | 0 | 0
E525 | 3.4835 | 3.5309 | 3.528 | 3.4982 | 3.4796 | 3.41 | 0 | 0 | 0
E530 | 2.9618 | 2.969 | 2.9694 | 2.9604 | 2.9156 | 2.98 | 0 | 0 | 0
E540 | 2.668 | 2.6748 | 2.6752 | 2.6934 | 2.6403 | 2.69 | 0 | 0 | 0
E545 | 3.2281 | 3.2333 | 3.2355 | 3.1632 | 3.1863 | 3.2 | 0 | 0 | 0
Mean IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 23.6243 | 24.0556 | 24.0556 | 24.0891 | 24.0816 | 23.99 | 0 | 0 | 0
E310 | 23.7556 | 24.1111 | 24.0556 | 24.0915 | 24.0897 | 24.01 | 0 | 0 | 0
E320 | 23.9005 | 24.3889 | 24.3889 | 24.2322 | 24.3274 | 24.53 | 0 | 0 | 0
E330 | 23.8797 | 24.2778 | 24.2778 | 24.2953 | 24.2955 | 24.18 | 0 | 0 | 0
E340 | 23.8756 | 24.2778 | 24.2778 | 24.3105 | 24.3089 | 24.21 | 0 | 0 | 0
E350 | 25.6595 | 26.1667 | 26.1667 | 26.2368 | 26.2686 | 26.15 | 0 | 0 | 0
E360 | 25.3649 | 25.6111 | 25.5556 | 25.4311 | 25.4809 | 25.37 | 0 | 0 | 0
E400 | 24.1263 | 24.0556 | 24.0556 | 24.0905 | 0 | 23.99 | 0 | 0 | 0
E410 | 24.1221 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0 | 0 | 0
E420 | 23.9262 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0 | 0 | 0
E430 | 23.9916 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0 | 0 | 0
E440 | 23.9118 | 24.0556 | 24.0556 | 24.0891 | 0 | 23.99 | 0 | 0 | 0
E500 | 20.2342 | 20.6667 | 20.5556 | 20.4037 | 21.0978 | 22.86 | 0 | 0 | 0
E500 May-Sep | 24.5723 | 25 | 25 | 24.9827 | 25 | 25 | 0 | 0 | 0
E510 May-Sep | 25.8168 | 25.1111 | 25.1111 | 24.9597 | 25 | 25 | 0 | 0 | 0
E520 | 13.5171 | 13.7778 | 13.7222 | 13.6259 | 14.1421 | 14.89 | 0 | 0 | 0
E522 | 16.9456 | 17.2778 | 17.2222 | 17.0327 | 17.729 | 18.7 | 0 | 0 | 0
E525 | 26.8443 | 27.3889 | 27.2778 | 27.1287 | 27.7709 | 30.69 | 0 | 0 | 0
E530 | 20.0253 | 20.6111 | 20.5556 | 20.5951 | 21.0978 | 22.86 | 0 | 0 | 0
E540 | 13.2893 | 13.7778 | 13.7222 | 13.8017 | 14.1406 | 14.98 | 0 | 0 | 0
E545 | 26.6052 | 27.3333 | 27.2778 | 27.3219 | 27.7166 | 30.69 | 0 | 0 | 0
Mean Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 0.0090691 | 0.0092 | 0.0092 | 0.0091654 | 0.0091748 | 0.0092 | 0 | 0 | 0
E310 | 0.011071 | 0.0113 | 0.0113 | 0.011154 | 0.011175 | 0.0111 | 0 | 0 | 0
E320 | 0.009988 | 0.0101 | 0.0101 | 0.010037 | 0.010049 | 0.0099 | 0 | 0 | 0
E330 | 0.0097409 | 0.0099 | 0.0099 | 0.0098806 | 0.0098116 | 0.0099 | 0 | 0 | 0
E340 | 0.0097914 | 0.0099 | 0.0099 | 0.0099021 | 0.0098683 | 0.0099 | 0 | 0 | 0
E350 | 0.0097059 | 0.01 | 0.01 | 0.0097964 | 0.0097585 | 0.00977 | 0 | 0 | 0
E360 | 0.0084995 | 0.0087 | 0.0087 | 0.0086063 | 0.0085524 | 0.00858 | 0 | 0 | 0
E400 | 0.0098011 | 0.01 | 0.01 | 0.010042 | 0 | 0.01 | 0 | 0 | 0
E410 | 0.0097405 | 0.0095 | 0.0095 | 0.0094823 | 0 | 0.0095 | 0 | 0 | 0
E420 | 0.0092639 | 0.0094 | 0.0094 | 0.0093476 | 0 | 0.0093 | 0 | 0 | 0
E430 | 0.0093103 | 0.0094 | 0.0094 | 0.009387 | 0 | 0.0094 | 0 | 0 | 0
E440 | 0.0091578 | 0.0093 | 0.0093 | 0.0092307 | 0 | 0.0092 | 0 | 0 | 0
E500 | 0.0097753 | 0 | 0 | 0.0091456 | 0.010218 | 0.0107 | 0 | 0 | 0
E500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.010999 | 0.011329 | 0.0109 | 0 | 0 | 0
E510 May-Sep | 0.011395 | 0.0114 | 0.0114 | 0.011008 | 0.011328 | 0.0109 | 0 | 0 | 0
E520 | 0.0066924 | 0 | 0 | 0.0060157 | 0.0070234 | 0.00763 | 0 | 0 | 0
E522 | 0.0081904 | 0 | 0 | 0.0074805 | 0.0085797 | 0.00901 | 0 | 0 | 0
E525 | 0.013713 | 0 | 0 | 0.01338 | 0.01398 | 0.0151 | 0 | 0 | 0
E530 | 0.0062265 | 0 | 0 | 0.0064848 | 0.0057975 | 0.00667 | 0 | 0 | 0
E540 | 0.0044601 | 0 | 0 | 0.0043402 | 0.0038546 | 0.00463 | 0 | 0 | 0
E545 | 0.0062265 | 0 | 0 | 0.0067479 | 0.006749 | 0.00722 | 0 | 0 | 0
Mean Relative Humidity
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E300 | 48.6149 | 48.26 | 48.28 | 47.9447 | 47.8261 | 47.93 | 0 | 0 | 0
E310 | 58.3307 | 58.51 | 58.53 | 57.961 | 57.841 | 57.8 | 0 | 0 | 0
E320 | 52.0053 | 51.21 | 51.25 | 51.4531 | 51.1034 | 49.94 | 0 | 0 | 0
E330 | 50.8445 | 50.58 | 50.65 | 50.6065 | 50.0848 | 50.7 | 0 | 0 | 0
E340 | 51.085 | 50.69 | 50.73 | 50.6474 | 50.2967 | 50.78 | 0 | 0 | 0
E350 | 45.484 | 45.45 | 45.55 | 44.5942 | 44.3162 | 44.56 | 0 | 0 | 0
E360 | 41.0335 | 41.49 | 41.49 | 41.3637 | 40.871 | 41.21 | 0 | 0 | 0
E400 | 50.7709 | 52.21 | 52.25 | 52.2746 | 0 | 52.01 | 0 | 0 | 0
E410 | 50.4971 | 49.65 | 49.63 | 49.5161 | 0 | 49.75 | 0 | 0 | 0
E420 | 48.7794 | 49.14 | 48.97 | 48.8495 | 0 | 48.76 | 0 | 0 | 0
E430 | 48.8219 | 49.17 | 49.3 | 49.0444 | 0 | 49.17 | 0 | 0 | 0
E440 | 48.3298 | 48.46 | 48.57 | 48.2689 | 0 | 48.23 | 0 | 0 | 0
E500 | 66.5261 | 0 | 0 | 57.9362 | 65.9419 | 63.73 | 0 | 0 | 0
E500 May-Sep | 57.0476 | 57.47 | 57.47 | 55.6602 | 57.0722 | 55.13 | 0 | 0 | 0
E510 May-Sep | 54.7001 | 57.36 | 57.36 | 55.778 | 57.0615 | 55.24 | 0 | 0 | 0
E520 | 69.8745 | 0 | 0 | 60.9282 | 70.2268 | 72.17 | 0 | 0 | 0
E522 | 68.6774 | 0 | 0 | 59.7074 | 68.2314 | 68.11 | 0 | 0 | 0
E525 | 61.4674 | 0 | 0 | 53.7167 | 60.1387 | 57.37 | 0 | 0 | 0
E530 | 46.7299 | 0 | 0 | 47.5315 | 41.4516 | 39.6 | 0 | 0 | 0
E540 | 48.521 | 0 | 0 | 46.1769 | 40.0509 | 43.82 | 0 | 0 | 0
E545 | 36.6249 | 0 | 0 | 38.63 | 36.8747 | 29.2 | 0 | 0 | 0
Weather Data Comparison, Annual Means E300 only
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
ODB | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91 | 0 | 0 | 0
OHR | 0.011643 | 0.0116 | 0.0116 | 0.011608 | 0.011649 | 0.0116 | 0 | 0 | 0
JUNE 28 HOURLY OUTPUT
Energy Consumption, Compressor (kWh,e)
Hour | TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 2055.7697 | 1897 | 1894 | 2153.3475 | 1886 | 1942.81 | 0 | 0 | 0
2 | 2053.6706 | 1941 | 1941 | 2166.9933 | 1964 | 1950.53 | 0 | 0 | 0
3 | 2054.4923 | 1897 | 1894 | 2147.8736 | 1881 | 1902.33 | 0 | 0 | 0
4 | 1830.0824 | 1891 | 1890 | 2109.7575 | 1878 | 1845.43 | 0 | 0 | 0
5 | 2029.3426 | 1697 | 1694 | 2031.5836 | 1756 | 1914.46 | 0 | 0 | 0
6 | 1839.4317 | 2126 | 2133 | 2181.6446 | 2075 | 2506.57 | 0 | 0 | 0
7 | 2667.2444 | 3198 | 3223 | 2926.8472 | 3035 | 3170.95 | 0 | 0 | 0
8 | 3552.7185 | 3135 | 3145 | 3571.6614 | 3303 | 3433.96 | 0 | 0 | 0
9 | 4364.7758 | 4528 | 4526 | 4771.5975 | 4483 | 4489.15 | 0 | 0 | 0
10 | 4441.0633 | 4651 | 4655 | 5029.2702 | 4594 | 4853.28 | 0 | 0 | 0
11 | 4999.595 | 5434 | 5456 | 5485.3257 | 5238 | 5164.22 | 0 | 0 | 0
12 | 5316.7711 | 5019 | 5015 | 5708.5515 | 5066 | 5004.96 | 0 | 0 | 0
13 | 6188.5477 | 6040 | 6036 | 7233.0374 | 6442 | 6454.59 | 0 | 0 | 0
14 | 6210.9293 | 6420 | 6429 | 7085.957 | 6523 | 6503.4 | 0 | 0 | 0
15 | 7922.4534 | 7671 | 7683 | 8689.9561 | 8000 | 8040.55 | 0 | 0 | 0
16 | 7964.823 | 8190 | 8222 | 8842.8175 | 8169 | 8133.59 | 0 | 0 | 0
17 | 5420.7775 | 5715 | 5696 | 5791.0239 | 5306 | 5211.79 | 0 | 0 | 0
18 | 5409.9868 | 5536 | 5531 | 5952.6309 | 5381 | 5122.29 | 0 | 0 | 0
19 | 5260.0345 | 4711 | 4689 | 5617.7336 | 4791 | 4831.72 | 0 | 0 | 0
20 | 4880.3429 | 4859 | 4855 | 5315.9924 | 4809 | 4874.85 | 0 | 0 | 0
21 | 3938.7143 | 3913 | 3918 | 4369.5515 | 3939 | 3935.62 | 0 | 0 | 0
22 | 3923.9563 | 3825 | 3823 | 4323.8097 | 3852 | 3844.33 | 0 | 0 | 0
23 | 4122.5716 | 3750 | 3748 | 4215.998 | 3752 | 3807.46 | 0 | 0 | 0
24 | 3877.3845 | 3880 | 3880 | 4194.2432 | 3794 | 3664.17 | 0 | 0 | 0
Energy Consumption, Condenser Fan (kWh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 256.5326 | 237 | 237 | Note 1 | 237 | 240.938 | 0 | 0 | 0
2 | 256.5271 | 240 | 241 | Note 1 | 244 | 241.104 | 0 | 0 | 0
3 | 256.5356 | 237 | 237 | Note 1 | 236 | 236.85 | 0 | 0 | 0
4 | 229.5857 | 237 | 236 | Note 1 | 236 | 231.118 | 0 | 0 | 0
5 | 256.394 | 215 | 215 | Note 1 | 224 | 238.687 | 0 | 0 | 0
6 | 229.5597 | 259 | 259 | Note 1 | 253 | 292.588 | 0 | 0 | 0
7 | 308.5446 | 352 | 353 | Note 1 | 334 | 342.969 | 0 | 0 | 0
8 | 384.0455 | 332 | 335 | Note 1 | 352 | 360.598 | 0 | 0 | 0
9 | 458.1014 | 469 | 467 | Note 1 | 463 | 460.788 | 0 | 0 | 0
10 | 457.9932 | 479 | 478 | Note 1 | 472 | 489.455 | 0 | 0 | 0
11 | 506.3045 | 537 | 536 | Note 1 | 516 | 508.218 | 0 | 0 | 0
12 | 529.3648 | 498 | 498 | Note 1 | 504 | 496.504 | 0 | 0 | 0
13 | 616.6094 | 597 | 600 | Note 1 | 642 | 639.274 | 0 | 0 | 0
14 | 616.1242 | 633 | 635 | Note 1 | 645 | 639.953 | 0 | 0 | 0
15 | 781.0016 | 751 | 754 | Note 1 | 785 | 784.905 | 0 | 0 | 0
16 | 781.0124 | 800 | 803 | Note 1 | 799 | 793.61 | 0 | 0 | 0
17 | 529.4985 | 561 | 556 | Note 1 | 519 | 509.581 | 0 | 0 | 0
18 | 529.3784 | 544 | 541 | Note 1 | 528 | 506.956 | 0 | 0 | 0
19 | 529.2289 | 481 | 479 | Note 1 | 492 | 492.97 | 0 | 0 | 0
20 | 506.2207 | 504 | 503 | Note 1 | 498 | 501.239 | 0 | 0 | 0
21 | 409.0843 | 405 | 406 | Note 1 | 408 | 405.543 | 0 | 0 | 0
22 | 409.5326 | 399 | 399 | Note 1 | 402 | 398.939 | 0 | 0 | 0
23 | 433.8551 | 395 | 394 | Note 1 | 395 | 397.275 | 0 | 0 | 0
24 | 409.5808 | 407 | 407 | Note 1 | 399 | 385.64 | 0 | 0 | 0
Coil Load, Total (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 8131.73 | 7552.3077 | 7544.9802 | 7602.8745 | 7472 | 7667.56 | 0 | 0 | 0
2 | 8115.8 | 7630.2723 | 7627.0482 | 7628.0999 | 7707 | 7674.46 | 0 | 0 | 0
3 | 8127.89 | 7550.256 | 7546.1526 | 7579.4624 | 7445 | 7527.94 | 0 | 0 | 0
4 | 7224.15 | 7533.8424 | 7528.2735 | 7463.8071 | 7432 | 7317.22 | 0 | 0 | 0
5 | 8104.85 | 6797.8683 | 6753.024 | 7218.877 | 7000 | 7514.35 | 0 | 0 | 0
6 | 7130.87 | 8136.1629 | 8185.1106 | 7563.2201 | 7915 | 9222.93 | 0 | 0 | 0
7 | 9711.38 | 11075.9559 | 11232.7644 | 9393.041 | 10450 | 10769.5 | 0 | 0 | 0
8 | 12121.31 | 10290.741 | 10271.6895 | 10820.4962 | 10813 | 11186.4 | 0 | 0 | 0
9 | 14555.62 | 14785.7226 | 14844.0495 | 14280.6923 | 14631 | 14744.4 | 0 | 0 | 0
10 | 14639.38 | 15339.9747 | 15392.7327 | 15005.1999 | 15099 | 15882.1 | 0 | 0 | 0
11 | 16374.09 | 17455.2774 | 17605.0515 | 16127.9094 | 16722 | 16614.5 | 0 | 0 | 0
12 | 17248.4 | 16215.1713 | 16187.6199 | 16742.4591 | 16258 | 16029.6 | 0 | 0 | 0
13 | 20498.21 | 19722.9921 | 19620.9933 | 21873.9592 | 21090 | 21179.7 | 0 | 0 | 0
14 | 20234.06 | 20808.3414 | 20819.1861 | 20933.4385 | 21067 | 21055.4 | 0 | 0 | 0
15 | 26687.28 | 25387.1496 | 25392.7185 | 26432.9109 | 26636 | 27069.8 | 0 | 0 | 0
16 | 26722.68 | 27581.0031 | 27721.1049 | 26943.3568 | 27416 | 27623.3 | 0 | 0 | 0
17 | 17231.33 | 18204.7341 | 18244.5957 | 16525.7603 | 16702 | 16551 | 0 | 0 | 0
18 | 17505.88 | 17933.3235 | 17977.8747 | 17405.5618 | 17312 | 16829.6 | 0 | 0 | 0
19 | 17661.69 | 16012.053 | 15914.4507 | 17082.2323 | 16232 | 16635.3 | 0 | 0 | 0
20 | 16989.81 | 17082.1611 | 17120.2641 | 16742.9941 | 16867 | 17131.1 | 0 | 0 | 0
21 | 13539.94 | 13435.4109 | 13445.0832 | 13611.4239 | 13484 | 13524.8 | 0 | 0 | 0
22 | 13564.54 | 13280.361 | 13285.0506 | 13561.3024 | 13322 | 13355.8 | 0 | 0 | 0
23 | 14531.34 | 13191.8448 | 13192.1379 | 13364.985 | 13139 | 13343.3 | 0 | 0 | 0
24 | 13691.76 | 13724.4075 | 13754.3037 | 13370.4665 | 13323 | 12972.7 | 0 | 0 | 0
Coil Load, Sensible (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 6189.34 | 5889.2583 | 5886.9135 | 5807.8573 | 5788 | 5870.06 | 0 | 0 | 0
2 | 6201.56 | 6069.8079 | 6067.17 | 5850.1562 | 5961 | 5871.7 | 0 | 0 | 0
3 | 6194.38 | 5881.3446 | 5878.1205 | 5806.3857 | 5788 | 5782.88 | 0 | 0 | 0
4 | 5548.55 | 5878.1205 | 5873.4309 | 5740.6566 | 5788 | 5683.06 | 0 | 0 | 0
5 | 6318.9 | 5675.2953 | 5671.7781 | 5611.5024 | 5580 | 5955.01 | 0 | 0 | 0
6 | 5686.24 | 6438.5277 | 6438.5277 | 6012.3325 | 6341 | 7311.79 | 0 | 0 | 0
7 | 7596.88 | 8342.2122 | 8347.7811 | 7528.0125 | 8277 | 8646.87 | 0 | 0 | 0
8 | 9558.23 | 9069.9795 | 9069.1002 | 8751.3077 | 9038 | 9298.63 | 0 | 0 | 0
9 | 11757.9 | 11872.6017 | 11875.2396 | 11758.2673 | 11971 | 11923.2 | 0 | 0 | 0
10 | 11506.4 | 12039.0825 | 12041.1342 | 11985.6398 | 11971 | 12287.1 | 0 | 0 | 0
11 | 12342.2 | 12811.9872 | 12817.5561 | 12473.8609 | 12731 | 12561.8 | 0 | 0 | 0
12 | 12810 | 12612.093 | 12610.9206 | 12655.4944 | 12559 | 12561.3 | 0 | 0 | 0
13 | 16816.1 | 17139.0225 | 17135.2122 | 17378.5032 | 17422 | 17430.7 | 0 | 0 | 0
14 | 17283.5 | 17638.1718 | 17639.0511 | 17574.6097 | 17629 | 17608.6 | 0 | 0 | 0
15 | 22882.4 | 22196.463 | 22196.7561 | 22454.4561 | 22491 | 22350.4 | 0 | 0 | 0
16 | 22284.7 | 22527.9591 | 22533.2349 | 22527.6692 | 22491 | 22292 | 0 | 0 | 0
17 | 13048.3 | 13599.2538 | 13600.1331 | 13046.9672 | 12939 | 12739.1 | 0 | 0 | 0
18 | 12720.6 | 12829.8663 | 12831.6249 | 12851.4495 | 12729 | 12180.9 | 0 | 0 | 0
19 | 12490.8 | 11875.5327 | 11871.1362 | 12151.7364 | 11761 | 11540.7 | 0 | 0 | 0
20 | 11655.3 | 11532.3126 | 11534.0712 | 11537.4992 | 11381 | 11359.2 | 0 | 0 | 0
21 | 8882.19 | 9302.4078 | 9302.7009 | 9049.8699 | 9036 | 8931.39 | 0 | 0 | 0
22 | 8880.28 | 8973.5496 | 8973.8427 | 8939.7425 | 8864 | 8747.22 | 0 | 0 | 0
23 | 9449.35 | 8787.4311 | 8787.4311 | 8740.9679 | 8656 | 8646.75 | 0 | 0 | 0
24 | 8806.54 | 8799.1551 | 8799.7413 | 8661.2371 | 8656 | 8359.6 | 0 | 0 | 0
Coil Load, Latent (kWh,thermal)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 1942.39 | 1663.0494 | 1658.0667 | 1795.0172 | 1684 | 1797.5 | 0 | 0 | 0
2 | 1914.24 | 1560.4644 | 1559.8782 | 1777.9436 | 1747 | 1802.77 | 0 | 0 | 0
3 | 1933.51 | 1668.9114 | 1668.0321 | 1773.0767 | 1657 | 1745.07 | 0 | 0 | 0
4 | 1675.6 | 1655.7219 | 1654.8426 | 1723.1504 | 1644 | 1634.17 | 0 | 0 | 0
5 | 1785.95 | 1122.573 | 1081.2459 | 1607.3746 | 1420 | 1559.34 | 0 | 0 | 0
6 | 1444.63 | 1697.6352 | 1746.5829 | 1550.8876 | 1574 | 1911.15 | 0 | 0 | 0
7 | 2114.5 | 2733.7437 | 2884.9833 | 1865.0285 | 2173 | 2122.59 | 0 | 0 | 0
8 | 2563.08 | 1220.7615 | 1202.5893 | 2069.1885 | 1775 | 1887.81 | 0 | 0 | 0
9 | 2797.72 | 2913.1209 | 2968.8099 | 2522.4251 | 2660 | 2821.19 | 0 | 0 | 0
10 | 3132.98 | 3300.8922 | 3351.5985 | 3019.5601 | 3128 | 3595.03 | 0 | 0 | 0
11 | 4031.89 | 4643.2902 | 4787.4954 | 3654.0485 | 3991 | 4052.76 | 0 | 0 | 0
12 | 4438.4 | 3603.0783 | 3576.6993 | 4086.9647 | 3699 | 3468.23 | 0 | 0 | 0
13 | 3682.11 | 2583.9696 | 2485.7811 | 4495.456 | 3669 | 3749.01 | 0 | 0 | 0
14 | 2950.56 | 3170.1696 | 3180.135 | 3358.8288 | 3438 | 3446.79 | 0 | 0 | 0
15 | 3804.88 | 3190.6866 | 3195.9624 | 3978.4548 | 4145 | 4719.45 | 0 | 0 | 0
16 | 4437.98 | 5053.044 | 5187.87 | 4415.6877 | 4925 | 5331.25 | 0 | 0 | 0
17 | 4183.03 | 4605.4803 | 4644.4626 | 3478.7931 | 3763 | 3811.95 | 0 | 0 | 0
18 | 4785.28 | 5103.4572 | 5146.2498 | 4554.1122 | 4582 | 4648.77 | 0 | 0 | 0
19 | 5170.89 | 4136.5203 | 4043.3145 | 4930.496 | 4470 | 5094.59 | 0 | 0 | 0
20 | 5334.51 | 5549.8485 | 5586.1929 | 5205.4948 | 5486 | 5771.92 | 0 | 0 | 0
21 | 4657.75 | 4133.0031 | 4142.3823 | 4561.554 | 4447 | 4593.42 | 0 | 0 | 0
22 | 4684.26 | 4306.8114 | 4311.2079 | 4621.5598 | 4459 | 4608.6 | 0 | 0 | 0
23 | 5081.99 | 4404.4137 | 4404.7068 | 4624.0171 | 4482 | 4696.56 | 0 | 0 | 0
24 | 4885.22 | 4925.2524 | 4954.5624 | 4709.2294 | 4666 | 4613.06 | 0 | 0 | 0
Zone Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 0.0090778 | 0.0094 | 0.0094 | 0.0092568 | 0.009276 | 0.0092502 | 0 | 0 | 0
2 | 0.0090138 | 0.0093 | 0.0093 | 0.0092201 | 0.009302 | 0.0092582 | 0 | 0 | 0
3 | 0.0090644 | 0.0094 | 0.0094 | 0.0092267 | 0.009239 | 0.0092068 | 0 | 0 | 0
4 | 0.0089864 | 0.0094 | 0.0094 | 0.0091699 | 0.009201 | 0.0091047 | 0 | 0 | 0
5 | 0.0088405 | 0.0089 | 0.009 | 0.009048 | 0.008969 | 0.0089519 | 0 | 0 | 0
6 | 0.0086578 | 0.0092 | 0.0092 | 0.0089018 | 0.009012 | 0.0091583 | 0 | 0 | 0
7 | 0.0091531 | 0.01 | 0.0098 | 0.0091706 | 0.00949 | 0.0094778 | 0 | 0 | 0
8 | 0.0095303 | 0.0094 | 0.0094 | 0.0094818 | 0.009314 | 0.0093737 | 0 | 0 | 0
9 | 0.0096727 | 0.0099 | 0.0099 | 0.0096209 | 0.009708 | 0.0097161 | 0 | 0 | 0
10 | 0.010058 | 0.0103 | 0.0102 | 0.0099775 | 0.010041 | 0.010237 | 0 | 0 | 0
11 | 0.010408 | 0.0109 | 0.0107 | 0.010392 | 0.010588 | 0.010622 | 0 | 0 | 0
12 | 0.010684 | 0.0108 | 0.0108 | 0.010701 | 0.01058 | 0.010433 | 0 | 0 | 0
13 | 0.010087 | 0.0101 | 0.0102 | 0.010129 | 0.009975 | 0.0099715 | 0 | 0 | 0
14 | 0.0097987 | 0.01 | 0.01 | 0.009694 | 0.009778 | 0.0097436 | 0 | 0 | 0
15 | 0.0095792 | 0.0098 | 0.0098 | 0.009521 | 0.009579 | 0.0097834 | 0 | 0 | 0
16 | 0.0096663 | 0.01 | 0.0098 | 0.0096238 | 0.009733 | 0.0098255 | 0 | 0 | 0
17 | 0.01077 | 0.0107 | 0.0107 | 0.010361 | 0.01044 | 0.010257 | 0 | 0 | 0
18 | 0.011184 | 0.0112 | 0.0112 | 0.010924 | 0.010912 | 0.010859 | 0 | 0 | 0
19 | 0.011131 | 0.011 | 0.0111 | 0.011075 | 0.010914 | 0.011024 | 0 | 0 | 0
20 | 0.010991 | 0.0114 | 0.0113 | 0.011126 | 0.011269 | 0.011357 | 0 | 0 | 0
21 | 0.01114 | 0.0113 | 0.0113 | 0.011355 | 0.011348 | 0.011378 | 0 | 0 | 0
22 | 0.011177 | 0.0114 | 0.0114 | 0.011403 | 0.011383 | 0.011398 | 0 | 0 | 0
23 | 0.011176 | 0.0115 | 0.0115 | 0.01142 | 0.011416 | 0.01145 | 0 | 0 | 0
24 | 0.011275 | 0.0117 | 0.0117 | 0.011476 | 0.011507 | 0.011462 | 0 | 0 | 0
COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 3.5167 | 3.539 | 3.5406 | 3.5307 | 3.5195 | 3.5112 | 0 | 0 | 0
2 | 3.513 | 3.4985 | 3.4954 | 3.5201 | 3.4905 | 3.5017 | 0 | 0 | 0
3 | 3.517 | 3.5381 | 3.5411 | 3.5288 | 3.5168 | 3.5191 | 0 | 0 | 0
4 | 3.5074 | 3.5403 | 3.5411 | 3.5378 | 3.5156 | 3.5238 | 0 | 0 | 0
5 | 3.5458 | 3.5554 | 3.5375 | 3.5533 | 3.5354 | 3.4899 | 0 | 0 | 0
6 | 3.4465 | 3.4114 | 3.4219 | 3.4668 | 3.3999 | 3.2949 | 0 | 0 | 0
7 | 3.2635 | 3.12 | 3.1412 | 3.2093 | 3.1018 | 3.0648 | 0 | 0 | 0
8 | 3.079 | 2.9682 | 2.9516 | 3.0295 | 2.9584 | 2.948 | 0 | 0 | 0
9 | 3.018 | 2.9589 | 2.973 | 2.9929 | 2.9581 | 2.9787 | 0 | 0 | 0
10 | 2.9882 | 2.9902 | 2.9988 | 2.9836 | 2.9805 | 2.9726 | 0 | 0 | 0
11 | 2.9739 | 2.9233 | 2.9381 | 2.9402 | 2.9062 | 2.929 | 0 | 0 | 0
12 | 2.9504 | 2.9391 | 2.9363 | 2.9329 | 2.9189 | 2.9137 | 0 | 0 | 0
13 | 3.0122 | 2.9717 | 2.9568 | 3.0242 | 2.9771 | 2.9856 | 0 | 0 | 0
14 | 2.9638 | 2.9503 | 2.9472 | 2.9542 | 2.939 | 2.9476 | 0 | 0 | 0
15 | 3.0663 | 3.0144 | 3.0097 | 3.0418 | 3.032 | 3.0672 | 0 | 0 | 0
16 | 3.0555 | 3.068 | 3.0716 | 3.0469 | 3.0571 | 3.0943 | 0 | 0 | 0
17 | 2.8959 | 2.9007 | 2.9182 | 2.8537 | 2.8673 | 2.8928 | 0 | 0 | 0
18 | 2.9474 | 2.9496 | 2.9608 | 2.924 | 2.9298 | 2.9897 | 0 | 0 | 0
19 | 3.0508 | 3.084 | 3.0794 | 3.0408 | 3.0725 | 3.1242 | 0 | 0 | 0
20 | 3.1541 | 3.1852 | 3.1953 | 3.1496 | 3.1783 | 3.1865 | 0 | 0 | 0
21 | 3.1142 | 3.1115 | 3.1094 | 3.1151 | 3.1019 | 3.1155 | 0 | 0 | 0
22 | 3.1302 | 3.144 | 3.1466 | 3.1364 | 3.1316 | 3.1475 | 0 | 0 | 0
23 | 3.1892 | 3.1826 | 3.185 | 3.1701 | 3.1683 | 3.1734 | 0 | 0 | 0
24 | 3.1938 | 3.2014 | 3.2084 | 3.1878 | 3.1774 | 3.2033 | 0 | 0 | 0
ODB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | 0 | 0 | 0
2 | 18.05 | 18.3333 | 18.3333 | 18.1125 | 18.3 | 18.3 | 0 | 0 | 0
3 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | 0 | 0 | 0
4 | 17.8 | 17.7778 | 17.7778 | 17.8 | 17.8 | 17.8 | 0 | 0 | 0
5 | 17.5 | 17.2222 | 17.2222 | 17.425 | 17.2 | 17.2 | 0 | 0 | 0
6 | 18.3 | 19.4444 | 19.4444 | 18.575 | 19.4 | 19.4 | 0 | 0 | 0
7 | 22.2 | 25 | 25 | 22.9 | 25 | 25 | 0 | 0 | 0
8 | 26.1 | 27.2222 | 27.2222 | 26.375 | 27.2 | 27.2 | 0 | 0 | 0
9 | 28.05 | 28.8889 | 28.8889 | 28.2625 | 28.9 | 28.9 | 0 | 0 | 0
10 | 28.9 | 28.8889 | 28.8889 | 28.9 | 28.9 | 28.9 | 0 | 0 | 0
11 | 30 | 31.1111 | 31.1111 | 30.275 | 31.1 | 31.1 | 0 | 0 | 0
12 | 30.85 | 30.5556 | 30.5556 | 30.7875 | 30.6 | 30.6 | 0 | 0 | 0
13 | 30.85 | 31.1111 | 31.1111 | 30.9125 | 31.1 | 31.1 | 0 | 0 | 0
14 | 31.4 | 31.6667 | 31.6667 | 31.475 | 31.7 | 31.7 | 0 | 0 | 0
15 | 31.95 | 32.2222 | 32.2222 | 32.0125 | 32.2 | 32.2 | 0 | 0 | 0
16 | 32.2 | 32.2222 | 32.2222 | 32.2 | 32.2 | 32.2 | 0 | 0 | 0
17 | 31.95 | 31.6667 | 31.6667 | 31.8875 | 31.7 | 31.7 | 0 | 0 | 0
18 | 31.4 | 31.1111 | 31.1111 | 31.325 | 31.1 | 31.1 | 0 | 0 | 0
19 | 29.7 | 28.3333 | 28.3333 | 29.35 | 28.3 | 28.3 | 0 | 0 | 0
20 | 27.75 | 27.2222 | 27.2222 | 27.6125 | 27.2 | 27.2 | 0 | 0 | 0
21 | 27.2 | 27.2222 | 27.2222 | 27.2 | 27.2 | 27.2 | 0 | 0 | 0
22 | 26.95 | 26.6667 | 26.6667 | 26.8875 | 26.7 | 26.7 | 0 | 0 | 0
23 | 26.4 | 26.1111 | 26.1111 | 26.325 | 26.1 | 26.1 | 0 | 0 | 0
24 | 26.1 | 26.1111 | 26.1111 | 26.1 | 26.1 | 26.1 | 0 | 0 | 0
EDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 23.4068 | 23.8333 | 23.8333 | 23.945 | 23.92 | 23.9367 | 0 | 0 | 0
2 | 23.3748 | 23.9444 | 23.9444 | 23.9636 | 24 | 23.9367 | 0 | 0 | 0
3 | 23.3833 | 23.8333 | 23.8333 | 23.9451 | 23.92 | 23.8958 | 0 | 0 | 0
4 | 23.3739 | 23.8333 | 23.8333 | 23.9169 | 23.92 | 23.8375 | 0 | 0 | 0
5 | 23.3503 | 23.7778 | 23.7778 | 23.8612 | 23.83 | 23.9757 | 0 | 0 | 0
6 | 23.4171 | 24.1111 | 24.1111 | 24.0335 | 24.16 | 24.5756 | 0 | 0 | 0
7 | 24.0395 | 24.9444 | 24.9444 | 24.6841 | 25 | 25.1643 | 0 | 0 | 0
8 | 24.5724 | 25.2778 | 25.2778 | 25.208 | 25.33 | 25.4533 | 0 | 0 | 0
9 | 25.0937 | 25.5556 | 25.5556 | 25.4906 | 25.59 | 25.5785 | 0 | 0 | 0
10 | 25.2815 | 25.5556 | 25.5556 | 25.5865 | 25.59 | 25.7393 | 0 | 0 | 0
11 | 25.3592 | 25.8889 | 25.8889 | 25.7953 | 25.91 | 25.8631 | 0 | 0 | 0
12 | 25.5877 | 25.8333 | 25.8333 | 25.8718 | 25.84 | 25.8628 | 0 | 0 | 0
13 | 26.53 | 25.9444 | 25.9444 | 25.8849 | 25.91 | 25.9424 | 0 | 0 | 0
14 | 26.5617 | 26.0556 | 26.0556 | 25.9689 | 26 | 26.022 | 0 | 0 | 0
15 | 26.7812 | 26.1111 | 26.1111 | 26.0513 | 26.08 | 26.1296 | 0 | 0 | 0
16 | 26.5632 | 26.1667 | 26.1667 | 26.0827 | 26.08 | 26.0323 | 0 | 0 | 0
17 | 26.198 | 26.0556 | 26.0556 | 26.0396 | 26 | 25.943 | 0 | 0 | 0
18 | 26.2263 | 25.9444 | 25.9444 | 25.9556 | 25.91 | 25.6955 | 0 | 0 | 0
19 | 25.7001 | 25.5 | 25.5 | 25.6558 | 25.5 | 25.4093 | 0 | 0 | 0
20 | 25.1673 | 25.3333 | 25.3333 | 25.3934 | 25.33 | 25.3281 | 0 | 0 | 0
21 | 24.6544 | 25.3333 | 25.3333 | 25.333 | 25.33 | 25.291 | 0 | 0 | 0
22 | 24.7445 | 25.2222 | 25.2222 | 25.2865 | 25.25 | 25.2092 | 0 | 0 | 0
23 | 24.6707 | 25.1111 | 25.1111 | 25.2013 | 25.16 | 25.1645 | 0 | 0 | 0
24 | 24.7257 | 25.1111 | 25.1111 | 25.1674 | 25.16 | 25.0374 | 0 | 0 | 0
EWB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 16.9641 | 17.34 | 17.34 | 0 | 17.155 | 17.3042 | 0 | 0 | 0
2 | 16.9046 | 17.29 | 17.29 | 0 | 17.238 | 17.31 | 0 | 0 | 0
3 | 16.9418 | 17.34 | 17.37 | 0 | 17.12 | 17.2367 | 0 | 0 | 0
4 | 16.8619 | 17.34 | 17.37 | 0 | 17.102 | 17.0785 | 0 | 0 | 0
5 | 16.6966 | 16.85 | 16.94 | 0 | 16.787 | 17.0075 | 0 | 0 | 0
6 | 16.5734 | 17.3 | 17.3 | 0 | 17.032 | 17.5412 | 0 | 0 | 0
7 | 17.3192 | 18.39 | 18.23 | 0 | 17.911 | 17.9926 | 0 | 0 | 0
8 | 17.7945 | 17.78 | 17.78 | 0 | 17.646 | 17.9591 | 0 | 0 | 0
9 | 17.973 | 18.36 | 18.28 | 0 | 18.118 | 18.3251 | 0 | 0 | 0
10 | 18.3972 | 18.68 | 18.6 | 0 | 18.442 | 18.8543 | 0 | 0 | 0
11 | 18.8246 | 19.48 | 19.33 | 0 | 19.142 | 19.1876 | 0 | 0 | 0
12 | 19.1202 | 19.23 | 19.23 | 0 | 18.935 | 18.8671 | 0 | 0 | 0
13 | 18.8377 | 18.56 | 18.64 | 0 | 18.326 | 18.518 | 0 | 0 | 0
14 | 18.5548 | 18.6 | 18.6 | 0 | 18.269 | 18.4421 | 0 | 0 | 0
15 | 18.5486 | 18.46 | 18.46 | 0 | 18.239 | 18.6471 | 0 | 0 | 0
16 | 18.673 | 18.84 | 18.76 | 0 | 18.557 | 18.7965 | 0 | 0 | 0
17 | 19.4032 | 19.35 | 19.35 | 0 | 19.063 | 19.1104 | 0 | 0 | 0
18 | 19.7724 | 19.75 | 19.68 | 0 | 19.458 | 19.3936 | 0 | 0 | 0
19 | 19.5753 | 19.32 | 19.4 | 0 | 19.199 | 19.5323 | 0 | 0 | 0
20 | 19.3718 | 19.76 | 19.76 | 0 | 19.65 | 19.7431 | 0 | 0 | 0
21 | 19.438 | 19.76 | 19.76 | 0 | 19.706 | 19.7437 | 0 | 0 | 0
22 | 19.4846 | 19.8 | 19.8 | 0 | 19.697 | 19.7887 | 0 | 0 | 0
23 | 19.4693 | 19.84 | 19.84 | 0 | 19.694 | 19.8355 | 0 | 0 | 0
24 | 19.5725 | 20.14 | 20.06 | 0 | 19.805 | 19.7678 | 0 | 0 | 0
OHR (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
1 | 0.011255 | 0.0114 | 0.0114 | 0.011202 | 0.0111 | 0.011072 | 0 | 0 | 0
2 | 0.011255 | 0.0112 | 0.0112 | 0.011296 | 0.011462 | 0.011432 | 0 | 0 | 0
3 | 0.011255 | 0.0114 | 0.0114 | 0.011199 | 0.0111 | 0.011072 | 0 | 0 | 0
4 | 0.011075 | 0.0114 | 0.0114 | 0.011061 | 0.0111 | 0.011072 | 0 | 0 | 0
5 | 0.01061 | 0.0103 | 0.0103 | 0.010484 | 0.01018 | 0.010155 | 0 | 0 | 0
6 | 0.010568 | 0.0113 | 0.0113 | 0.010648 | 0.011001 | 0.01097 | 0 | 0 | 0
7 | 0.012071 | 0.0133 | 0.0133 | 0.012288 | 0.01314 | 0.013099 | 0 | 0 | 0
8 | 0.012173 | 0.0109 | 0.0109 | 0.011849 | 0.011075 | 0.011039 | 0 | 0 | 0
9 | 0.011538 | 0.0117 | 0.0117 | 0.01158 | 0.011995 | 0.011957 | 0 | 0 | 0
10 | 0.012388 | 0.0125 | 0.0125 | 0.012406 | 0.01276 | 0.012719 | 0 | 0 | 0
11 | 0.013776 | 0.0148 | 0.0148 | 0.013949 | 0.014809 | 0.014761 | 0 | 0 | 0
12 | 0.014041 | 0.0134 | 0.0134 | 0.013761 | 0.013253 | 0.013211 | 0 | 0 | 0
13 | 0.012315 | 0.0115 | 0.0115 | 0.011999 | 0.011329 | 0.011293 | 0 | 0 | 0
14 | 0.011543 | 0.0121 | 0.0121 | 0.011528 | 0.011729 | 0.011692 | 0 | 0 | 0
15 | 0.012069 | 0.0119 | 0.0119 | 0.012086 | 0.012379 | 0.01234 | 0 | 0 | 0
16 | 0.013324 | 0.0144 | 0.0144 | 0.013492 | 0.014232 | 0.014188 | 0 | 0 | 0
17 | 0.014505 | 0.0146 | 0.0146 | 0.014504 | 0.01473 | 0.014684 | 0 | 0 | 0
18 | 0.015234 | 0.0157 | 0.0157 | 0.015288 | 0.015684 | 0.015634 | 0 | 0 | 0
19 | 0.015134 | 0.0143 | 0.0143 | 0.01493 | 0.014539 | 0.014493 | 0 | 0 | 0
20 | 0.015748 | 0.0164 | 0.0164 | 0.01597 | 0.016878 | 0.016824 | 0 | 0 | 0
21 | 0.016886 | 0.0164 | 0.0164 | 0.01681 | 0.016878 | 0.016824 | 0 | 0 | 0
22 | 0.016863 | 0.0167 | 0.0167 | 0.016771 | 0.016832 | 0.016777 | 0 | 0 | 0
23 | 0.016867 | 0.0169 | 0.0169 | 0.016784 | 0.016889 | 0.016835 | 0 | 0 | 0
24 | 0.017112 | 0.0178 | 0.0178 | 0.017077 | 0.017329 | 0.017273 | 0 | 0 | 0
E500, E530 Average Daily Outputs
Energy Consumption, Total (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 3892.9389 | 3975.4583 | 3975.1667 | 4019.3858 | 3901.0417 | 4073 | 0 | 0 | 0
E500Jun25 | 5044.9219 | 5204.3333 | 5204.0833 | 5244.3836 | 5066.5 | 5230 | 0 | 0 | 0
E530Apr30 | 3022.7732 | 3062 | 3061.7917 | 3131.8977 | 3091.5417 | 3144 | 0 | 0 | 0
E530Jun25 | 3894.1233 | 3978.2083 | 3978.0833 | 4090.8917 | 3934.625 | 4043 | 0 | 0 | 0
Energy Consumption, Compressor (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 3014.619 | 3119.8333 | 3119.6667 | 3501.4974 | 3020.0417 | 3159 | 0 | 0 | 0
E500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 | 4677.7875 | 4105.9583 | 4239 | 0 | 0 | 0
E530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 | 2716.0206 | 2378.4583 | 2411 | 0 | 0 | 0
E530Jun25 | 3118.0954 | 3243 | 3242.9583 | 3632.6991 | 3165.5833 | 3248 | 0 | 0 | 0
Energy Consumption, Condenser Fan (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 376.0762 | 389.125 | 389.0833 | Note 1 | 377.25 | 391 | 0 | 0 | 0
E500Jun25 | 411.4946 | 426.3333 | 426.3333 | Note 1 | 411.3333 | 424 | 0 | 0 | 0
E530Apr30 | 304.5625 | 311.1667 | 311.125 | Note 1 | 305.3333 | 314 | 0 | 0 | 0
E530Jun25 | 332.2771 | 339.625 | 339.625 | Note 1 | 329.25 | 340 | 0 | 0 | 0
Energy Consumption, Indoor Fan (Wh,e)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 502.2437 | 466.5 | 466.4167 | 517.8884 | 503.75 | 522 | 0 | 0 | 0
E500Jun25 | 549.5444 | 514.4583 | 514.3333 | 566.5961 | 549.2083 | 566 | 0 | 0 | 0
E530Apr30 | 406.7383 | 360.7917 | 360.75 | 415.8771 | 407.75 | 419 | 0 | 0 | 0
E530Jun25 | 443.7507 | 395.5833 | 395.5 | 458.1925 | 439.7917 | 454 | 0 | 0 | 0
Total Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 13185.6871 | 13732.6998 | 13732.9074 | 13653.7633 | 13169.5417 | 13673 | 0 | 0 | 0
E500Jun25 | 13188.0504 | 13837.5319 | 13837.3853 | 13734.0071 | 13198.0833 | 13727 | 0 | 0 | 0
E530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 0 | 0 | 0
E530Jun25 | 9376.2963 | 9760.7918 | 9760.6941 | 9843.2403 | 9387.625 | 9834 | 0 | 0 | 0
Sensible Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 9374.7971 | 9924.8179 | 9925.0255 | 9849.8339 | 9365.4583 | 9902 | 0 | 0 | 0
E500Jun25 | 9377.6867 | 9981.2396 | 9981.0931 | 9923.758 | 9387.625 | 9946 | 0 | 0 | 0
E530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 0 | 0 | 0
E530Jun25 | 9376.2963 | 9760.7674 | 9760.6697 | 9843.2403 | 9387.625 | 9834 | 0 | 0 | 0
Latent Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 3810.89 | 3807.8819 | 3807.8819 | 3803.9295 | 3804.375 | 3770 | 0 | 0 | 0
E500Jun25 | 3810.3637 | 3856.2923 | 3856.2923 | 3810.249 | 3810.4167 | 3780 | 0 | 0 | 0
E530Apr30 | -5.4771e-13 | 0 | 0 | 3.0182e-13 | 0 | 0 | 0 | 0 | 0
E530Jun25 | 7.2905e-13 | 0.024425 | 0.024425 | 3.5571e-13 | 0 | 0 | 0 | 0 | 0
Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 0.010675 | 0.011 | 0.011 | 0.010646 | 0.010938 | 0.016 | 0 | 0 | 0
E500Jun25 | 0.011168 | 0.0115 | 0.0115 | 0.011144 | 0.011479 | 0.011 | 0 | 0 | 0
E530Apr30 | 0.006208 | 0.0071 | 0.0071 | 0.006466 | 0.005485 | 0.00674 | 0 | 0 | 0
E530Jun25 | 0.006208 | 0.0078 | 0.0078 | 0.006466 | 0.005478 | 0.00674 | 0 | 0 | 0
COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 3.8448 | 3.9136 | 3.9139 | 3.8588 | 3.8372 | 3.85 | 0 | 0 | 0
E500Jun25 | 2.9313 | 2.9505 | 2.9506 | 2.9346 | 2.9213 | 2.94 | 0 | 0 | 0
E530Apr30 | 3.5431 | 3.5988 | 3.5991 | 3.4048 | 3.4604 | 3.59 | 0 | 0 | 0
E530Jun25 | 2.7197 | 2.7245 | 2.7245 | 2.7405 | 2.69 | 2.74 | 0 | 0 | 0
ODB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 0 | 0 | 0
E500Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 0 | 0 | 0
E530Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 0 | 0 | 0
E530Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 0 | 0 | 0
EDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E500Apr30 | 24.6411 | 24.9444 | 24.9444 | 24.982 | 25 | 25 | 0 | 0 | 0
E500Jun25 | 24.5478 | 25 | 25 | 24.9831 | 25 | 25 | 0 | 0 | 0
E530Apr30 | 24.365 | 24.9444 | 24.6667 | 25.0003 | 25 | 25 | 0 | 0 | 0
E530Jun25 | 24.3537 | 24.9444 | 24.9444 | 25.0003 | 25 | 25 | 0 | 0 | 0
Hourly integrated maxima for consumptions and loads
Compressor + Condenser Fan + Indoor Fan Energy Consumption (Wh,e)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7089 | 07/20 | 15:00 | 11932 | 202 | 15 | 11548 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 12594.4016 | 20-Jul | 15 | 12583 | 2002-07-20 | 15 | 12595 | 37457 | 15 | 12572.0793 | 07/20 | 15:00 | 12653 | 202 | 15 | 12162 | 37849 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 13028.1986 | 20-Jul | 15 | 12916 | 2002-07-20 | 15 | 12981 | 37457 | 15 | 12988.8392 | 07/20 | 15:00 | 13104 | 202 | 15 | 12875 | 37822 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 13346.701 | 20-Jul | 15 | 13212 | 2002-07-20 | 15 | 13407 | 37457 | 15 | 13356.2349 | 07/20 | 15:00 | 13467 | 202 | 15 | 13335 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 13180.9018 | 20-Jul | 15 | 13158 | 2002-07-20 | 15 | 13190 | 37457 | 15 | 13174.9258 | 07/20 | 15:00 | 13277 | 202 | 15 | 13101 | 37822 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 11626.889 | 20-Jul | 15 | 11654 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7017 | 07/20 | 15:00 | 11932 | 202 | 15 | 11546 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 12769.5022 | 20-Jul | 15 | 12736 | 2002-07-20 | 15 | 12726 | 37457 | 15 | 12776.4285 | 07/20 | 15:00 | 12863 | 202 | 15 | 12762 | 37822 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11677 | 38248 | 15 | 11995.6974 | 07/20 | 15:00 | 0 | 0 | 0 | 11519 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7089 | 07/20 | 15:00 | 0 | 0 | 0 | 11549 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7089 | 07/20 | 15:00 | 0 | 0 | 0 | 11548 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7089 | 07/20 | 15:00 | 0 | 0 | 0 | 11548 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 37457 | 15 | 11995.7089 | 07/20 | 15:00 | 0 | 0 | 0 | 11461 | 37849 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 10166.4831 | 20-Jul | 15 | 10431 | 2002-07-20 | 15 | 10425 | 37457 | 15 | 10438.5175 | 07/20 | 15:00 | 10177 | 202 | 15 | 10274 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 11204.8968 | 20-Jul | 15 | 11590 | 2002-07-20 | 15 | 11587 | 37457 | 15 | 11450.7514 | 07/20 | 15:00 | 11186 | 202 | 15 | 11344 | 37822 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 11035.3898 | 20-Jul | 15 | 10989 | 2002-07-20 | 15 | 11014 | 37457 | 15 | 11261.8296 | 07/20 | 15:00 | 11044 | 202 | 15 | 10684 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 10430.7791 | 20-Jul | 15 | 10972 | 2002-07-20 | 15 | 10966 | 37457 | 15 | 10902.675 | 07/20 | 15:00 | 10639 | 202 | 15 | 10747 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 9366.7481 | 20-Jul | 15 | 9538 | 2002-07-20 | 15 | 9531 | 37457 | 15 | 9588.2506 | 07/20 | 15:00 | 9419 | 202 | 15 | 9585 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 8028.3285 | 20-Jul | 15 | 8059 | 2002-07-20 | 15 | 8055 | 37457 | 15 | 8293.041 | 07/20 | 15:00 | 7992 | 202 | 15 | 8089 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 8698.9562 | 20-Jul | 15 | 8943 | 2002-07-20 | 15 | 8939 | 37457 | 15 | 9076.4428 | 07/20 | 15:00 | 8846 | 202 | 15 | 8985 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 7204.827 | 20-Jul | 15 | 7350 | 2002-07-20 | 15 | 7346 | 37457 | 15 | 7767.989 | 07/20 | 15:00 | 7351 | 202 | 15 | 7471 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 23457 | 202 | 15 | 22908 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 23094.3 | 10-Sep | 15 | 23080 | 2004-09-10 | 16 | 23119 | 2004-06-04 | 16 | 23145.0651 | 07/11 | 16:00 | 23078 | 254 | 15 | 22649 | 37785 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 31315.6 | 24-Apr | 16 | 31119 | 2004-04-24 | 16 | 31072 | 2002-04-24 | 16 | 31528.7254 | 04/24 | 15:00 | 31134 | 155 | 16 | 30967 | 37735 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 33226.1 | 14-Jun | 14 | 33410 | 2002-06-14 | 14 | 34490 | 2002-06-14 | 15 | 34692.1931 | 06/14 | 14:00 | 33997 | 115 | 16 | 33421 | 37873 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 32828.9 | 24-Apr | 15 | 32086 | 2002-05-16 | 16 | 32086 | 2002-05-16 | 16 | 32737.1011 | 04/24 | 15:00 | 32940 | 115 | 16 | 32180 | 37735 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.136 | 07/20 | 15:00 | 23457 | 202 | 15 | 22876 | 37812 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 32060.7 | 24-Apr | 16 | 32111 | 2003-04-24 | 16 | 32065 | 2004-04-24 | 16 | 32409.2976 | 04/24 | 16:00 | 31981 | 115 | 16 | 32179 | 37735 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1222 | 07/20 | 15:00 | 0 | 0 | 0 | 22877 | 37810 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 23265.7 | 10-Sep | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 0 | 0 | 0 | 22893 | 37831 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 0 | 0 | 0 | 22893 | 37831 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 0 | 0 | 0 | 22893 | 37831 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 0 | 0 | 0 | 22875 | 37849 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 19549.2 | 28-Oct | 15 | 20009 | 2003-06-04 | 16 | 20008 | 2002-09-10 | 16 | 19795.9105 | 07/20 | 15:00 | 18776 | 156 | 15 | 19818 | 37831 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 21729.2 | 29-Apr | 19 | 22513 | 2002-07-11 | 15 | 22513 | 2003-07-11 | 15 | 22227.967 | 07/20 | 16:00 | 21121 | 156 | 13 | 22269 | 37822 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 19415.9 | 28-Sep | 15 | 20159 | 2004-05-26 | 16 | 20154 | 2004-05-26 | 16 | 20012.5751 | 07/30 | 16:00 | 18969 | 202 | 16 | 20378 | 37764 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 19488.8 | 12-Mai | 15 | 20137 | 2002-07-11 | 16 | 20135 | 2002-07-11 | 16 | 19901.8714 | 07/20 | 15:00 | 18785 | 156 | 15 | 19920 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 19702.7 | 26-Jul | 16 | 19850 | 2002-04-24 | 16 | 19850 | 2002-04-24 | 16 | 19599.0538 | 07/20 | 15:00 | 18759 | 156 | 15 | 19661 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19656.1402 | 07/20 | 15:00 | 18776 | 156 | 15 | 19626 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19812.465 | 07/20 | 15:00 | 18794 | 156 | 15 | 19799 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19538.7609 | 07/20 | 15:00 | 18759 | 156 | 15 | 19497 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Latent Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9394 | 2001-09-03 | 15 | 10595.085 | 07/10 | 13:00 | 10375 | 247 | 15 | 10392 | 37867 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 15907 | 03-Sep | 15 | 15139 | 2001-09-03 | 15 | 15270 | 2001-09-03 | 15 | 16644.3073 | 08/04 | 15:00 | 16112 | 217 | 15 | 16077 | 37867 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 23147.3 | 02-Oct | 10 | 31497 | 2002-10-02 | 9 | 31503 | 2002-10-02 | 9 | 22756.175 | 10/02 | 10:00 | 21697 | 261 | 12 | 21929 | 37895 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 27825.2 | 18-Sep | 16 | 26941 | 2003-09-18 | 15 | 40809 | 2002-10-02 | 9 | 27596.7005 | 09/18 | 16:00 | 28184 | 262 | 15 | 27488 | 37882 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 24848.3 | 02-Oct | 9 | 30451 | 2002-10-02 | 9 | 36011 | 2002-10-02 | 9 | 24435.7652 | 10/02 | 10:00 | 24225 | 247 | 17 | 23794 | 37895 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 9751.26 | 01-Oct | 13 | 9303 | 2001-09-03 | 15 | 9393 | 2001-09-03 | 15 | 10595.6426 | 07/10 | 13:00 | 10755 | 276 | 8 | 11603 | 37836 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 9275.16 | 02-Oct | 10 | 10026 | 2002-10-02 | 9 | 10336 | 2002-10-02 | 9 | 8907.2199 | 10/02 | 10:00 | 8859 | 247 | 17 | 8934 | 37867 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 27075.3 | 16-Sep | 15 | 25578 | 2002-09-18 | 14 | 32396 | 2003-09-18 | 15 | 26767.6767 | 09/16 | 15:00 | 0 | 0 | 0 | 26645 | 37880 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 11138.9 | 16-Sep | 15 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | 10595.085 | 07/10 | 13:00 | 0 | 0 | 0 | 10377 | 37873 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 9751.04 | 01-Oct | 13 | 9304 | 2001-09-03 | 15 | 9394 | 2003-09-03 | 15 | 10595.085 | 07/10 | 13:00 | 0 | 0 | 0 | 10394 | 37867 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 9635.7 | 03-Sep | 16 | 11105 | 2004-10-24 | 14 | 11101 | 2003-05-21 | 15 | 11375.3248 | 10/24 | 13:00 | 0 | 0 | 0 | 10394 | 37867 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | 10595.085 | 07/10 | 13:00 | 0 | 0 | 0 | 10139 | 37867 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 7965.46 | 06-Oct | 15 | 7733 | 2001-09-03 | 15 | 7733 | 2001-09-03 | 15 | 7908.9572 | 06/29 | 16:00 | 7805 | 181 | 16 | 7762 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 8892.56 | 15-Sep | 11 | 8723 | 2002-10-02 | 9 | 8723 | 2003-10-02 | 9 | 9041.0375 | 06/17 | 14:00 | 8850 | 169 | 14 | 8874 | 37789 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 7913.7 | 28-Sep | 15 | 7785 | 2001-09-03 | 15 | 7785 | 2001-09-03 | 15 | 7785.2261 | 06/29 | 16:00 | 7726 | 182 | 16 | 7964 | 37764 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 7906.7 | 02-Mai | 15 | 7760 | 2001-09-03 | 15 | 7760 | 2001-09-03 | 15 | 7850.1656 | 06/29 | 16:00 | 7743 | 181 | 16 | 7745 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 8037.07 | 26-Jul | 16 | 7663 | 2001-09-03 | 15 | 7663 | 2001-09-03 | 15 | 8006.3955 | 06/29 | 16:00 | 7938 | 181 | 16 | 7820 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 1.6431e-11 | 18-Jun | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1783 | 03/16 | 10:00 | 179 | 71 | 11 | 35.9 | 37926 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 627.186 | 11-Mar | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1636.359 | 03/11 | 10:00 | 845 | 71 | 10 | 1181 | 37691 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 1.8119e-11 | 01-Jul | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2784e-12 | 05/29 | 13:00 | 4 | 202 | 15 | 0 | 37622 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible + Latent Coil Load (Wh,th)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 32502 | 202 | 15 | 32072 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 37328 | 03-Sep | 15 | 36750 | 2004-09-03 | 16 | 37033 | 2004-09-03 | 16 | 37372.5209 | 09/17 | 15:00 | 37261 | 247 | 15 | 36991 | 37867 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 40317.6 | 03-Sep | 16 | 53813 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9 | 40097.0154 | 10/02 | 10:00 | 39904 | 247 | 16 | 39920 | 37867 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 43492 | 02-Oct | 9 | 43628 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9 | 43597.9449 | 10/02 | 09:00 | 43978 | 276 | 9 | 42415 | 37812 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 41651.7 | 02-Oct | 10 | 50819 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9 | 41608.4737 | 10/02 | 10:00 | 41366 | 247 | 15 | 41132 | 37867 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31454 | 2001-07-20 | 15 | 33057.4487 | 07/20 | 15:00 | 32502 | 202 | 15 | 32077 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 38857.16 | 02-Oct | 10 | 40613 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9 | 38691.4863 | 10/02 | 11:00 | 38322 | 276 | 10 | 38451 | 37896 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 41178.6 | 16-Sep | 15 | 40543 | 2002-09-18 | 14 | 49838 | 2003-09-18 | 15 | 41112.206 | 09/16 | 15:00 | 0 | 0 | 0 | 40774 | 37880 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 0 | 0 | 0 | 32073 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 0 | 0 | 0 | 32072 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 0 | 0 | 0 | 32072 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2003-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 0 | 0 | 0 | 31777 | 37810 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 27485.51 | 28-Oct | 15 | 27707 | 2001-08-16 | 16 | 27706 | 2001-08-16 | 16 | 27656.4201 | 06/29 | 16:00 | 26567 | 181 | 16 | 27555 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 30593.05 | 29-Apr | 19 | 31188 | 2001-07-20 | 15 | 31188 | 2001-07-20 | 15 | 31194.5493 | 06/17 | 14:00 | 29948 | 169 | 14 | 31097 | 37789 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 27329.6 | 28-Sep | 15 | 27878 | 2004-08-14 | 16 | 27878 | 2004-07-23 | 16 | 27731.0711 | 06/29 | 16:00 | 26675 | 202 | 16 | 28343 | 37764 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 27383.59 | 12-Mai | 15 | 27868 | 2002-08-16 | 16 | 27866 | 2002-08-16 | 16 | 27698.162 | 06/29 | 16:00 | 26514 | 181 | 16 | 27636 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 27739.77 | 26-Jul | 16 | 27466 | 2002-07-08 | 16 | 27466 | 2002-07-08 | 16 | 27564.3415 | 06/29 | 16:00 | 26683 | 181 | 16 | 27462 | 37801 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19656.1402 | 07/20 | 15:00 | 18776 | 156 | 15 | 19626 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19812.465 | 07/20 | 15:00 | 18794 | 156 | 15 | 19799 | 37849 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19538.7609 | 07/20 | 15:00 | 18764 | 202 | 15 | 19497 | 37776 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weather Data Checks, E300 only, Maxima
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
ODB | 34.7 | 20-Jul | 15 | 35 | 2002-07-20 | 15 | 35 | 37457 | 1900-01-14 | 34.775 | 07/20 | 15:00 | 35 | 202 | 15 | 35 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OHR | 0.021878 | 02-Oct | 9 | 0.0225 | 2002-10-02 | 9 | 0.0225 | 2002-10-02 | 1900-01-08 | 0.021868 | 37531 | 09:00 | 0.022406 | 10/02 | 9 | 0.0223 | 276 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maxima, Minima for COP2 and zone conditions
Maximum COP2
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 4.1683 | 16-Apr | 3 | 3.869 | 2002-04-30 | 16 | 3.857 | 2002-04-30 | 16 | 3.9232 | 04/30 | 15:00 | 3.8706 | 121 | 16 | 3.88 | 37741 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 4.1433 | 30-Apr | 15 | 4.141 | 2002-04-30 | 16 | 4.128 | 2002-04-30 | 16 | 4.1954 | 04/30 | 15:00 | 4.1276 | 121 | 15 | 4.12 | 37741 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 4.1683 | 16-Apr | 3 | 5.143 | 2002-10-02 | 9 | 4.967 | 2002-10-02 | 9 | 3.9648 | 09/16 | 15:00 | 3.9433 | 260 | 15 | 4.38 | 37973 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 4.1683 | 16-Apr | 3 | 4.109 | 2003-06-17 | 16 | 5.595 | 2002-10-02 | 9 | 4.0962 | 09/16 | 14:00 | 4.1219 | 169 | 16 | 4.05 | 37789 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 4.1683 | 16-Apr | 3 | 4.621 | 2002-10-02 | 9 | 5.339 | 2002-10-02 | 9 | 4.0147 | 09/16 | 15:00 | 4.0172 | 260 | 16 | 3.95 | 37880 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 4.1683 | 16-Apr | 3 | 3.889 | 2003-04-27 | 5 | 3.863 | 2004-10-05 | 3 | 4.3453 | 10/13 | 01:00 | 3.9321 | 278 | 24 | 3.88 | 37741 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 4.401 | 05-Oct | 1 | 4.428 | 2002-10-04 | 24 | 4.427 | 2002-10-04 | 24 | 4.4308 | 10/04 | 24:00 | 4.432 | 278 | 24 | 4.44 | 37898 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 4.0769 | 16-Sep | 15 | 4.088 | 2003-06-17 | 16 | 4.776 | 2003-09-18 | 15 | 4.0961 | 09/16 | 14:00 | 0 | 0 | 0 | 4.05 | 37789 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 3.8879 | 30-Apr | 15 | 3.903 | 2002-04-30 | 15 | 3.855 | 2002-04-30 | 16 | 4.0403 | 04/30 | 15:00 | 0 | 0 | 0 | 3.84 | 37762 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 3.7813 | 27-Sep | 16 | 3.807 | 2003-05-21 | 15 | 3.759 | 2003-09-27 | 15 | 3.8446 | 05/21 | 15:00 | 0 | 0 | 0 | 3.94 | 37762 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 3.7813 | 27-Sep | 16 | 3.805 | 2003-10-24 | 15 | 3.759 | 2003-09-27 | 15 | 3.8044 | 05/21 | 15:00 | 0 | 0 | 0 | 3.93 | 37741 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 3.8835 | 12-Dez | 7 | 3.774 | 2002-09-27 | 15 | 3.759 | 2002-09-27 | 15 | 3.8044 | 05/21 | 15:00 | 0 | 0 | 0 | 3.81 | 37741 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 4.2751 | 13-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.2343 | 03/16 | 10:00 | 4.1846 | 76 | 10 | 4.14 | 37741 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 4.6925 | 05-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.7069 | 10/05 | 01:00 | 4.6896 | 278 | 24 | 4.53 | 37745 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 3.8137 | 30-Apr | 15 | 4.896 | 2004-03-16 | 10 | 4.652 | 2003-03-16 | 10 | 3.838 | 04/30 | 15:00 | 3.8017 | 121 | 16 | 3.84 | 37741 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 3.9855 | 16-Mar | 10 | 6.233 | 2004-03-11 | 10 | 5.678 | 2004-03-11 | 10 | 4.0074 | 04/30 | 15:00 | 3.9858 | 121 | 16 | 4 | 37741 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 4.7178 | 13-Oct | 1 | 6.325 | 2004-04-12 | 9 | 6.031 | 2004-03-16 | 10 | 4.6776 | 03/16 | 10:00 | 4.6381 | 76 | 10 | 4.4 | 37696 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 4.0061 | 02-Nov | 1 | 3.981 | 2004-03-11 | 10 | 3.85 | 2004-10-13 | 9 | 3.9202 | 03/16 | 10:00 | 3.84 | 76 | 10 | 3.88 | 37696 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 3.456 | 30-Apr | 15 | 3.456 | 2004-04-30 | 16 | 3.455 | 2004-04-30 | 16 | 3.5169 | 03/16 | 10:00 | 3.6667 | 71 | 22 | 3.69 | 37911 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 4.2505 | 16-Mar | 10 | 4.275 | 2004-03-16 | 10 | 4.428 | 2004-03-16 | 10 | 4.2157 | 03/16 | 10:00 | 4.1565 | 76 | 10 | 4.17 | 37696 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum COP2
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 2.7931 | 24-Apr | 17 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 2.7856 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 2.8652 | 01-Dec | 15 | 2.85 | 2002-12-01 | 14 | 2.851 | 2002-12-01 | 12 | 2.8671 | 12/01 | 15:00 | 2.8726 | 1900-12-01 | 15 | 2.87 | 2003-12-01 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 2.8252 | 31-Mar | 14 | 2.801 | 2002-12-01 | 14 | 2.805 | 2003-12-01 | 15 | 2.8231 | 03/31 | 15:00 | 2.8145 | 1900-03-31 | 15 | 2.83 | 2003-03-31 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 2.7904 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 2.7859 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 2.8252 | 31-Mar | 14 | 2.799 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 2.7819 | 31-Mar | 19 | 2.734 | 2002-12-03 | 15 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 | 0 | 0 | 0 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 2.7858 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 0 | 0 | 0 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 2.7931 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 0 | 0 | 0 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 2.7711 | 30-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 | 0 | 0 | 0 | 2.81 | 2003-06-14 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 2.7825 | 31-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 | 0 | 0 | 0 | 2.81 | 2003-04-08 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 2.6852 | 30-Jul | 12 | 2.693 | 2002-07-29 | 12 | 2.652 | 2004-03-30 | 17 | 2.6947 | 07/30 | 12:00 | 2.6665 | 1900-07-30 | 12 | 2.71 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 2.888 | 31-Mar | 15 | 2.817 | 2004-04-05 | 17 | 2.652 | 2004-03-30 | 17 | 2.8993 | 03/31 | 15:00 | 2.8817 | 1900-03-31 | 15 | 2.9 | 2003-03-31 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 2.4417 | 30-Jul | 12 | 2.463 | 2004-04-05 | 17 | 2.394 | 2004-04-05 | 17 | 2.4618 | 07/30 | 12:00 | 2.3333 | 1900-01-28 | 10 | 2.47 | 2003-07-30 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 2.5689 | 08-Jul | 17 | 2.572 | 2002-07-29 | 12 | 2.562 | 2004-03-31 | 17 | 2.5777 | 07/30 | 12:00 | 2.4286 | 1900-03-30 | 17 | 2.59 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 2.9111 | 14-Jul | 17 | 2.939 | 2003-07-30 | 12 | 2.814 | 2004-03-31 | 17 | 2.9333 | 07/30 | 12:00 | 2.8941 | 1900-07-29 | 12 | 2.9 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 2.5013 | 30-Jul | 12 | 2.495 | 2002-07-29 | 12 | 2.498 | 2002-07-29 | 12 | 2.4945 | 07/30 | 12:00 | 2.4733 | 1900-07-29 | 12 | 2.52 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 2.253 | 30-Jul | 12 | 2.261 | 2003-07-29 | 12 | 2.262 | 2012-07-30 | 12 | 2.2794 | 07/30 | 12:00 | 2.1429 | 1900-04-05 | 20 | 2.28 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 2.7325 | 14-Jul | 17 | 2.72 | 2003-07-29 | 12 | 2.722 | 2002-07-30 | 12 | 2.6585 | 07/30 | 12:00 | 2.692 | 1900-07-29 | 12 | 2.72 | 2003-07-29 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum IDB (°C)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0033 | 09/23 | 08:00 | 25.05 | 52 | 17 | 26.19 | 37928 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 27.0778 | 20-Jul | 15 | 26.89 | 2004-07-20 | 16 | 26.72 | 2002-07-20 | 16 | 26.5567 | 07/20 | 16:00 | 26.62 | 202 | 15 | 27.19 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 32.3604 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.5 | 2003-07-08 | 16 | 31.844 | 07/20 | 15:00 | 32.32 | 202 | 15 | 31.65 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 32.2321 | 20-Jul | 15 | 31.72 | 2004-07-08 | 16 | 32 | 2003-07-20 | 16 | 31.4963 | 07/20 | 15:00 | 31.9 | 202 | 15 | 31.3 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 32.3066 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.56 | 2003-07-08 | 16 | 31.7451 | 07/20 | 15:00 | 32.15 | 202 | 15 | 31.58 | 37810 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 34.5841 | 01-Oct | 24 | 34.94 | 2003-06-23 | 24 | 34.94 | 2004-06-24 | 24 | 35.0021 | 10/01 | 02:00 | 35 | 112 | 1 | 35 | 37732 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 33.7585 | 10-Jul | 13 | 32.78 | 2002-07-20 | 15 | 32.56 | 2004-07-20 | 16 | 32.8198 | 07/10 | 13:00 | 33 | 202 | 15 | 33.13 | 37812 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 27.1148 | 16-Sep | 15 | 27.56 | 2003-09-16 | 16 | 28.83 | 2002-09-18 | 16 | 26.9032 | 09/16 | 16:00 | 0 | 0 | 0 | 26.04 | 37848 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 26.8256 | 23-Oct | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0033 | 09/23 | 08:00 | 0 | 0 | 0 | 26.19 | 37928 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0033 | 09/23 | 08:00 | 0 | 0 | 0 | 26.23 | 37914 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 27.1992 | 01-Nov | 16 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0038 | 04/24 | 20:00 | 0 | 0 | 0 | 26.45 | 37917 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 27.0452 | 28-Apr | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0038 | 04/24 | 20:00 | 0 | 0 | 0 | 26.26 | 37917 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 25.8054 | 30-Apr | 15 | 25.11 | 2001-04-21 | 16 | 25.11 | 2001-04-21 | 16 | 25.0017 | 04/05 | 19:00 | 25.02 | 90 | 17 | 25 | 37691 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 26.1003 | 09-Jul | 15 | 25.11 | 2001-04-21 | 3 | 25.11 | 2001-04-21 | 3 | 25.0017 | 04/05 | 19:00 | 25.02 | 90 | 17 | 25 | 37735 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 16.1232 | 15-Aug | 15 | 16.11 | 2002-08-16 | 16 | 15.94 | 2004-07-10 | 16 | 15.2669 | 07/20 | 16:00 | 15.98 | 202 | 15 | 18.62 | 37776 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 21.0091 | 16-Jul | 15 | 20.11 | 2001-04-21 | 15 | 20.11 | 2003-04-21 | 15 | 20.0027 | 04/17 | 24:00 | 20.05 | 73 | 22 | 20.93 | 37732 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 36.08 | 10-Mai | 16 | 35.06 | 2003-04-21 | 16 | 35.06 | 2003-04-21 | 16 | 34.9964 | 03/11 | 12:00 | 35 | 71 | 10 | 35 | 37691 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 26.116 | 04-Jun | 15 | 25.06 | 2001-04-21 | 16 | 25.06 | 2001-04-21 | 16 | 25.0027 | 04/05 | 20:00 | 25.02 | 90 | 17 | 25 | 37691 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 16.1465 | 21-Sep | 16 | 15.11 | 2004-05-31 | 16 | 15.11 | 2004-05-31 | 16 | 15.0028 | 04/16 | 01:00 | 15.05 | 28 | 20 | 15 | 37691 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 35.6715 | 20-Jul | 15 | 35 | 2003-04-21 | 15 | 35 | 2004-04-21 | 15 | 35.0003 | 07/14 | 18:00 | 35 | 71 | 10 | 35 | 37691 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum IDB (°C)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7262 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 7.93 | 06-Jan | 6 | 10.83 | 2001-01-06 | 7 | 10.78 | 2001-01-06 | 7 | 7.7562 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7247 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7247 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7265 | 01/06 | 06:00 | 8 | 6 | 5 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 0 | 0 | 0 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 0 | 0 | 0 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 0 | 0 | 0 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 0 | 0 | 0 | 6.99 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 0 | 0 | 0 | 7 | 37627 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8363 | 12/21 | 01:00 | 8.54 | 355 | 20 | 24.04 | 37726 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8363 | 12/21 | 01:00 | 8.54 | 355 | 20 | 24.04 | 37726 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 8.3053 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.733 | 12/21 | 01:00 | 8.51 | 355 | 20 | 13.57 | 37926 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 8.4141 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.7911 | 12/21 | 01:00 | 8.54 | 355 | 20 | 15.98 | 37723 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 8.4442 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 8.9123 | 12/21 | 01:00 | 8.54 | 355 | 20 | 33.01 | 37712 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 8.4215 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9817 | 12/21 | 02:00 | 8.54 | 355 | 20 | 24.04 | 37726 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 8.2278 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.8775 | 12/21 | 01:00 | 8.51 | 355 | 20 | 14.95 | 37974 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 8.4486 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0584 | 12/21 | 02:00 | 8.54 | 355 | 20 | 33.01 | 37712 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Humidity Ratio (kg/kg)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 0.013284 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 | 0.013457 | 321 | 16 | 0.0134 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 0.01575 | 01-Oct | 23 | 0.0188 | 2002-10-15 | 9 | 0.0189 | 2002-10-15 | 9 | 0.015502 | 10/01 | 08:00 | 0.015432 | 276 | 8 | 0.0157 | 37896 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 0.018017 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0176 | 2002-07-10 | 12 | 0.017703 | 10/01 | 11:00 | 0.017547 | 192 | 12 | 0.0177 | 37812 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 0.017651 | 10-Jul | 12 | 0.0178 | 2003-10-02 | 9 | 0.0177 | 2002-07-10 | 13 | 0.017823 | 07/10 | 12:00 | 0.017045 | 192 | 13 | 0.0177 | 37812 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 0.017871 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0174 | 2002-07-10 | 12 | 0.017707 | 07/10 | 12:00 | 0.017272 | 192 | 13 | 0.0177 | 37812 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 0.016758 | 01-Oct | 24 | 0.0199 | 2002-08-02 | 22 | 0.0199 | 2002-08-02 | 22 | 0.016945 | 10/02 | 01:00 | 0.016479 | 276 | 2 | 0.0166 | 37896 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 0.013433 | 10-Jul | 13 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 | 0.013457 | 321 | 16 | 0.0134 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 0.016944 | 05-Apr | 22 | 0.017 | 2002-04-05 | 21 | 0.017 | 2003-04-05 | 21 | 0.016893 | 04/05 | 22:00 | 0 | 0 | 0 | 0.0173 | 37733 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 0.016835 | 05-Apr | 22 | 0.0169 | 2002-04-02 | 5 | 0.0169 | 2002-04-02 | 5 | 0.016431 | 04/06 | 05:00 | 0 | 0 | 0 | 0.0173 | 37733 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 0.014297 | 02-Apr | 10 | 0.0147 | 2003-04-01 | 21 | 0.0141 | 2002-04-17 | 3 | 0.014607 | 04/02 | 18:00 | 0 | 0 | 0 | 0.0147 | 37713 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 0.016231 | 02-Apr | 5 | 0.0156 | 2002-04-02 | 4 | 0.0156 | 2003-04-02 | 4 | 0.016146 | 04/02 | 05:00 | 0 | 0 | 0 | 0.0158 | 37713 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 0.013313 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 | 0 | 0 | 0 | 0.0134 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 0.01172 | 11-Jul | 15 | 0.0119 | 2004-07-20 | 15 | 0.0118 | 2004-04-06 | 10 | 0.01138 | 07/20 | 15:00 | 0.011713 | 202 | 15 | 0.0115 | 37691 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 0.011871 | 07-Sep | 15 | 0.0119 | 2001-07-20 | 15 | 0.0119 | 2001-07-20 | 15 | 0.01139 | 07/20 | 15:00 | 0.011716 | 202 | 15 | 0.0115 | 37691 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 0.0075403 | 07-Sep | 15 | 0.0077 | 2004-07-10 | 16 | 0.0078 | 2004-03-29 | 10 | 0.007104 | 07/20 | 16:00 | 0.007566 | 202 | 15 | 0.0106 | 37626 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 0.0094264 | 20-Jul | 16 | 0.0095 | 2003-06-04 | 15 | 0.0138 | 2004-04-06 | 10 | 0.0089745 | 07/20 | 15:00 | 0.009398 | 202 | 15 | 0.0107 | 37622 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 0.017932 | 10-Mai | 16 | 0.018 | 2004-07-20 | 15 | 0.018 | 2002-07-20 | 15 | 0.017848 | 07/20 | 15:00 | 0.017626 | 202 | 15 | 0.0173 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 0.0069892 | 01-Jan | 1 | 0.0081 | 2001-07-20 | 15 | 0.0081 | 2004-07-20 | 15 | 0.0067904 | 03/11 | 01:00 | 0.005491 | 92 | 1 | 0.00677 | 37920 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 0.006084 | 01-Jan | 1 | 0.005 | 2003-06-04 | 13 | 0.0063 | 2004-04-08 | 8 | 0.0067904 | 03/11 | 01:00 | 0.003256 | 92 | 1 | 0.00634 | 37691 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 0.0069892 | 01-Jan | 1 | 0.0122 | 2004-07-20 | 15 | 0.0122 | 2004-07-20 | 15 | 0.0067904 | 12/31 | 17:00 | 0.006689 | 92 | 1 | 0.00763 | 37930 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Humidity Ratio (kg/kg)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019435 | 01/05 | 07:00 | 0.002019 | 5 | 7 | 0.00196 | 37626 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019351 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 11 | 3 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0 | 0 | 0 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0 | 0 | 0 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0 | 0 | 0 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0 | 0 | 0 | 0.00197 | 37626 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0 | 0 | 0 | 0.00197 | 37626 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 0.0068276 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0069608 | 12/20 | 12:00 | 0.006908 | 355 | 20 | 0.0103 | 37927 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 0.0068276 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0069608 | 12/20 | 12:00 | 0.006908 | 355 | 20 | 0.0105 | 37713 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 0.006103 | 26-Nov | 2 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.006466 | 11/10 | 07:00 | 0.006525 | 332 | 23 | 0.00657 | 37926 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 0.0068215 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0069388 | 12/20 | 12:00 | 0.006908 | 355 | 20 | 0.00783 | 37713 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 0.0068356 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.006998 | 12/20 | 12:00 | 0.006909 | 355 | 20 | 0.0154 | 37927 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 0.006208 | 01-Apr | 1 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0064432 | 10/17 | 10:00 | 0.005454 | 306 | 21 | 0.00663 | 37712 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 0.0041096 | 05-Oct | 3 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0038106 | 10/17 | 10:00 | 0.003253 | 120 | 23 | 0.0042 | 37909 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 0.006208 | 01-Apr | 1 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 0.0067904 | 04/01 | 01:00 | 0.006685 | 202 | 15 | 0.007 | 37712 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Relative Humidity (%)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.7762 | 11/16 | 17:00 | 68 | 321 | 16 | 67.44 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 77.7029 | 02-Oct | 4 | 100.18 | 2002-10-15 | 9 | 100.7 | 2002-10-15 | 9 | 77.9255 | 10/02 | 08:00 | 77 | 164 | 8 | 78.19 | 37896 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 81.8358 | 18-Sep | 10 | 83.41 | 2004-10-02 | 9 | 83.67 | 2003-04-22 | 18 | 82.7149 | 09/18 | 10:00 | 83 | 247 | 17 | 81.88 | 37880 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 76.6591 | 22-Sep | 20 | 78.46 | 2004-10-02 | 9 | 77.94 | 2003-09-18 | 9 | 76.6386 | 09/22 | 20:00 | 76 | 162 | 18 | 78.7 | 37866 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 79.9293 | 18-Sep | 10 | 81.37 | 2004-09-18 | 9 | 81.26 | 2003-04-22 | 18 | 80.5452 | 09/18 | 10:00 | 80 | 247 | 17 | 80.25 | 37880 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 68.7892 | 16-Nov | 17 | 81.12 | 2003-08-07 | 21 | 81.12 | 2003-08-07 | 21 | 67.7762 | 11/16 | 17:00 | 70 | 276 | 8 | 72.65 | 37836 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.776 | 11/16 | 17:00 | 68 | 321 | 16 | 67.44 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 83.7534 | 05-Apr | 22 | 85.57 | 2002-04-05 | 21 | 85.57 | 2003-04-05 | 21 | 84.6321 | 04/05 | 22:00 | 0 | 0 | 0 | 86.31 | 37733 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 83.2247 | 05-Apr | 22 | 84.79 | 2002-04-02 | 5 | 84.79 | 2002-04-02 | 5 | 82.3688 | 04/06 | 01:00 | 0 | 0 | 0 | 86.18 | 37733 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 70.8411 | 02-Apr | 10 | 74.51 | 2003-04-17 | 7 | 71.53 | 2002-04-17 | 3 | 73.2771 | 04/02 | 18:00 | 0 | 0 | 0 | 73.85 | 37713 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 80.7087 | 02-Apr | 5 | 78.43 | 2002-04-02 | 4 | 78.43 | 2003-04-02 | 4 | 80.716 | 04/02 | 05:00 | 0 | 0 | 0 | 78.94 | 37713 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 68.7242 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.7762 | 11/16 | 17:00 | 0 | 0 | 0 | 67.51 | 37941 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 100 | 21-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 11/21 | 24:00 | 100 | 319 | 5 | 60.08 | 37712 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 100 | 21-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 11/21 | 24:00 | 100 | 319 | 5 | 57.51 | 37712 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 90.2299 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 93.6042 | 12/20 | 11:00 | 95 | 355 | 17 | 71.77 | 37849 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 100 | 18-Dec | 8 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 12/16 | 03:00 | 100 | 350 | 1 | 71.32 | 37716 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 100 | 12-Nov | 20 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 100 | 11/12 | 24:00 | 100 | 316 | 23 | 51.12 | 37712 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 91.0445 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 91.698 | 12/20 | 11:00 | 79 | 355 | 8 | 36.01 | 37731 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 61.275 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 54.8557 | 12/20 | 11:00 | 47 | 355 | 6 | 39.96 | 37729 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 90.8772 | 20-Dec | 22 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 96.074 | 12/20 | 11:00 | 97 | 355 | 4 | 24.14 | 37979 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Relative Humidity (%)
| TRNSYS | Date | Hour | DOE21E-J | Date | Hour | DOE21E-E | Date | Hour | EnargyPlus | Date | Hour | CODY | Date | Hour | HOT3000 | Date | Hour | YourData | Date | Hour | Extra | Date | Hour | Extra | Date | Hour
E300 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 311 | 5 | 14.94 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E310 | 13.3898 | 06-Nov | 6 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 15.471 | 11/06 | 08:00 | 16 | 311 | 8 | 15.93 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.7974 | 11/06 | 06:00 | 15 | 311 | 5 | 12.92 | 37975 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3879 | 11/06 | 06:00 | 15 | 311 | 5 | 14.94 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3879 | 11/06 | 06:00 | 15 | 311 | 5 | 14.94 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 311 | 5 | 14.94 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 311 | 5 | 14.94 | 37931 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400 | 13.209 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 | 0 | 0 | 0 | 14.57 | 37931 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410 | 13.2091 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.1877 | 11/06 | 06:00 | 0 | 0 | 0 | 14.58 | 37931 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420 | 13.2099 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 11/06 | 06:00 | 0 | 0 | 0 | 14.59 | 37931 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430 | 13.2078 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 | 0 | 0 | 0 | 14.58 | 37931 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440 | 13.2069 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 | 0 | 0 | 0 | 14.54 | 37931 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500 | 53.4054 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 53.4256 | 04/30 | 04:00 | 54 | 278 | 24 | 52.83 | 37899 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E510 | 52.0879 | 04-Oct | 23 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 53.5323 | 05/04 | 04:00 | 54 | 278 | 23 | 53.15 | 37745 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E520 | 61.2679 | 25-Nov | 24 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 61.1938 | 11/10 | 04:00 | 61 | 332 | 22 | 61.9 | 37822 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E522 | 58.5054 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 57.8308 | 04/30 | 04:00 | 60 | 278 | 23 | 57.97 | 37899 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E525 | 45.5284 | 30-Apr | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 46.1063 | 10/05 | 02:00 | 44 | 125 | 4 | 44.4 | 37899 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E530 | 29.5934 | 04-Jun | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 32.5613 | 04/18 | 18:00 | 28 | 92 | 10 | 33.68 | 37712 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E540 | 36.4749 | 21-Sep | 16 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 35.8475 | 09/28 | 18:00 | 31 | 92 | 1 | 39.74 | 37899 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E545 | 17.1244 | 20-Jul | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | 19.2467 | 04/18 | 17:00 | 19 | 92 | 10 | 20.14 | 37712 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DIFFERENCE COMPARISONS ("DELTA") START AT 1450
SENSITIVITY DIFFERENCE COMPARISONS ("DELTA")
Delta Total Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 4339.6026 | 4629 | 4629 | 4410.4348 | 4543.158 | 4538 | 0 | 0 | 0
E320-E300 | 4425.8798 | 3995 | 4037 | 4351.305 | 4424.404 | 4387 | 0 | 0 | 0
E330-E300 | 5329.5231 | 4958 | 4683 | 5445.065 | 5558.726 | 5260 | 0 | 0 | 0
E330-E320 | 903.6433 | 963 | 646 | 1093.76 | 1134.322 | 873 | 0 | 0 | 0
E340-E300 | 4985.5179 | 4608 | 4510 | 5047.6908 | 5088.85 | 4877 | 0 | 0 | 0
E330-E340 | 344.0053 | 350 | 173 | 397.3742 | 469.876 | 383 | 0 | 0 | 0
E350-E300 | -3396.7978 | -4203 | -4207 | -3647.5233 | -3389.819 | -3328 | 0 | 0 | 0
E360-E300 | 19665.0145 | 19314 | 19261 | 19920.5204 | 19866.847 | 19998 | 0 | 0 | 0
E400-E300 | -3588.6237 | -3904 | -3879 | -3758.0865 | -34976.411 | -3657 | 0 | 0 | 0
E410-E300 | -3555.3454 | -3082 | -3056 | -3013.2237 | -34976.411 | -3567 | 0 | 0 | 0
E420-E300 | -2246.7696 | -2220 | -1845 | -2045.1846 | -34976.411 | -1862 | 0 | 0 | 0
E430-E300 | -3095.7459 | -2818 | -2944 | -2938.2118 | -34976.411 | -3252 | 0 | 0 | 0
E440-E300 | -1942.4562 | -1718 | -1782 | -1738.9033 | -34976.411 | -1822 | 0 | 0 | 0
E500-E300 | -13295.8902 | -11933 | -11933 | -11947.9102 | -12653.458 | -11932 | 0 | 0 | 0
E510-E500 | 17217.9243 | 18099 | 18100 | 17760.3056 | 17414.1 | 17794 | 0 | 0 | 0
E525-E520 | -4665.708 | -4981 | -4969 | -5031.5465 | -4889.357 | -4458 | 0 | 0 | 0
E530-E500 | -5056.616 | -5277 | -5285 | -5081.8579 | -4880.485 | -5263 | 0 | 0 | 0
E545-E540 | -3743.2989 | -4076 | -4083 | -3514.133 | -3745.491 | -3825 | 0 | 0 | 0
Delta Compressor Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 3986.0911 | 4244 | 4244 | 4410.4348 | 4166.82 | 4177 | 0 | 0 | 0
E320-E300 | 4079.6031 | 3681 | 3721 | 4351.305 | 4076.025 | 4036 | 0 | 0 | 0
E330-E300 | 4946.1978 | 4603 | 4352 | 5445.065 | 5157.732 | 4899 | 0 | 0 | 0
E330-E320 | 866.5947 | 922 | 631 | 1093.76 | 1081.707 | 863 | 0 | 0 | 0
E340-E300 | 4609.403 | 4260 | 4172 | 5047.6908 | 4702.789 | 4524 | 0 | 0 | 0
E330-E340 | 336.7947 | 343 | 180 | 397.3742 | 454.943 | 375 | 0 | 0 | 0
E350-E300 | -3036.6939 | -3767 | -3772 | -3647.5233 | -3031.946 | -2985 | 0 | 0 | 0
E360-E300 | 17752.3056 | 17430 | 17382 | 19920.5204 | 17927.161 | 18065 | 0 | 0 | 0
E400-E300 | -3174.5856 | -3463 | -3442 | -3758.0865 | -21770.001 | -3247 | 0 | 0 | 0
E410-E300 | -3149.0399 | -2746 | -2723 | -3013.2237 | -21770.001 | -3191 | 0 | 0 | 0
E420-E300 | -1994.9489 | -1973 | -1639 | -2045.1846 | -21770.001 | -1662 | 0 | 0 | 0
E430-E300 | -2754.9132 | -2510 | -2622 | -2938.2118 | -21770.001 | -2910 | 0 | 0 | 0
E440-E300 | -1724.4011 | -1527 | -1584 | -1738.9033 | -21770.001 | -1627 | 0 | 0 | 0
E500-E300 | -4499.2388 | -3096 | -3095 | -3716.3612 | -3912.149 | -3354 | 0 | 0 | 0
E510-E500 | 13805.7311 | 14303 | 14304 | 15725.2175 | 13913.445 | 14230 | 0 | 0 | 0
E525-E520 | -2963.4018 | -3241 | -3233 | -4083.0918 | -3148.17 | -2742 | 0 | 0 | 0
E530-E500 | -4197.3004 | -4346 | -4354 | -4573.0283 | -4001.924 | -4350 | 0 | 0 | 0
E545-E540 | -2398.8748 | -2713 | -2720 | -2885.5257 | -2413.197 | -2449 | 0 | 0 | 0
Delta Condenser Fan Consumption |  |  | (kWh)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 353.5115 | 385 | 385 | 0 | 376.338 | 368 | 0 | 0 | 0
E320-E300 | 346.2767 | 314 | 316 | 0 | 348.379 | 358 | 0 | 0 | 0
E330-E300 | 383.3254 | 355 | 331 | 0 | 400.994 | 370 | 0 | 0 | 0
E330-E320 | 37.0487 | 41 | 15 | 0 | 52.615 | 12 | 0 | 0 | 0
E340-E300 | 376.1148 | 348 | 338 | 0 | 386.061 | 361 | 0 | 0 | 0
E330-E340 | 7.2105 | 7 | -7 | 0 | 14.933 | 9 | 0 | 0 | 0
E350-E300 | -360.1038 | -436 | -435 | 0 | -357.873 | -353 | 0 | 0 | 0
E360-E300 | 1912.7089 | 1884 | 1879 | 0 | 1939.686 | 1949 | 0 | 0 | 0
E400-E300 | -414.0381 | -441 | -437 | 0 | -2326.49 | -421 | 0 | 0 | 0
E410-E300 | -406.3054 | -336 | -333 | 0 | -2326.49 | -387 | 0 | 0 | 0
E420-E300 | -251.8207 | -247 | -206 | 0 | -2326.49 | -208 | 0 | 0 | 0
E430-E300 | -340.8327 | -308 | -322 | 0 | -2326.49 | -353 | 0 | 0 | 0
E440-E300 | -218.0552 | -191 | -198 | 0 | -2326.49 | -203 | 0 | 0 | 0
E500-E300 | -480.5531 | -326 | -327 | 0 | -414.621 | -347 | 0 | 0 | 0
E510-E500 | 1461.0219 | 1534 | 1534 | 0 | 1498.872 | 1526 | 0 | 0 | 0
E525-E520 | -728.888 | -752 | -750 | 0 | -745.624 | -733 | 0 | 0 | 0
E530-E500 | -367.939 | -395 | -395 | 0 | -376.185 | -391 | 0 | 0 | 0
E545-E540 | -575.6512 | -606 | -606 | 0 | -570.545 | -589 | 0 | 0 | 0
Delta ID Fan Consumption |  | (kWh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400-E300 | 0 | 0 | 0 | 0 | -10879.92 | 0 | 0 | 0 | 0
E410-E300 | 0 | 0 | 0 | 0 | -10879.92 | 0 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | 0 | -10879.92 | 0 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | 0 | -10879.92 | 0 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | 0 | -10879.92 | 0 | 0 | 0 | 0
E500-E300 | -8316.0984 | -8511 | -8511 | -8231.549 | -8326.688 | -8241 | 0 | 0 | 0
E510-E500 | 1951.1712 | 2262 | 2262 | 2035.088 | 2001.783 | 2038 | 0 | 0 | 0
E525-E520 | -973.4182 | -988 | -986 | -948.4547 | -995.563 | -979 | 0 | 0 | 0
E530-E500 | -491.3766 | -536 | -536 | -508.8296 | -502.376 | -522 | 0 | 0 | 0
E545-E540 | -768.7729 | -757 | -757 | -628.6074 | -761.749 | -787 | 0 | 0 | 0
Delta Total Coil Load |  | (kWh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 18915.2641 | 20111.3496 | 20120.1426 | 19017.6634 | 19551.277 | 19004 | 0 | 0 | 0
E320-E300 | 19364.8105 | 19072.8963 | 19201.2741 | 19104.8408 | 19396.718 | 18700 | 0 | 0 | 0
E330-E300 | 24586.004 | 23446.5345 | 23701.5315 | 25480.9315 | 25968.326 | 23751 | 0 | 0 | 0
E330-E320 | 5221.1935 | 4373.6382 | 4500.2574 | 6376.0907 | 6571.608 | 5051 | 0 | 0 | 0
E340-E300 | 22301.1114 | 21744.2097 | 21931.2075 | 22803.5302 | 22931.621 | 21496 | 0 | 0 | 0
E330-E340 | 2284.8926 | 1702.3248 | 1770.324 | 2677.4013 | 3036.705 | 2255 | 0 | 0 | 0
E350-E300 | -11038.8699 | -13547.082 | -13657.2876 | -11735.4503 | -10884.426 | -10868 | 0 | 0 | 0
E360-E300 | 82547.1951 | 82523.7705 | 82561.8735 | 83877.689 | 83455.59 | 83911 | 0 | 0 | 0
E400-E300 | -11634.0454 | -12365.889 | -12266.8212 | -11839.4983 | -77744.589 | -11359 | 0 | 0 | 0
E410-E300 | -11754.0136 | -10503.8247 | -10448.4288 | -10258.5757 | -77744.589 | -12082 | 0 | 0 | 0
E420-E300 | -7817.5601 | -7672.4787 | -6409.8039 | -7081.9071 | -77744.589 | -6454 | 0 | 0 | 0
E430-E300 | -10670.5555 | -9642.6969 | -10072.6746 | -10042.2431 | -77744.589 | -11057 | 0 | 0 | 0
E440-E300 | -6715.504 | -5903.3271 | -6110.8419 | -5967.8964 | -77744.589 | -6228 | 0 | 0 | 0
E500-E300 | -17069.7612 | -11287.5741 | -11299.5912 | -12740.6412 | -14639.223 | -12643 | 0 | 0 | 0
E510-E500 | 60530.8791 | 63325.1343 | 63324.8412 | 62439.2031 | 60539.443 | 62424 | 0 | 0 | 0
E525-E520 | -128.599 | -1172.1069 | -1170.3483 | -1184.9597 | -210.544 | -991 | 0 | 0 | 0
E530-E500 | -18311.2583 | -19361.5998 | -19361.5998 | -18600.8043 | -18229.952 | -18612 | 0 | 0 | 0
E545-E540 | -131.4753 | -890.1447 | -890.1447 | -846.3904 | -204.732 | -794 | 0 | 0 | 0
Delta Sensible Coil Load
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | -405.371 | 504.132 | 507.9423 | -100.4356 | -24.393 | -108 | 0 | 0 | 0
E320-E300 | 6197.4569 | 6900.1602 | 6942.0735 | 6585.5914 | 6799.339 | 7543 | 0 | 0 | 0
E330-E300 | 6421.6281 | 7514.2047 | 7522.9977 | 7908.0123 | 7439.994 | 6631 | 0 | 0 | 0
E330-E320 | 224.1712 | 614.0445 | 580.9242 | 1322.421 | 640.655 | -912 | 0 | 0 | 0
E340-E300 | 6370.8576 | 7256.5698 | 7305.8106 | 7225.3169 | 7171.095 | 6215 | 0 | 0 | 0
E330-E340 | 50.7704 | 257.6349 | 217.1871 | 682.6954 | 268.899 | 416 | 0 | 0 | 0
E350-E300 | -6290.9181 | -8112.4218 | -8128.2492 | -6830.4744 | -6620.663 | -6423 | 0 | 0 | 0
E360-E300 | 78315.0867 | 79122.9312 | 79134.9483 | 79545.0534 | 78996.242 | 79506 | 0 | 0 | 0
E400-E300 | -14709.3889 | -14377.7274 | -14367.762 | -14566.8442 | -55209.465 | -14010 | 0 | 0 | 0
E410-E300 | -10985.1029 | -8138.2146 | -8144.9559 | -8062.8549 | -55209.465 | -9606 | 0 | 0 | 0
E420-E300 | -6271.9238 | -6130.7727 | -5192.5596 | -5721.4244 | -55209.465 | -5207 | 0 | 0 | 0
E430-E300 | -8798.4022 | -8065.5258 | -8350.7121 | -8254.3534 | -55209.465 | -9048 | 0 | 0 | 0
E440-E300 | -5785.676 | -5204.2836 | -5312.7306 | -5165.0306 | -55209.465 | -5406 | 0 | 0 | 0
E500-E300 | -11617.9484 | -8147.0076 | -8158.7316 | -7808.6231 | -10335.24 | -7661 | 0 | 0 | 0
E510-E500 | 43046.1977 | 45710.1174 | 45709.8243 | 44950.3557 | 43050.834 | 45083 | 0 | 0 | 0
E525-E520 | -130.6037 | -883.9896 | -882.231 | -1187.4385 | -201.619 | -949 | 0 | 0 | 0
E530-E500 | 2.048 | -1076.2632 | -1075.9701 | -369.1301 | 0 | -528 | 0 | 0 | 0
E545-E540 | -130.4955 | -808.6629 | -808.6629 | -837.5233 | -201.642 | -792 | 0 | 0 | 0
Delta Latent Coil Load
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 19320.6351 | 19607.2176 | 19612.2003 | 19118.099 | 19575.693 | 19111 | 0 | 0 | 0
E320-E300 | 13167.3536 | 12172.7361 | 12259.2006 | 12519.2494 | 12597.449 | 11157 | 0 | 0 | 0
E330-E300 | 18164.3759 | 15932.3298 | 16178.5338 | 17572.9191 | 18528.23 | 17119 | 0 | 0 | 0
E330-E320 | 4997.0223 | 3759.5937 | 3919.3332 | 5053.6697 | 5930.781 | 5962 | 0 | 0 | 0
E340-E300 | 15930.2538 | 14487.6399 | 14625.3969 | 15578.2133 | 15760.481 | 15279 | 0 | 0 | 0
E330-E340 | 2234.1221 | 1444.6899 | 1553.1369 | 1994.7059 | 2767.749 | 1840 | 0 | 0 | 0
E350-E300 | -4747.9518 | -5434.6602 | -5529.0384 | -4904.9759 | -4263.749 | -4446 | 0 | 0 | 0
E360-E300 | 4232.1084 | 3400.8393 | 3426.9252 | 4332.6356 | 4459.339 | 4403 | 0 | 0 | 0
E400-E300 | 3075.3436 | 2011.8384 | 2100.9408 | 2727.3459 | -22535.143 | 2650 | 0 | 0 | 0
E410-E300 | -768.9108 | -2365.6101 | -2303.4729 | -2195.7208 | -22535.143 | -2477 | 0 | 0 | 0
E420-E300 | -1545.6363 | -1541.706 | -1217.2443 | -1360.4828 | -22535.143 | -1212 | 0 | 0 | 0
E430-E300 | -1872.1533 | -1577.1711 | -1721.9625 | -1787.8897 | -22535.143 | -2010 | 0 | 0 | 0
E440-E300 | -929.828 | -699.0435 | -798.1113 | -802.8657 | -22535.143 | -823 | 0 | 0 | 0
E500-E300 | -5451.8128 | -3140.5665 | -3140.8596 | -4932.0181 | -4304.002 | -4983 | 0 | 0 | 0
E510-E500 | 17484.6814 | 17615.0169 | 17615.0169 | 17488.8475 | 17488.438 | 17340 | 0 | 0 | 0
E525-E520 | 2.0047 | -288.1173 | -288.1173 | 2.4788 | -8.624 | -42 | 0 | 0 | 0
E530-E500 | -18313.3062 | -18285.3366 | -18285.6297 | -18231.6742 | -18229.955 | -18084 | 0 | 0 | 0
E545-E540 | -0.97976 | -81.4818 | -81.4818 | -8.8672 | -3.086 | -2 | 0 | 0 | 0
Delta Mean COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.16552 | 0.1798 | 0.18013 | 0.16518 | 0.17086 | 0.15 | 0 | 0 | 0
E320-E300 | 0.17083 | 0.22029 | 0.21969 | 0.1753 | 0.17958 | 0.16 | 0 | 0 | 0
E330-E300 | 0.24166 | 0.25649 | 0.29907 | 0.26442 | 0.2709 | 0.23 | 0 | 0 | 0
E330-E320 | 0.070831 | 0.036201 | 0.079382 | 0.089118 | 0.091321 | 0.07 | 0 | 0 | 0
E340-E300 | 0.20521 | 0.23966 | 0.25826 | 0.22045 | 0.22316 | 0.19 | 0 | 0 | 0
E330-E340 | 0.036452 | 0.016833 | 0.040815 | 0.043961 | 0.047744 | 0.04 | 0 | 0 | 0
E350-E300 | -0.00011501 | 0.003096 | -0.0019178 | 0.0043635 | 0.0025325 | 0 | 0 | 0 | 0
E360-E300 | 0.41996 | 0.46293 | 0.46845 | 0.43775 | 0.44031 | 0.43 | 0 | 0 | 0
E400-E300 | 0.0012106 | 0.013724 | 0.014548 | 0.016855 | -3.2264 | 0.03 | 0 | 0 | 0
E410-E300 | -0.0095511 | -0.025269 | -0.026661 | -0.023168 | -3.2264 | -0.02 | 0 | 0 | 0
E420-E300 | -0.023 | -0.022394 | -0.019831 | -0.020419 | -3.2264 | -0.02 | 0 | 0 | 0
E430-E300 | -0.02827 | -0.024649 | -0.025889 | -0.024351 | -3.2264 | -0.02 | 0 | 0 | 0
E440-E300 | -0.017725 | -0.015393 | -0.015474 | -0.01474 | -3.2264 | -0.01 | 0 | 0 | 0
E500-E300 | -0.045013 | -0.010183 | -0.010822 | -0.033871 | -0.034365 | -0.03 | 0 | 0 | 0
E510-E500 | 0.40948 | 0.41598 | 0.41577 | 0.40814 | 0.39713 | 0.41 | 0 | 0 | 0
E525-E520 | 0.58247 | 0.57414 | 0.57204 | 0.57773 | 0.60629 | 0.49 | 0 | 0 | 0
E530-E500 | -0.24223 | -0.25849 | -0.25718 | -0.24762 | -0.27645 | -0.22 | 0 | 0 | 0
E545-E540 | 0.5601 | 0.55853 | 0.56036 | 0.46974 | 0.54604 | 0.51 | 0 | 0 | 0
Delta Mean IDB
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.1313 | 0.055556 | 0 | 0.0023647 | 0.0080616 | 0.02 | 0 | 0 | 0
E320-E300 | 0.27622 | 0.33333 | 0.33333 | 0.14305 | 0.24571 | 0.54 | 0 | 0 | 0
E330-E300 | 0.25545 | 0.22222 | 0.22222 | 0.20615 | 0.21382 | 0.19 | 0 | 0 | 0
E330-E320 | -0.02077 | -0.11111 | -0.11111 | 0.063101 | -0.031885 | -0.35 | 0 | 0 | 0
E340-E300 | 0.25135 | 0.22222 | 0.22222 | 0.22139 | 0.22722 | 0.22 | 0 | 0 | 0
E330-E340 | 0.0041016 | 0 | 0 | -0.015241 | -0.013394 | -0.03 | 0 | 0 | 0
E350-E300 | 2.0352 | 2.1111 | 2.1111 | 2.1477 | 2.187 | 2.16 | 0 | 0 | 0
E360-E300 | 1.7407 | 1.5556 | 1.5 | 1.342 | 1.3992 | 1.38 | 0 | 0 | 0
E400-E300 | 0.50202 | 0 | 0 | 0.0013587 | -24.0816 | 0 | 0 | 0 | 0
E410-E300 | 0.49787 | 0 | 0 | -0.00011132 | -24.0816 | 0 | 0 | 0 | 0
E420-E300 | 0.3019 | 0 | 0 | -6.2527e-05 | -24.0816 | 0 | 0 | 0 | 0
E430-E300 | 0.36731 | 0 | 0 | -6.9725e-05 | -24.0816 | 0 | 0 | 0 | 0
E440-E300 | 0.2875 | 0 | 0 | -3.3826e-05 | -24.0816 | 0 | 0 | 0 | 0
E500-E300 | -3.3901 | -3.3889 | -3.5 | -3.6854 | -2.9838 | -1.13 | 0 | 0 | 0
E510-E500 | 1.2445 | 0.11111 | 0.11111 | -0.022969 | 0 | 0 | 0 | 0 | 0
E525-E520 | 13.3272 | 13.6111 | 13.5556 | 13.5028 | 13.6289 | 15.8 | 0 | 0 | 0
E530-E500 | -0.20888 | -0.055556 | 0 | 0.1914 | 0 | 0 | 0 | 0 | 0
E545-E540 | 13.3159 | 13.5556 | 13.5556 | 13.5202 | 13.576 | 15.71 | 0 | 0 | 0
Delta Mean Humidity Ratio
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.0020018 | 0.0021 | 0.0021 | 0.0019881 | 0.0019998 | 0.0019 | 0 | 0 | 0
E320-E300 | 0.00091896 | 0.0009 | 0.0009 | 0.0008715 | 0.00087438 | 0.0007 | 0 | 0 | 0
E330-E300 | 0.00067186 | 0.0007 | 0.0007 | 0.00071519 | 0.00063678 | 0.0007 | 0 | 0 | 0
E330-E320 | -0.00024709 | -0.0002 | -0.0002 | -0.00015631 | -0.00023759 | 0 | 0 | 0 | 0
E340-E300 | 0.00072232 | 0.0007 | 0.0007 | 0.00073675 | 0.00069351 | 0.0007 | 0 | 0 | 0
E330-E340 | -5.0461e-05 | 0 | 0 | -2.1555e-05 | -5.6729e-05 | 0 | 0 | 0 | 0
E350-E300 | 0.00063685 | 0.0008 | 0.0008 | 0.00063099 | 0.00058373 | 0.00057 | 0 | 0 | 0
E360-E300 | -0.0005696 | -0.0005 | -0.0005 | -0.00055909 | -0.00062237 | -0.00062 | 0 | 0 | 0
E400-E300 | 0.00073206 | 0.0008 | 0.0008 | 0.00087651 | -0.0091748 | 0.0008 | 0 | 0 | 0
E410-E300 | 0.00067139 | 0.0003 | 0.0003 | 0.0003169 | -0.0091748 | 0.0003 | 0 | 0 | 0
E420-E300 | 0.00019481 | 0.0002 | 0.0002 | 0.00018218 | -0.0091748 | 0.0001 | 0 | 0 | 0
E430-E300 | 0.00024119 | 0.0002 | 0.0002 | 0.00022163 | -0.0091748 | 0.0002 | 0 | 0 | 0
E440-E300 | 8.8738e-05 | 0.0001 | 0.0001 | 6.5316e-05 | -0.0091748 | 0 | 0 | 0 | 0
E500-E300 | 0.00070622 | -0.0092 | -0.0092 | -1.9753e-05 | 0.0010435 | 0.0015 | 0 | 0 | 0
E510-E500 | 0.00037457 | 0 | 0 | 8.3769e-06 | -8.8998e-07 | 0 | 0 | 0 | 0
E525-E520 | 0.0070203 | 0 | 0 | 0.0073646 | 0.0069569 | 0.00747 | 0 | 0 | 0
E530-E500 | -0.0035488 | 0 | 0 | -0.0026609 | -0.0044208 | -0.00403 | 0 | 0 | 0
E545-E540 | 0.0017664 | 0 | 0 | 0.0024077 | 0.0028945 | 0.00259 | 0 | 0 | 0
Delta Mean Relative Humidity
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 9.7158 | 10.25 | 10.25 | 10.0163 | 10.0148 | 9.87 | 0 | 0 | 0
E320-E300 | 3.3904 | 2.95 | 2.97 | 3.5083 | 3.2773 | 2.01 | 0 | 0 | 0
E330-E300 | 2.2296 | 2.32 | 2.37 | 2.6617 | 2.2587 | 2.77 | 0 | 0 | 0
E330-E320 | -1.1608 | -0.63 | -0.6 | -0.84659 | -1.0186 | 0.76 | 0 | 0 | 0
E340-E300 | 2.4702 | 2.43 | 2.45 | 2.7026 | 2.4705 | 2.85 | 0 | 0 | 0
E330-E340 | -0.24056 | -0.11 | -0.08 | -0.040899 | -0.21187 | -0.08 | 0 | 0 | 0
E350-E300 | -3.1309 | -2.81 | -2.73 | -3.3505 | -3.5099 | -3.37 | 0 | 0 | 0
E360-E300 | -7.5814 | -6.77 | -6.79 | -6.581 | -6.9551 | -6.72 | 0 | 0 | 0
E400-E300 | 2.156 | 3.95 | 3.97 | 4.3298 | -47.8261 | 4.08 | 0 | 0 | 0
E410-E300 | 1.8822 | 1.39 | 1.35 | 1.5714 | -47.8261 | 1.82 | 0 | 0 | 0
E420-E300 | 0.16451 | 0.88 | 0.69 | 0.90472 | -47.8261 | 0.83 | 0 | 0 | 0
E430-E300 | 0.20708 | 0.91 | 1.02 | 1.0997 | -47.8261 | 1.24 | 0 | 0 | 0
E440-E300 | -0.28509 | 0.2 | 0.29 | 0.32416 | -47.8261 | 0.3 | 0 | 0 | 0
E500-E300 | 17.9113 | -48.26 | -48.28 | 9.9915 | 18.1158 | 15.8 | 0 | 0 | 0
E510-E500 | -2.3476 | -0.11 | -0.11 | 0.11782 | -0.010621 | 0.11 | 0 | 0 | 0
E525-E520 | -8.4071 | 0 | 0 | -7.2115 | -10.0881 | -14.8 | 0 | 0 | 0
E530-E500 | -19.7962 | 0 | 0 | -10.4047 | -24.4903 | -24.13 | 0 | 0 | 0
E545-E540 | -11.8961 | 0 | 0 | -7.5469 | -3.1763 | -14.62 | 0 | 0 | 0
Hourly Integrated Maxima and Minima Sensitivities
Delta Max Compressor+ODfan+IDfan Consumption
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 968.3645 | 1019 | 993 | 576.3704 | 721 | 614 | 0 | 0 | 0
E320-E300 | 1402.1615 | 1352 | 1379 | 993.1303 | 1172 | 1327 | 0 | 0 | 0
E330-E300 | 1720.664 | 1648 | 1805 | 1360.526 | 1535 | 1787 | 0 | 0 | 0
E330-E320 | 318.5024 | 296 | 426 | 367.3957 | 363 | 460 | 0 | 0 | 0
E340-E300 | 1554.8648 | 1594 | 1588 | 1179.2169 | 1345 | 1553 | 0 | 0 | 0
E330-E340 | 165.7992 | 54 | 217 | 181.3091 | 190 | 234 | 0 | 0 | 0
E350-E300 | 0.85194 | 90 | 0 | -0.0072418 | 0 | -2 | 0 | 0 | 0
E360-E300 | 1143.4651 | 1172 | 1124 | 780.7195 | 931 | 1214 | 0 | 0 | 0
E400-E300 | 1.8307 | 0 | 75 | -0.01154 | -11932 | -29 | 0 | 0 | 0
E410-E300 | 1.8307 | 0 | 0 | 0 | -11932 | 1 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | 0 | -11932 | 0 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | 1.0004e-10 | -11932 | 0 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | 1.0004e-10 | -11932 | -87 | 0 | 0 | 0
E500-E300 | -1459.5539 | -1133 | -1177 | -1557.1915 | -1755 | -1274 | 0 | 0 | 0
E510-E500 | 1038.4136 | 1159 | 1162 | 1012.234 | 1009 | 1070 | 0 | 0 | 0
E525-E520 | -1668.6417 | -1451 | -1483 | -1673.579 | -1625 | -1099 | 0 | 0 | 0
E530-E500 | -2138.1546 | -2372 | -2370 | -2145.4765 | -2185 | -2185 | 0 | 0 | 0
E545-E540 | -1494.1291 | -1593 | -1593 | -1308.4538 | -1495 | -1514 | 0 | 0 | 0
Delta Sensible Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | -183.1 | -123 | -86 | -318.1104 | -379 | -259 | 0 | 0 | 0
E320-E300 | 8038.2 | 7916 | 7867 | 8065.5499 | 7677 | 8059 | 0 | 0 | 0
E330-E300 | 9948.7 | 10207 | 11285 | 11229.0176 | 10540 | 10513 | 0 | 0 | 0
E330-E320 | 1910.5 | 2291 | 3418 | 3163.4677 | 2863 | 2454 | 0 | 0 | 0
E340-E300 | 9551.5 | 8883 | 8881 | 9273.9256 | 9483 | 9272 | 0 | 0 | 0
E330-E340 | 397.2 | 1324 | 2404 | 1955.092 | 1057 | 1241 | 0 | 0 | 0
E350-E300 | 0.1 | 0 | 0 | -0.039522 | 0 | -32 | 0 | 0 | 0
E360-E300 | 8783.3 | 8908 | 8860 | 8946.1221 | 8524 | 9271 | 0 | 0 | 0
E400-E300 | 0.1 | 0 | 0 | -0.05333 | -23457 | -31 | 0 | 0 | 0
E410-E300 | -11.7 | 0 | 0 | -3.3106e-10 | -23457 | -15 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | 2.9104e-11 | -23457 | -15 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | 5.0204e-10 | -23457 | -15 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | 3.0559e-10 | -23457 | -33 | 0 | 0 | 0
E500-E300 | -3728.2 | -3194 | -3197 | -3667.2651 | -4681 | -3090 | 0 | 0 | 0
E510-E500 | 2180 | 2504 | 2505 | 2432.0566 | 2345 | 2451 | 0 | 0 | 0
E525-E520 | 286.8 | -309 | -304 | -413.5213 | -210 | -717 | 0 | 0 | 0
E530-E500 | 284.9 | -433 | -433 | -139.7703 | 0 | -192 | 0 | 0 | 0
E545-E540 | 500.2 | -291 | -292 | -273.7041 | -35 | -302 | 0 | 0 | 0
Delta Latent Coil Load (Wh,th)
| TUD0302 | "NREL0702 | "NREL0102 | Gard0702 | UR0702 | UR0702 | UR0702
E310-E300 | 6271.3 | 5835 | 5876 | 6049.2222 | 5737 | 5685 | 0 | 0 | 0
E320-E300 | 13511.6 | 22193 | 22109 | 12161.09 | 11322 | 11537 | 0 | 0 | 0
E330-E300 | 18189.5 | 17637 | 31415 | 17001.6155 | 17809 | 17096 | 0 | 0 | 0
E330-E320 | 4677.9 | -4556 | 9306 | 4840.5255 | 6487 | 5559 | 0 | 0 | 0
E340-E300 | 15212.6 | 21147 | 26617 | 13840.6802 | 13850 | 13402 | 0 | 0 | 0
E330-E340 | 2976.9 | -3510 | 4798 | 3160.9352 | 3959 | 3694 | 0 | 0 | 0
E350-E300 | 115.56 | -1 | -1 | 0.55759 | 380 | 1211 | 0 | 0 | 0
E360-E300 | -360.54 | 722 | 942 | -1687.8651 | -1516 | -1458 | 0 | 0 | 0
E400-E300 | 17439.6 | 16274 | 23002 | 16172.5916 | -10375 | 16253 | 0 | 0 | 0
E410-E300 | 1503.2 | 0 | -3 | 5.457e-11 | -10375 | -15 | 0 | 0 | 0
E420-E300 | 115.34 | 0 | 0 | -1.3824e-10 | -10375 | 2 | 0 | 0 | 0
E430-E300 | 0 | 1801 | 1707 | 780.2398 | -10375 | 2 | 0 | 0 | 0
E440-E300 | 0 | 0 | -3 | -8.3674e-11 | -10375 | -253 | 0 | 0 | 0
E500-E300 | -1670.24 | -1571 | -1661 | -2686.1278 | -2570 | -2630 | 0 | 0 | 0
E510-E500 | 927.1 | 990 | 990 | 1132.0803 | 1045 | 1112 | 0 | 0 | 0
E525-E520 | 123.37 | -122 | -122 | 221.1694 | 212 | -144 | 0 | 0 | 0
E530-E500 | -7965.46 | -7733 | -7733 | -7798.7789 | -7626 | -7726.1 | 0 | 0 | 0
E545-E540 | -627.186 | 0 | 0 | -1636.359 | -841 | -1181 | 0 | 0 | 0
Delta Sensible+Latent Coil Load (Wh,th)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 5153.95 | 5349 | 5578 | 4315.0471 | 4759 | 4919 | 0 | 0 | 0
E320-E300 | 8143.55 | 22412 | 22368 | 7039.5416 | 7402 | 7848 | 0 | 0 | 0
E330-E300 | 11317.95 | 12227 | 33117 | 10540.4711 | 11476 | 10343 | 0 | 0 | 0
E330-E320 | 3174.4 | -10185 | 10749 | 3500.9295 | 4074 | 2495 | 0 | 0 | 0
E340-E300 | 9477.65 | 19418 | 28094 | 8550.9999 | 8864 | 9060 | 0 | 0 | 0
E330-E340 | 1840.3 | -7191 | 5023 | 1989.4712 | 2612 | 1283 | 0 | 0 | 0
E350-E300 | -82.32 | 0 | -1 | -0.025077 | 0 | 5 | 0 | 0 | 0
E360-E300 | 6683.11 | 9212 | 9564 | 5634.0125 | 5820 | 6379 | 0 | 0 | 0
E400-E300 | 9004.55 | 9142 | 18383 | 8054.7322 | -32502 | 8702 | 0 | 0 | 0
E410-E300 | -82.32 | 0 | 0 | 0 | -32502 | 1 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | 0 | -32502 | 0 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | 2.7649e-10 | -32502 | 0 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | 2.7649e-10 | -32502 | -295 | 0 | 0 | 0
E500-E300 | -4688.54 | -3694 | -3749 | -5401.0537 | -5935 | -4517 | 0 | 0 | 0
E510-E500 | 3107.54 | 3481 | 3482 | 3538.1292 | 3381 | 3542 | 0 | 0 | 0
E525-E520 | 410.17 | -412 | -412 | -166.7296 | 8 | -881 | 0 | 0 | 0
E530-E500 | -7651.41 | -8131 | -8131 | -8000.2799 | -7791 | -7929 | 0 | 0 | 0
E545-E540 | 500.2 | -291 | -292 | -273.7041 | -30 | -302 | 0 | 0 | 0
Delta Max COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | -0.025037 | 0.272 | 0.271 | 0.27226 | 0.25703 | 0.24 | 0 | 0 | 0
E320-E300 | 0 | 1.274 | 1.11 | 0.041596 | 0.072694 | 0.5 | 0 | 0 | 0
E330-E300 | 0 | 0.24 | 1.738 | 0.17299 | 0.25134 | 0.17 | 0 | 0 | 0
E330-E320 | 0 | -1.034 | 0.628 | 0.13139 | 0.17864 | -0.33 | 0 | 0 | 0
E340-E300 | 0 | 0.752 | 1.482 | 0.091522 | 0.14655 | 0.07 | 0 | 0 | 0
E330-E340 | 0 | -0.512 | 0.256 | 0.081466 | 0.10479 | 0.1 | 0 | 0 | 0
E350-E300 | 0 | 0.02 | 0.006 | 0.42216 | 0.061488 | 0 | 0 | 0 | 0
E360-E300 | 0.23263 | 0.559 | 0.57 | 0.50758 | 0.5614 | 0.56 | 0 | 0 | 0
E400-E300 | -0.091398 | 0.219 | 0.919 | 0.17297 | -3.8706 | 0.17 | 0 | 0 | 0
E410-E300 | -0.28043 | 0.034 | -0.002 | 0.11717 | -3.8706 | -0.04 | 0 | 0 | 0
E420-E300 | -0.38705 | -0.062 | -0.098 | -0.078559 | -3.8706 | 0.06 | 0 | 0 | 0
E430-E300 | -0.38705 | -0.064 | -0.098 | -0.11877 | -3.8706 | 0.05 | 0 | 0 | 0
E440-E300 | -0.28486 | -0.095 | -0.098 | -0.11877 | -3.8706 | -0.07 | 0 | 0 | 0
E500-E300 | 0.1068 | 3.498 | 1.444 | 0.31113 | 0.31401 | 0.26 | 0 | 0 | 0
E510-E500 | 0.4174 | 0 | 0 | 0.47259 | 0.50496 | 0.39 | 0 | 0 | 0
E525-E520 | 0.90402 | 1.429 | 1.379 | 0.83955 | 0.83633 | 0.56 | 0 | 0 | 0
E530-E500 | -0.26907 | -3.386 | -1.451 | -0.31413 | -0.34458 | -0.26 | 0 | 0 | 0
E545-E540 | 0.79448 | 0.819 | 0.973 | 0.69873 | 0.48982 | 0.48 | 0 | 0 | 0
Delta Min COP2
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.072169 | 0.052 | 0.05 | 0.092733 | 0.087015 | 0.06 | 0 | 0 | 0
E320-E300 | 0.032137 | 0.003 | 0.004 | 0.048689 | 0.028893 | 0.02 | 0 | 0 | 0
E330-E300 | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0 | 0 | 0
E330-E320 | 0 | -0.003 | -0.004 | 0.0054718 | 0.0088028 | 0.01 | 0 | 0 | 0
E340-E300 | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0 | 0 | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300 | -0.0026372 | 0 | 0 | -8.3391e-08 | 0.00027963 | 0 | 0 | 0 | 0
E360-E300 | 0.032137 | 0.001 | 0 | 0.054163 | 0.037696 | 0.03 | 0 | 0 | 0
E400-E300 | -0.011155 | -0.064 | -0.066 | -4.2365e-07 | -2.7856 | 0 | 0 | 0 | 0
E410-E300 | -0.0072339 | 0 | 0 | -2.5567e-07 | -2.7856 | 0 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | 0 | -2.7856 | 0 | 0 | 0 | 0
E430-E300 | -0.021929 | -0.064 | -0.066 | 4.885e-15 | -2.7856 | 0 | 0 | 0 | 0
E440-E300 | -0.010585 | -0.064 | -0.066 | 0 | -2.7856 | 0 | 0 | 0 | 0
E500-E300 | -0.10787 | -0.105 | -0.149 | -0.079652 | -0.11916 | -0.1 | 0 | 0 | 0
E510-E500 | 0.20276 | 0.124 | 0 | 0.20451 | 0.21527 | 0.19 | 0 | 0 | 0
E525-E520 | 0.46939 | 0.476 | 0.42 | 0.47145 | 0.56074 | 0.43 | 0 | 0 | 0
E530-E500 | -0.18393 | -0.198 | -0.154 | -0.20025 | -0.19318 | -0.19 | 0 | 0 | 0
E545-E540 | 0.4795 | 0.459 | 0.46 | 0.37917 | 0.54916 | 0.44 | 0 | 0 | 0
Delta Max IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.8779 | 1.78 | 1.61 | 1.5534 | 1.57 | 1 | 0 | 0 | 0
E320-E300 | 6.1605 | 6.5 | 6.39 | 6.8407 | 7.27 | 5.46 | 0 | 0 | 0
E330-E300 | 6.0322 | 6.61 | 6.89 | 6.493 | 6.85 | 5.11 | 0 | 0 | 0
E330-E320 | -0.1283 | 0.11 | 0.5 | -0.34771 | -0.42 | -0.35 | 0 | 0 | 0
E340-E300 | 6.1067 | 6.5 | 6.45 | 6.7419 | 7.1 | 5.39 | 0 | 0 | 0
E330-E340 | -0.0745 | 0.11 | 0.44 | -0.24889 | -0.25 | -0.28 | 0 | 0 | 0
E350-E300 | 8.3842 | 9.83 | 9.83 | 9.9988 | 9.95 | 8.81 | 0 | 0 | 0
E360-E300 | 7.5586 | 7.67 | 7.45 | 7.8165 | 7.95 | 6.94 | 0 | 0 | 0
E400-E300 | 0.9149 | 2.45 | 3.72 | 1.8999 | -25.05 | -0.15 | 0 | 0 | 0
E410-E300 | 0.6257 | 0 | 0 | -2.694e-10 | -25.05 | 0 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | -1.56e-11 | -25.05 | 0.04 | 0 | 0 | 0
E430-E300 | 0.9993 | 0 | 0 | 0.00048996 | -25.05 | 0.26 | 0 | 0 | 0
E440-E300 | 0.8453 | 0 | 0 | 0.00048996 | -25.05 | 0.07 | 0 | 0 | 0
E500-E300 | -0.3945 | 0 | 0 | -0.001584 | -0.03 | -1.19 | 0 | 0 | 0
E510-E500 | 0.2949 | 0 | 0 | 8.488e-07 | 0 | 0 | 0 | 0 | 0
E525-E520 | 19.9568 | 18.95 | 19.12 | 19.7296 | 19.02 | 16.38 | 0 | 0 | 0
E530-E500 | 0.3106 | -0.05 | -0.05 | 0.0010308 | 0 | 0 | 0 | 0 | 0
E545-E540 | 19.525 | 19.89 | 19.89 | 19.9975 | 19.95 | 20 | 0 | 0 | 0
Delta Min IDB (°C)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0 | 0 | 0 | -7.6877e-05 | 0 | 0 | 0 | 0 | 0
E320-E300 | 0 | 1.94 | 1.95 | -0.97006 | 0 | 0 | 0 | 0 | 0
E330-E300 | 0 | 0 | 0 | -0.0015637 | 0 | 0 | 0 | 0 | 0
E330-E320 | 0 | -1.94 | -1.95 | 0.96849 | 0 | 0 | 0 | 0 | 0
E340-E300 | 0 | 0 | 0 | -0.0015637 | 0 | 0 | 0 | 0 | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300 | 0 | 0 | 0 | 0.00017992 | 0 | 0 | 0 | 0 | 0
E400-E300 | 0 | 0 | 0 | -3.0198e-14 | -8 | 0 | 0 | 0 | 0
E410-E300 | 0 | 0 | 0 | -3.0198e-14 | -8 | 0 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | -3.0198e-14 | -8 | 0 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | -3.0198e-14 | -8 | 0 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | -3.0198e-14 | -8 | 0.01 | 0 | 0 | 0
E500-E300 | 0.49703 | -0.72 | -0.89 | 0.11004 | 0.54 | 17.05 | 0 | 0 | 0
E510-E500 | 0 | 0 | 0 | 9.3018e-09 | 0 | 0 | 0 | 0 | 0
E525-E520 | 0.13889 | 0.06 | 0.05 | 0.17939 | 0.03 | 19.44 | 0 | 0 | 0
E530-E500 | -0.00551 | 0 | 0 | 0.14539 | 0 | 0 | 0 | 0 | 0
E545-E540 | 0.22078 | 0.06 | 0.05 | 0.18093 | 0.03 | 18.06 | 0 | 0 | 0
Delta Max Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.0024658 | 0.005 | 0.0052 | 0.0019812 | 0.001975 | 0.0023 | 0 | 0 | 0
E320-E300 | 0.0047326 | 0.0039 | 0.0039 | 0.0041823 | 0.00409 | 0.0043 | 0 | 0 | 0
E330-E300 | 0.0043671 | 0.004 | 0.004 | 0.004303 | 0.003588 | 0.0043 | 0 | 0 | 0
E330-E320 | -0.0003655 | 0.0001 | 0.0001 | 0.00012066 | -0.000502 | 0 | 0 | 0 | 0
E340-E300 | 0.0045871 | 0.0039 | 0.0037 | 0.0041869 | 0.003815 | 0.0043 | 0 | 0 | 0
E330-E340 | -0.00022 | 0.0001 | 0.0003 | 0.00011606 | -0.000227 | 0 | 0 | 0 | 0
E350-E300 | 0.0034739 | 0.0061 | 0.0062 | 0.0034245 | 0.003022 | 0.0032 | 0 | 0 | 0
E360-E300 | 0.0001491 | 0 | 0 | -3.5233e-08 | 0 | 0 | 0 | 0 | 0
E400-E300 | 0.0036593 | 0.0032 | 0.0033 | 0.0033728 | -0.013457 | 0.0039 | 0 | 0 | 0
E410-E300 | 0.0035512 | 0.0031 | 0.0032 | 0.002911 | -0.013457 | 0.0039 | 0 | 0 | 0
E420-E300 | 0.0010125 | 0.0009 | 0.0004 | 0.0010861 | -0.013457 | 0.0013 | 0 | 0 | 0
E430-E300 | 0.0029463 | 0.0018 | 0.0019 | 0.0026257 | -0.013457 | 0.0024 | 0 | 0 | 0
E440-E300 | 2.85e-05 | 0 | 0 | 1.6639e-12 | -0.013457 | 0 | 0 | 0 | 0
E500-E300 | -0.0015646 | -0.0019 | -0.0019 | -0.0021408 | -0.001744 | -0.0019 | 0 | 0 | 0
E510-E500 | 0.0001517 | 0 | 0.0001 | 1.0006e-05 | 3e-06 | 0 | 0 | 0 | 0
E525-E520 | 0.010392 | 0.0103 | 0.0102 | 0.010744 | 0.01006 | 0.0067 | 0 | 0 | 0
E530-E500 | -0.0047305 | -0.0038 | -0.0037 | -0.0045893 | -0.006222 | -0.00473 | 0 | 0 | 0
E545-E540 | 0.0009051 | 0.0072 | 0.0059 | 4.3897e-15 | 0.003433 | 0.00129 | 0 | 0 | 0
Delta Min Humidity Ratio (kg/kg)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 1e-08 | 0 | 0 | 1.4269e-05 | 5.1e-05 | -1e-05 | 0 | 0 | 0
E320-E300 | 0 | 0 | 0 | 5.8778e-06 | 0 | 0 | 0 | 0 | 0
E330-E300 | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | 0 | 0 | 0
E330-E320 | 0 | 0 | 0 | -5.8949e-06 | 0 | 0 | 0 | 0 | 0
E340-E300 | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | 0 | 0 | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300 | 0 | 0 | 0 | -2.2215e-11 | 0 | 0 | 0 | 0 | 0
E400-E300 | 0 | 0 | 0 | 3.0931e-12 | -0.001968 | 0 | 0 | 0 | 0
E410-E300 | 0 | 0 | 0 | 2.4278e-12 | -0.001968 | 0 | 0 | 0 | 0
E420-E300 | 0 | 0 | 0 | -7.6947e-13 | -0.001968 | 0 | 0 | 0 | 0
E430-E300 | 0 | 0 | 0 | 3.0931e-12 | -0.001968 | 0 | 0 | 0 | 0
E440-E300 | 0 | 0 | 0 | -9.3204e-13 | -0.001968 | 0 | 0 | 0 | 0
E500-E300 | 0.0049507 | -0.0017 | -0.0017 | 0.0050316 | 0.00494 | 0.00833 | 0 | 0 | 0
E510-E500 | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0 | 0 | 0
E525-E520 | 0.00073266 | 0 | 0 | 0.00053199 | 0.000384 | 0.00883 | 0 | 0 | 0
E530-E500 | -0.00061959 | 0 | 0 | -0.00051756 | -0.001454 | -0.00367 | 0 | 0 | 0
E545-E540 | 0.0020983 | 0 | 0 | 0.0029798 | 0.003432 | 0.0028 | 0 | 0 | 0
Delta Max Relative Humidity (%)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 8.9137 | 30.83 | 31.85 | 10.1493 | 9 | 10.75 | 0 | 0 | 0
E320-E300 | 13.0466 | 14.06 | 14.82 | 14.9388 | 15 | 14.44 | 0 | 0 | 0
E330-E300 | 7.8699 | 9.11 | 9.09 | 8.8625 | 8 | 11.26 | 0 | 0 | 0
E330-E320 | -5.1767 | -4.95 | -5.73 | -6.0763 | -7 | -3.18 | 0 | 0 | 0
E340-E300 | 11.1401 | 12.02 | 12.41 | 12.7691 | 12 | 12.81 | 0 | 0 | 0
E330-E340 | -3.2702 | -2.91 | -3.32 | -3.9066 | -4 | -1.55 | 0 | 0 | 0
E350-E300 | 0 | 11.77 | 12.27 | 0 | 2 | 5.21 | 0 | 0 | 0
E360-E300 | 0 | 0 | 0 | -0.00017286 | 0 | 0 | 0 | 0 | 0
E400-E300 | 14.9642 | 16.22 | 16.72 | 16.856 | -68 | 18.87 | 0 | 0 | 0
E410-E300 | 14.4355 | 15.44 | 15.94 | 14.5926 | -68 | 18.74 | 0 | 0 | 0
E420-E300 | 2.0519 | 5.16 | 2.68 | 5.5009 | -68 | 6.41 | 0 | 0 | 0
E430-E300 | 11.9195 | 9.08 | 9.58 | 12.9398 | -68 | 11.5 | 0 | 0 | 0
E440-E300 | -0.065 | 0 | 0 | 8.1634e-09 | -68 | 0.07 | 0 | 0 | 0
E500-E300 | 31.2108 | -69.35 | -68.85 | 32.2238 | 32 | -7.36 | 0 | 0 | 0
E510-E500 | 0 | 0 | 0 | 0 | 0 | -2.57 | 0 | 0 | 0
E525-E520 | 9.7701 | 0 | 0 | 6.3958 | 5 | -20.65 | 0 | 0 | 0
E530-E500 | -8.9555 | 0 | 0 | -8.302 | -21 | -24.07 | 0 | 0 | 0
E545-E540 | 29.6022 | 0 | 0 | 41.2182 | 50 | -15.82 | 0 | 0 | 0
Delta Min Relative Humidity (%)
| TRNSYS | DOE21E-J | DOE21E-E | EnargyPlus | CODY | HOT3000 | YourData | Extra | Extra
E310-E300 | 0.0586 | 0 | 0 | 1.0832 | 1 | 0.99 | 0 | 0 | 0
E320-E300 | 0 | 0 | 0 | 0.40959 | 0 | -2.02 | 0 | 0 | 0
E330-E300 | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0 | 0 | 0
E330-E320 | 0 | 0 | 0 | -0.40947 | 0 | 2.02 | 0 | 0 | 0
E340-E300 | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0 | 0 | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300 | 0 | 0 | 0 | -5.6978e-05 | 0 | 0 | 0 | 0 | 0
E400-E300 | -0.1222 | 0 | 0 | -0.46234 | -15 | -0.37 | 0 | 0 | 0
E410-E300 | -0.1221 | 0 | 0 | -0.20009 | -15 | -0.36 | 0 | 0 | 0
E420-E300 | -0.1213 | 0 | 0 | -0.46224 | -15 | -0.35 | 0 | 0 | 0
E430-E300 | -0.1234 | 0 | 0 | -0.46235 | -15 | -0.36 | 0 | 0 | 0
E440-E300 | -0.1243 | 0 | 0 | -0.46235 | -15 | -0.4 | 0 | 0 | 0
E500-E300 | 40.0742 | -11.97 | -11.97 | 39.0378 | 39 | 37.89 | 0 | 0 | 0
E510-E500 | -1.3175 | 0 | 0 | 0.10666 | 0 | 0.32 | 0 | 0 | 0
E525-E520 | -15.7395 | 0 | 0 | -15.0875 | -17 | -17.5 | 0 | 0 | 0
E530-E500 | -23.812 | 0 | 0 | -20.8644 | -26 | -19.15 | 0 | 0 | 0
E545-E540 | -19.3505 | 0 | 0 | -16.6007 | -12 | -19.6 | 0 | 0 | 0

## B
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
TRNSYS-TUD, received 19 Feb 2003 with revs by jn 20 Feb 2003, and for 5 Apr 2003 results as noted below
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
TRNSYS-TUD, received 19 Feb 2003 with revs by jn 20 Feb 2003, and for 5 Apr 2003 results as noted below
• deleted column J (other COP2 calcs by Thoi), 20 Feb 2003
• column i: recalc COP2 based on spec (annual sum total coil load)/(annual sum compressor + OD fan energy) [previously TUD used average of hourly calculated COP2 when compressor operating; was only slight difference from spec definition]. 20 Feb 2003
• E440 updated for corrected IP to SI psychrometric enthalpy conversion, for 5 Apr 2003 results
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 35633.7773 | 22353.5343 | 2400.3229 | 10879.92 | 80426.8675 | 56661.7484 | 23765.119 | 3.2491 | 23.6243 | 0.0090691 | 48.6149 | 19.9145 | 0.011643 | E300 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15 | 34.7 | 20-Jul | 15 | 0.021878 | 02-Oct | 9
E310 | 39973.3798 | 26339.6254 | 2753.8345 | 10879.92 | 99342.1316 | 56256.3775 | 43085.7541 | 3.4146 | 23.7556 | 0.011071 | 58.3307 |  |  | E310 | 12594.4016 | 20-Jul | 15 | 23094.3 | 10-Sep | 15 | 15907 | 03-Sep | 15 | 37328 | 03-Sep | 15
E320 | 40059.657 | 26433.1374 | 2746.5996 | 10879.92 | 99791.678 | 62859.2053 | 36932.4726 | 3.4199 | 23.9005 | 0.009988 | 52.0053 |  |  | E320 | 13028.1986 | 20-Jul | 15 | 31315.6 | 24-Apr | 16 | 23147.3 | 02-Oct | 10 | 40317.6 | 03-Sep | 16
E330 | 40963.3004 | 27299.7321 | 2783.6483 | 10879.92 | 105012.8715 | 63083.3765 | 41929.495 | 3.4907 | 23.8797 | 0.0097409 | 50.8445 |  |  | E330 | 13346.701 | 20-Jul | 15 | 33226.1 | 14-Jun | 14 | 27825.2 | 18-Sep | 16 | 43492 | 02-Oct | 9
E340 | 40619.2951 | 26962.9373 | 2776.4378 | 10879.92 | 102727.9789 | 63032.6061 | 39695.3729 | 3.4543 | 23.8756 | 0.0097914 | 51.085 |  |  | E340 | 13180.9018 | 20-Jul | 15 | 32828.9 | 24-Apr | 15 | 24848.3 | 02-Oct | 9 | 41651.7 | 02-Oct | 10
E350 | 32236.9795 | 19316.8404 | 2040.2191 | 10879.92 | 69387.9976 | 50370.8304 | 19017.1672 | 3.2489 | 25.6595 | 0.0097059 | 45.484 |  |  | E350 | 11626.889 | 20-Jul | 15 | 23277.5 | 29-Jul | 15 | 9751.26 | 01-Oct | 13 | 32091.73 | 08-Jul | 15
E360 | 55298.7917 | 40105.8399 | 4313.0318 | 10879.92 | 162974.0626 | 134976.8351 | 27997.2274 | 3.669 | 25.3649 | 0.0084995 | 41.0335 |  |  | E360 | 12769.5022 | 20-Jul | 15 | 32060.7 | 24-Apr | 16 | 9275.16 | 02-Oct | 10 | 38857.16 | 02-Oct | 10
E400 | 32045.1536 | 19178.9487 | 1986.2848 | 10879.92 | 68792.8221 | 41952.3595 | 26840.4626 | 3.2503 | 24.1263 | 0.0098011 | 50.7709 |  |  | E400 | 11627.8677 | 20-Jul | 15 | 23277.5 | 29-Jul | 15 | 27075.3 | 16-Sep | 15 | 41178.6 | 16-Sep | 15
E410 | 32078.4319 | 19204.4944 | 1994.0175 | 10879.92 | 68672.8538 | 45676.6456 | 22996.2083 | 3.2395 | 24.1221 | 0.0097405 | 50.4971 |  |  | E410 | 11627.8677 | 20-Jul | 15 | 23265.7 | 10-Sep | 16 | 11138.9 | 16-Sep | 15 | 32091.73 | 08-Jul | 15
E420 | 33387.0076 | 20358.5854 | 2148.5022 | 10879.92 | 72609.3074 | 50389.8247 | 22219.4827 | 3.2261 | 23.9262 | 0.0092639 | 48.7794 |  |  | E420 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9751.04 | 01-Oct | 13 | 32174.05 | 08-Jul | 15
E430 | 32538.0313 | 19598.6211 | 2059.4903 | 10879.92 | 69756.312 | 47863.3462 | 21892.9657 | 3.2208 | 23.9916 | 0.0093103 | 48.8219 |  |  | E430 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15
E440 | 33691.321 | 20629.1333 | 2182.2678 | 10879.92 | 73711.3635 | 50876.0725 | 22835.291 | 3.2313 | 23.9118 | 0.0091578 | 48.3298 |  |  | E440 | 11626.0371 | 20-Jul | 15 | 23277.4 | 20-Jul | 16 | 9635.7 | 03-Sep | 16 | 32174.05 | 08-Jul | 15
E500 | 22337.887 | 17854.2956 | 1919.7698 | 2563.8216 | 63357.1063 | 45043.8 | 18313.3062 | 3.2041 | 20.2342 | 0.0097753 | 66.5261 |  |  | E500 | 10166.4831 | 20-Jul | 15 | 19549.2 | 28-Oct | 15 | 7965.46 | 06-Oct | 15 | 27485.51 | 28-Oct | 15
E500 May-Sep | 17390.8511 | 13942.1479 | 1476.6547 | 1972.0485 | 48443.4308 | 34443.2344 | 14000.1964 | 3.1418 | 24.5723 | 0.011021 | 57.0476 |  |  | E510 | 11204.8968 | 20-Jul | 15 | 21729.2 | 29-Apr | 19 | 8892.56 | 15-Sep | 11 | 30593.05 | 29-Apr | 19
E510 May-Sep | 34608.7754 | 27747.879 | 2937.6766 | 3923.2198 | 108974.3099 | 77489.4321 | 31484.8778 | 3.5513 | 25.8168 | 0.011395 | 54.7001 |  |  | E520 | 11035.3898 | 20-Jul | 15 | 19415.9 | 28-Sep | 15 | 7913.7 | 28-Sep | 15 | 27329.6 | 28-Sep | 15
E520 | 24986.582 | 19521.2767 | 2340.1169 | 3125.1884 | 63421.5444 | 45109.6141 | 18311.9303 | 2.9011 | 13.5171 | 0.0066924 | 69.8745 |  |  | E522 | 10430.7791 | 20-Jul | 15 | 19488.8 | 12-Mai | 15 | 7906.7 | 02-Mai | 15 | 27383.59 | 12-Mai | 15
E522 | 23544.1607 | 18620.3108 | 2108.2783 | 2815.5716 | 63389.2228 | 45076.0312 | 18313.1916 | 3.0581 | 16.9456 | 0.0081904 | 68.6774 |  |  | E525 | 9366.7481 | 20-Jul | 15 | 19702.7 | 26-Jul | 16 | 8037.07 | 26-Jul | 16 | 27739.77 | 26-Jul | 16
E525 | 20320.874 | 16557.8748 | 1611.2289 | 2151.7702 | 63292.9454 | 44979.0103 | 18313.9351 | 3.4835 | 26.8443 | 0.013713 | 61.4674 |  |  | E530 | 8028.3285 | 20-Jul | 15 | 19834.1 | 29-Mai | 15 | 1.6431e-11 | 18-Jun | 16 | 19834.1 | 29-Mai | 15
E530 | 17281.271 | 13656.9951 | 1551.8309 | 2072.4451 | 45045.848 | 45045.848 | 5.6053e-13 | 2.9618 | 20.0253 | 0.0062265 | 46.7299 |  |  | E540 | 8698.9562 | 20-Jul | 15 | 19575 | 30-Aug | 16 | 627.186 | 11-Mar | 10 | 19575 | 30-Aug | 16
E540 | 19430.3785 | 15020.7433 | 1888.1035 | 2521.5317 | 45112.827 | 45111.8473 | 0.97976 | 2.668 | 13.2893 | 0.0044601 | 48.521 |  |  | E545 | 7204.827 | 20-Jul | 15 | 20075.2 | 17-Jun | 16 | 1.8119e-11 | 01-Jul | 16 | 20075.2 | 17-Jun | 16
E545 | 15687.0796 | 12621.8685 | 1312.4522 | 1752.7588 | 44981.3517 | 44981.3517 | -3.3573e-14 | 3.2281 | 26.6052 | 0.0062265 | 36.6249
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2055.7697 | 256.5326 | 8131.73 | 6189.34 | 1942.39 | 0.0090778 | 3.5167 | 18.05 | 23.4068 | 16.9641 | 0.011255 |  |  | E300 | 4.1683 | 16-Apr | 3 | 2.7931 | 24-Apr | 17 | 26.1999 | 07-Jul | 15 | 7.93 | 06-Jan | 6 | 0.013284 | 16-Nov | 17 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
2 | 2053.6706 | 256.5271 | 8115.8 | 6201.56 | 1914.24 | 0.0090138 | 3.513 | 18.05 | 23.3748 | 16.9046 | 0.011255 |  |  | E310 | 4.1433 | 30-Apr | 15 | 2.8652 | 01-Dec | 15 | 27.0778 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.01575 | 01-Oct | 23 | 0.0018769 | 11-Jan | 3 | 77.7029 | 02-Oct | 4 | 13.3898 | 06-Nov | 6
3 | 2054.4923 | 256.5356 | 8127.89 | 6194.38 | 1933.51 | 0.0090644 | 3.517 | 18.05 | 23.3833 | 16.9418 | 0.011255 |  |  | E320 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.3604 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.018017 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 81.8358 | 18-Sep | 10 | 13.3312 | 06-Nov | 5
4 | 1830.0824 | 229.5857 | 7224.15 | 5548.55 | 1675.6 | 0.0089864 | 3.5074 | 17.8 | 23.3739 | 16.8619 | 0.011075 |  |  | E330 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.2321 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.017651 | 10-Jul | 12 | 0.0018769 | 11-Jan | 3 | 76.6591 | 22-Sep | 20 | 13.3312 | 06-Nov | 5
5 | 2029.3426 | 256.394 | 8104.85 | 6318.9 | 1785.95 | 0.0088405 | 3.5458 | 17.5 | 23.3503 | 16.6966 | 0.01061 |  |  | E340 | 4.1683 | 16-Apr | 3 | 2.8252 | 31-Mar | 14 | 32.3066 | 20-Jul | 15 | 7.93 | 06-Jan | 6 | 0.017871 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 79.9293 | 18-Sep | 10 | 13.3312 | 06-Nov | 5
6 | 1839.4317 | 229.5597 | 7130.87 | 5686.24 | 1444.63 | 0.0086578 | 3.4465 | 18.3 | 23.4171 | 16.5734 | 0.010568 |  |  | E350 | 4.1683 | 16-Apr | 3 | 2.7904 | 24-Apr | 17 | 34.5841 | 01-Oct | 24 | 7.93 | 06-Jan | 6 | 0.016758 | 01-Oct | 24 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
7 | 2667.2444 | 308.5446 | 9711.38 | 7596.88 | 2114.5 | 0.0091531 | 3.2635 | 22.2 | 24.0395 | 17.3192 | 0.012071 |  |  | E360 | 4.401 | 05-Oct | 1 | 2.8252 | 31-Mar | 14 | 33.7585 | 10-Jul | 13 | 7.93 | 06-Jan | 6 | 0.013433 | 10-Jul | 13 | 0.0018769 | 11-Jan | 3 | 68.7892 | 16-Nov | 17 | 13.3312 | 06-Nov | 5
8 | 3552.7185 | 384.0455 | 12121.31 | 9558.23 | 2563.08 | 0.0095303 | 3.079 | 26.1 | 24.5724 | 17.7945 | 0.012173 |  |  | E400 | 4.0769 | 16-Sep | 15 | 2.7819 | 31-Mar | 19 | 27.1148 | 16-Sep | 15 | 7.93 | 06-Jan | 6 | 0.016944 | 05-Apr | 22 | 0.0018769 | 11-Jan | 3 | 83.7534 | 05-Apr | 22 | 13.209 | 06-Nov | 5
9 | 4364.7758 | 458.1014 | 14555.62 | 11757.9 | 2797.72 | 0.0096727 | 3.018 | 28.05 | 25.0937 | 17.973 | 0.011538 |  |  | E410 | 3.8879 | 30-Apr | 15 | 2.7858 | 24-Apr | 17 | 26.8256 | 23-Oct | 15 | 7.93 | 06-Jan | 6 | 0.016835 | 05-Apr | 22 | 0.0018769 | 11-Jan | 3 | 83.2247 | 05-Apr | 22 | 13.2091 | 06-Nov | 5
10 | 4441.0633 | 457.9932 | 14639.38 | 11506.4 | 3132.98 | 0.010058 | 2.9882 | 28.9 | 25.2815 | 18.3972 | 0.012388 |  |  | E420 | 3.7813 | 27-Sep | 16 | 2.7931 | 24-Apr | 17 | 26.1999 | 07-Jul | 15 | 7.93 | 06-Jan | 6 | 0.014297 | 02-Apr | 10 | 0.0018769 | 11-Jan | 3 | 70.8411 | 02-Apr | 10 | 13.2099 | 06-Nov | 5
11 | 4999.595 | 506.3045 | 16374.09 | 12342.2 | 4031.89 | 0.010408 | 2.9739 | 30 | 25.3592 | 18.8246 | 0.013776 |  |  | E430 | 3.7813 | 27-Sep | 16 | 2.7711 | 30-Mar | 19 | 27.1992 | 01-Nov | 16 | 7.93 | 06-Jan | 6 | 0.016231 | 02-Apr | 5 | 0.0018769 | 11-Jan | 3 | 80.7087 | 02-Apr | 5 | 13.2078 | 06-Nov | 5
12 | 5316.7711 | 529.3648 | 17248.4 | 12810 | 4438.4 | 0.010684 | 2.9504 | 30.85 | 25.5877 | 19.1202 | 0.014041 |  |  | E440 | 3.8835 | 12-Dez | 7 | 2.7825 | 31-Mar | 19 | 27.0452 | 28-Apr | 15 | 7.93 | 06-Jan | 6 | 0.013313 | 16-Nov | 17 | 0.0018769 | 11-Jan | 3 | 68.7242 | 16-Nov | 17 | 13.2069 | 06-Nov | 5
13 | 6188.5477 | 616.6094 | 20498.21 | 16816.1 | 3682.11 | 0.010087 | 3.0122 | 30.85 | 26.53 | 18.8377 | 0.012315 |  |  | E500 | 4.2751 | 13-Oct | 1 | 2.6852 | 30-Jul | 12 | 25.8054 | 30-Apr | 15 | 8.427 | 20-Dec | 22 | 0.01172 | 11-Jul | 15 | 0.0068276 | 20-Dec | 22 | 100 | 21-Nov | 24 | 53.4054 | 30-Apr | 15
14 | 6210.9293 | 616.1242 | 20234.06 | 17283.5 | 2950.56 | 0.0097987 | 2.9638 | 31.4 | 26.5617 | 18.5548 | 0.011543 |  |  | E510 | 4.6925 | 05-Oct | 1 | 2.888 | 31-Mar | 15 | 26.1003 | 09-Jul | 15 | 8.427 | 20-Dec | 22 | 0.011871 | 07-Sep | 15 | 0.0068276 | 20-Dec | 22 | 100 | 21-Nov | 24 | 52.0879 | 04-Oct | 23
15 | 7922.4534 | 781.0016 | 26687.28 | 22882.4 | 3804.88 | 0.0095792 | 3.0663 | 31.95 | 26.7812 | 18.5486 | 0.012069 |  |  | E520 | 3.8137 | 30-Apr | 15 | 2.4417 | 30-Jul | 12 | 16.1232 | 15-Aug | 15 | 8.3053 | 20-Dec | 22 | 0.0075403 | 07-Sep | 15 | 0.006103 | 26-Nov | 2 | 90.2299 | 20-Dec | 22 | 61.2679 | 25-Nov | 24
16 | 7964.823 | 781.0124 | 26722.68 | 22284.7 | 4437.98 | 0.0096663 | 3.0555 | 32.2 | 26.5632 | 18.673 | 0.013324 |  |  | E522 | 3.9855 | 16-Mar | 10 | 2.5689 | 08-Jul | 17 | 21.0091 | 16-Jul | 15 | 8.4141 | 20-Dec | 22 | 0.0094264 | 20-Jul | 16 | 0.0068215 | 20-Dec | 22 | 100 | 18-Dec | 8 | 58.5054 | 30-Apr | 15
17 | 5420.7775 | 529.4985 | 17231.33 | 13048.3 | 4183.03 | 0.01077 | 2.8959 | 31.95 | 26.198 | 19.4032 | 0.014505 |  |  | E525 | 4.7178 | 13-Oct | 1 | 2.9111 | 14-Jul | 17 | 36.08 | 10-Mai | 16 | 8.4442 | 20-Dec | 22 | 0.017932 | 10-Mai | 16 | 0.0068356 | 20-Dec | 22 | 100 | 12-Nov | 20 | 45.5284 | 30-Apr | 15
18 | 5409.9868 | 529.3784 | 17505.88 | 12720.6 | 4785.28 | 0.011184 | 2.9474 | 31.4 | 26.2263 | 19.7724 | 0.015234 |  |  | E530 | 4.0061 | 02-Nov | 1 | 2.5013 | 30-Jul | 12 | 26.116 | 04-Jun | 15 | 8.4215 | 20-Dec | 22 | 0.0069892 | 01-Jan | 1 | 0.006208 | 01-Apr | 1 | 91.0445 | 20-Dec | 22 | 29.5934 | 04-Jun | 15
19 | 5260.0345 | 529.2289 | 17661.69 | 12490.8 | 5170.89 | 0.011131 | 3.0508 | 29.7 | 25.7001 | 19.5753 | 0.015134 |  |  | E540 | 3.456 | 30-Apr | 15 | 2.253 | 30-Jul | 12 | 16.1465 | 21-Sep | 16 | 8.2278 | 20-Dec | 22 | 0.006084 | 01-Jan | 1 | 0.0041096 | 05-Oct | 3 | 61.275 | 20-Dec | 22 | 36.4749 | 21-Sep | 16
20 | 4880.3429 | 506.2207 | 16989.81 | 11655.3 | 5334.51 | 0.010991 | 3.1541 | 27.75 | 25.1673 | 19.3718 | 0.015748 |  |  | E545 | 4.2505 | 16-Mar | 10 | 2.7325 | 14-Jul | 17 | 35.6715 | 20-Jul | 15 | 8.4486 | 20-Dec | 22 | 0.0069892 | 01-Jan | 1 | 0.006208 | 01-Apr | 1 | 90.8772 | 20-Dec | 22 | 17.1244 | 20-Jul | 15
21 | 3938.7143 | 409.0843 | 13539.94 | 8882.19 | 4657.75 | 0.01114 | 3.1142 | 27.2 | 24.6544 | 19.438 | 0.016886 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3923.9563 | 409.5326 | 13564.54 | 8880.28 | 4684.26 | 0.011177 | 3.1302 | 26.95 | 24.7445 | 19.4846 | 0.016863
23 | 4122.5716 | 433.8551 | 14531.34 | 9449.35 | 5081.99 | 0.011176 | 3.1892 | 26.4 | 24.6707 | 19.4693 | 0.016867
24 | 3877.3845 | 409.5808 | 13691.76 | 8806.54 | 4885.22 | 0.011275 | 3.1938 | 26.1 | 24.7257 | 19.5725 | 0.017112
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3892.9389 | 3014.619 | 376.0762 | 502.2437 | 13185.6871 | 9374.7971 | 3810.89 | 0.010675 | 3.8448 | 16.7917 | 24.6411
June 25 | 5044.9219 | 4083.8829 | 411.4946 | 549.5444 | 13188.0504 | 9377.6867 | 3810.3637 | 0.011168 | 2.9313 | 29.5167 | 24.5478
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3022.7732 | 2311.4724 | 304.5625 | 406.7383 | 9353.1633 | 9353.1633 | -5.4771e-13 | 0.006208 | 3.5431 | 16.7917 | 24.365
June 25 | 3894.1233 | 3118.0954 | 332.2771 | 443.7507 | 9376.2963 | 9376.2963 | 7.2905e-13 | 0.006208 | 2.7197 | 29.5167 | 24.3537

## C
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
DOE-2.2 NT42j; 16 Jun 2004 rev for FLOOR-WEIGHT = 0.74 (zone air mass)
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34750 | 21569 | 2301 | 10880 | 77283.4356 | 55796.8608 | 21486.5748 | 3.2377 | 24.0556 | 0.0092 | 48.26 | 19.8889 | 0.0116 | E300 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15 | 35 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 | 39379 | 25813 | 2686 | 10880 | 97394.7852 | 56300.9928 | 41093.7924 | 3.4175 | 24.1111 | 0.0113 | 58.51 | ODB, OHR |  | E310 | 12583 | 2002-07-20 | 15 | 23080 | 2004-09-10 | 16 | 15139 | 2001-09-03 | 15 | 36750 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 | 38745 | 25250 | 2615 | 10880 | 96356.3319 | 62697.021 | 33659.3109 | 3.458 | 24.3889 | 0.0101 | 51.21 | from E500 |  | E320 | 12916 | 2002-07-20 | 15 | 31119 | 2004-04-24 | 16 | 31497 | 2002-10-02 | 9 | 53813 | 2002-10-02 | 9
E330 | 39708 | 26172 | 2656 | 10880 | 100729.9701 | 63311.0655 | 37418.9046 | 3.4942 | 24.2778 | 0.0099 | 50.58 |  |  | E330 | 13212 | 2002-07-20 | 15 | 33410 | 2002-06-14 | 14 | 26941 | 2003-09-18 | 15 | 43628 | 2002-10-02 | 9
E340 | 39358 | 25829 | 2649 | 10880 | 99027.6453 | 63053.4306 | 35974.2147 | 3.4773 | 24.2778 | 0.0099 | 50.69 |  |  | E340 | 13158 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 30451 | 2002-10-02 | 9 | 50819 | 2002-10-02 | 9
E350 | 30547 | 17802 | 1865 | 10880 | 63736.3536 | 47684.439 | 16051.9146 | 3.2408 | 26.1667 | 0.01 | 45.45 |  |  | E350 | 11654 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9303 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E360 | 54064 | 38999 | 4185 | 10880 | 159807.2061 | 134919.792 | 24887.4141 | 3.7006 | 25.6111 | 0.0087 | 41.49 |  |  | E360 | 12736 | 2002-07-20 | 15 | 32111 | 2003-04-24 | 16 | 10026 | 2002-10-02 | 9 | 40613 | 2002-10-02 | 9
E400 | 30846 | 18106 | 1860 | 10880 | 64917.5466 | 41419.1334 | 23498.4132 | 3.2514 | 24.0556 | 0.01 | 52.21 |  |  | E400 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 25578 | 2002-09-18 | 14 | 40543 | 2002-09-18 | 14
E410 | 31668 | 18823 | 1965 | 10880 | 66779.6109 | 47658.6462 | 19120.9647 | 3.2124 | 24.0556 | 0.0095 | 49.65 |  |  | E410 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E420 | 32530 | 19596 | 2054 | 10880 | 69610.9569 | 49666.0881 | 19944.8688 | 3.2153 | 24.0556 | 0.0094 | 49.14 |  |  | E420 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E430 | 31932 | 19059 | 1993 | 10880 | 67640.7387 | 47731.335 | 19909.4037 | 3.213 | 24.0556 | 0.0094 | 49.17 |  |  | E430 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 11105 | 2004-10-24 | 14 | 31401 | 2001-07-20 | 15
E440 | 33032 | 20042 | 2110 | 10880 | 71380.1085 | 50592.5772 | 20787.5313 | 3.2223 | 24.0556 | 0.0093 | 48.46 |  |  | E440 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E500 | 22817 | 18473 | 1975 | 2369 | 65995.8615 | 47649.8532 | 18346.0083 | 3.2275 | 20.6667 |  |  |  |  | E500 | 10431 | 2002-07-20 | 15 | 20009 | 2003-06-04 | 16 | 7733 | 2001-09-03 | 15 | 27707 | 2001-08-16 | 16
E500 May-Sep | 17872 | 14508 | 1527 | 1837 | 50692.8174 | 36595.5867 | 14097.2307 | 3.1614 | 25 | 0.0114 | 57.47 |  |  | E510 | 11590 | 2002-07-20 | 15 | 22513 | 2002-07-11 | 15 | 8723 | 2002-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep | 35971 | 28811 | 3061 | 4099 | 114017.9517 | 82305.7041 | 31712.2476 | 3.5774 | 25.1111 | 0.0114 | 57.36 |  |  | E520 | 10989 | 2002-07-20 | 15 | 20159 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-08-14 | 16
E520 | 25389 | 20121 | 2394 | 2874 | 66571.2168 | 48101.5203 | 18469.6965 | 2.9567 | 13.7778 |  |  |  |  | E522 | 10972 | 2002-07-20 | 15 | 20137 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27868 | 2002-08-16 | 16
E522 | 24293 | 19407 | 2182 | 2704 | 66373.0812 | 47962.2978 | 18410.7834 | 3.0744 | 17.2778 |  |  |  |  | E525 | 9538 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 | 20408 | 16880 | 1642 | 1886 | 65399.1099 | 47217.5307 | 18181.5792 | 3.5309 | 27.3889 |  |  |  |  | E530 | 8059 | 2002-07-20 | 15 | 19576 | 2002-04-24 | 16 | 0 | 0 | 0 | 19576 | 2002-04-24 | 16
E530 | 17540 | 14127 | 1580 | 1833 | 46634.2617 | 46573.59 | 60.6717 | 2.969 | 20.6111 |  |  |  |  | E540 | 8943 | 2002-07-20 | 15 | 19766 | 2002-04-24 | 16 | 0 | 0 | 0 | 19766 | 2002-04-24 | 16
E540 | 19878 | 15680 | 1940 | 2258 | 47129.8938 | 47022.9123 | 106.9815 | 2.6748 | 13.7778 |  |  |  |  | E545 | 7350 | 2002-07-20 | 15 | 19475 | 2002-04-24 | 16 | 0 | 0 | 0 | 19475 | 2002-04-24 | 16
E545 | 15802 | 12967 | 1334 | 1501 | 46239.7491 | 46214.2494 | 25.4997 | 3.2333 | 27.3333
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1897 | 237 | 7552.3077 | 5889.2583 | 1663.0494 | 0.0094 | 3.539 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.869 | 2002-04-30 | 16 | 2.798 | 2002-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 1941 | 240 | 7630.2723 | 6069.8079 | 1560.4644 | 0.0093 | 3.4985 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.141 | 2002-04-30 | 16 | 2.85 | 2002-12-01 | 14 | 26.89 | 2004-07-20 | 16 | 8.89 | 2001-01-06 | 6 | 0.0188 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.18 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 1897 | 237 | 7550.256 | 5881.3446 | 1668.9114 | 0.0094 | 3.5381 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E320 | 5.143 | 2002-10-02 | 9 | 2.801 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 10.83 | 2001-01-06 | 7 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.41 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
4 | 1891 | 237 | 7533.8424 | 5878.1205 | 1655.7219 | 0.0094 | 3.5403 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101593.5104 | E330 | 4.109 | 2003-06-17 | 16 | 2.798 | 2002-12-01 | 14 | 31.72 | 2004-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0178 | 2003-10-02 | 9 | 0.0017 | 2001-01-04 | 24 | 78.46 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
5 | 1697 | 215 | 6797.8683 | 5675.2953 | 1122.573 | 0.0089 | 3.5554 | 17.2222 | 23.7778 | 16.85 | 0.0103 | 0.0091 | 101593.5104 | E340 | 4.621 | 2002-10-02 | 9 | 2.798 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.37 | 2004-09-18 | 9 | 11.97 | 2002-11-06 | 4
6 | 2126 | 259 | 8136.1629 | 6438.5277 | 1697.6352 | 0.0092 | 3.4114 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.889 | 2003-04-27 | 5 | 2.798 | 2004-12-01 | 14 | 34.94 | 2003-06-23 | 24 | 8.89 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3198 | 352 | 11075.9559 | 8342.2122 | 2733.7437 | 0.01 | 3.12 | 25 | 24.9444 | 18.39 | 0.0133 | 0.0105 | 101593.5104 | E360 | 4.428 | 2002-10-04 | 24 | 2.799 | 2002-12-01 | 14 | 32.78 | 2002-07-20 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3135 | 332 | 10290.741 | 9069.9795 | 1220.7615 | 0.0094 | 2.9682 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.088 | 2003-06-17 | 16 | 2.734 | 2002-12-03 | 15 | 27.56 | 2003-09-16 | 16 | 8.89 | 2001-01-06 | 6 | 0.017 | 2002-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2002-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4528 | 469 | 14785.7226 | 11872.6017 | 2913.1209 | 0.0099 | 2.9589 | 28.8889 | 25.5556 | 18.36 | 0.0117 | 0.0102 | 101593.5104 | E410 | 3.903 | 2002-04-30 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 4651 | 479 | 15339.9747 | 12039.0825 | 3300.8922 | 0.0103 | 2.9902 | 28.8889 | 25.5556 | 18.68 | 0.0125 | 0.0106 | 101593.5104 | E420 | 3.807 | 2003-05-21 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0147 | 2003-04-01 | 21 | 0.0017 | 2001-01-04 | 24 | 74.51 | 2003-04-17 | 7 | 11.97 | 2002-11-06 | 4
11 | 5434 | 537 | 17455.2774 | 12811.9872 | 4643.2902 | 0.0109 | 2.9233 | 31.1111 | 25.8889 | 19.48 | 0.0148 | 0.0115 | 101593.5104 | E430 | 3.805 | 2003-10-24 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0156 | 2002-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2002-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5019 | 498 | 16215.1713 | 12612.093 | 3603.0783 | 0.0108 | 2.9391 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.774 | 2002-09-27 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6040 | 597 | 19722.9921 | 17139.0225 | 2583.9696 | 0.0101 | 2.9717 | 31.1111 | 25.9444 | 18.56 | 0.0115 | 0.0103 | 101593.5104 | E500 | 7.367 | 2004-03-11 | 10 | 2.693 | 2002-07-29 | 12 | 25.11 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 6420 | 633 | 20808.3414 | 17638.1718 | 3170.1696 | 0.01 | 2.9503 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 7.367 | 2004-03-11 | 10 | 2.817 | 2004-04-05 | 17 | 25.11 | 2001-04-21 | 3 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 7671 | 751 | 25387.1496 | 22196.463 | 3190.6866 | 0.0098 | 3.0144 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 4.896 | 2004-03-16 | 10 | 2.463 | 2004-04-05 | 17 | 16.11 | 2002-08-16 | 16 | 8.11 | 2004-12-20 | 12 | 0.0077 | 2004-07-10 | 16 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8190 | 800 | 27581.0031 | 22527.9591 | 5053.044 | 0.01 | 3.068 | 32.2222 | 26.1667 | 18.84 | 0.0144 | 0.0106 | 101254.8653 | E522 | 6.233 | 2004-03-11 | 10 | 2.572 | 2002-07-29 | 12 | 20.11 | 2001-04-21 | 15 | 8.17 | 2004-12-20 | 12 | 0.0095 | 2003-06-04 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 5715 | 561 | 18204.7341 | 13599.2538 | 4605.4803 | 0.0107 | 2.9007 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 6.325 | 2004-04-12 | 9 | 2.939 | 2003-07-30 | 12 | 35.06 | 2003-04-21 | 16 | 8.17 | 2004-12-20 | 13 | 0.018 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 5536 | 544 | 17933.3235 | 12829.8663 | 5103.4572 | 0.0112 | 2.9496 | 31.1111 | 25.9444 | 19.75 | 0.0157 | 0.0119 | 101254.8653 | E530 | 3.981 | 2004-03-11 | 10 | 2.495 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0081 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 4711 | 481 | 16012.053 | 11875.5327 | 4136.5203 | 0.011 | 3.084 | 28.3333 | 25.5 | 19.32 | 0.0143 | 0.0115 | 101254.8653 | E540 | 3.456 | 2004-04-30 | 16 | 2.261 | 2003-07-29 | 12 | 15.11 | 2004-05-31 | 16 | 8.11 | 2004-12-20 | 12 | 0.005 | 2003-06-04 | 13 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 4859 | 504 | 17082.1611 | 11532.3126 | 5549.8485 | 0.0114 | 3.1852 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 4.275 | 2004-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-04-21 | 15 | 8.17 | 2004-12-20 | 13 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 3913 | 405 | 13435.4109 | 9302.4078 | 4133.0031 | 0.0113 | 3.1115 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 3825 | 399 | 13280.361 | 8973.5496 | 4306.8114 | 0.0114 | 3.144 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 3750 | 395 | 13191.8448 | 8787.4311 | 4404.4137 | 0.0115 | 3.1826 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 3880 | 407 | 13724.4075 | 8799.1551 | 4925.2524 | 0.0117 | 3.2014 | 26.1111 | 25.1111 | 20.14 | 0.0178 | 0.0127 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3975.4583 | 3119.8333 | 389.125 | 466.5 | 13732.6998 | 9924.8179 | 3807.8819 | 0.011 | 3.9136 | 16.8333 | 24.9444
June 25 | 5204.3333 | 4263.5417 | 426.3333 | 514.4583 | 13837.5319 | 9981.2396 | 3856.2923 | 0.0115 | 2.9505 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3062 | 2390.0417 | 311.1667 | 360.7917 | 9721.15 | 9721.15 | 0 | 0.0071 | 3.5988 | 16.8333 | 24.9444
June 25 | 3978.2083 | 3243 | 339.625 | 395.5833 | 9760.7918 | 9760.7674 | 0.024425 | 0.0078 | 2.7245 | 29.5 | 24.9444
DOE-2.2 NT42j, 17 Nov 2003
enter raw doe2 results below
bold entries not changed
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s; ODB Date: E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor |  | ODB Date: Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Compr + Both Fans Wh: Energy Consumption; Sensible Hour: E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans Wh: Compr + Both Fans; Sensible Date: Sensible; Latent Date: Latent; Sensible + Latent Wh: Sensible + Latent; ODB Date: ODB; Outdoor Humidity Ratio kg/kg: Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Btu) | (Btu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 23870 | 2301 | 10880 | 263676 |  | 73308 | 3.2377 | 75.3 | 0.0092 | 48.26 | 67.8 | 0.0116 | E300 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15 | 95 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 |  | 28499 | 2686 | 10880 | 332292 |  | 140204 | 3.4175 | 75.4 | 0.0113 | 58.51 |  |  | E310 | 12583 | 2002-07-20 | 15 | 23080 | 2004-09-10 | 16 | 15139 | 2001-09-03 | 15 | 36750 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27865 | 2615 | 10880 | 328749 |  | 114839 | 3.458 | 75.9 | 0.0101 | 51.21 |  |  | E320 | 12916 | 2002-07-20 | 15 | 31119 | 2004-04-24 | 16 | 31497 | 2002-10-02 | 9 | 53813 | 2002-10-02 | 9
E330 |  | 28828 | 2656 | 10880 | 343671 |  | 127666 | 3.4942 | 75.7 | 0.0099 | 50.58 |  |  | E330 | 13212 | 2002-07-20 | 15 | 33410 | 2002-06-14 | 14 | 26941 | 2003-09-18 | 15 | 43628 | 2002-10-02 | 9
E340 |  | 28478 | 2649 | 10880 | 337863 |  | 122737 | 3.4773 | 75.7 | 0.0099 | 50.69 |  |  | E340 | 13158 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 30451 | 2002-10-02 | 9 | 50819 | 2002-10-02 | 9
E350 |  | 19667 | 1865 | 10880 | 217456 |  | 54766 | 3.2408 | 79.1 | 0.01 | 45.45 |  |  | E350 | 11654 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9303 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E360 |  | 43184 | 4185 | 10880 | 545231 |  | 84911 | 3.7006 | 78.1 | 0.0087 | 41.49 |  |  | E360 | 12736 | 2002-07-20 | 15 | 32111 | 2003-04-24 | 16 | 10026 | 2002-10-02 | 9 | 40613 | 2002-10-02 | 9
E400 |  | 19966 | 1860 | 10880 | 221486 |  | 80172 | 3.2514 | 75.3 | 0.01 | 52.21 |  |  | E400 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 25578 | 2002-09-18 | 14 | 40543 | 2002-09-18 | 14
E410 |  | 20788 | 1965 | 10880 | 227839 |  | 65237 | 3.2124 | 75.3 | 0.0095 | 49.65 |  |  | E410 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E420 |  | 21650 | 2054 | 10880 | 237499 |  | 68048 | 3.2153 | 75.3 | 0.0094 | 49.14 |  |  | E420 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E430 |  | 21052 | 1993 | 10880 | 230777 |  | 67927 | 3.213 | 75.3 | 0.0094 | 49.17 |  |  | E430 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 11105 | 2004-10-24 | 14 | 31401 | 2001-07-20 | 15
E440 |  | 22152 | 2110 | 10880 | 243535 |  | 70923 | 3.2223 | 75.3 | 0.0093 | 48.46 |  |  | E440 | 11564 | 2002-07-20 | 15 | 23203 | 2002-07-20 | 15 | 9304 | 2001-09-03 | 15 | 31401 | 2001-07-20 | 15
E500 |  | 20448 | 1975 | 2369 | 225165 |  | 62593 | 3.2275 | 69.2 |  |  |  |  | E500 | 10431 | 2002-07-20 | 15 | 20009 | 2003-06-04 | 16 | 7733 | 2001-09-03 | 15 | 27707 | 2001-08-16 | 16
E500 May-Sep |  | 16035 | 1527 | 1837 | 172954 |  | 48097 | 3.1614 | 77 | 0.0114 | 57.47 |  |  | E510 | 11590 | 2002-07-20 | 15 | 22513 | 2002-07-11 | 15 | 8723 | 2002-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep |  | 31872 | 3061 | 4099 | 389007 |  | 108196 | 3.5774 | 77.2 | 0.0114 | 57.36 |  |  | E520 | 10989 | 2002-07-20 | 15 | 20159 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-08-14 | 16
E520 |  | 22515 | 2394 | 2874 | 227128 |  | 63015 | 2.9567 | 56.8 |  |  |  |  | E522 | 10972 | 2002-07-20 | 15 | 20137 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27868 | 2002-08-16 | 16
E522 |  | 21589 | 2182 | 2704 | 226452 |  | 62814 | 3.0744 | 63.1 |  |  |  |  | E525 | 9538 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 |  | 18522 | 1642 | 1886 | 223129 |  | 62032 | 3.5309 | 81.3 |  |  |  |  | E530 | Compr + Both Fans Wh: 8059; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19576; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19576; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E530 |  | 15707 | 1580 | 1833 | 159107 |  | 207 | 2.969 | 69.1 |  |  |  |  | E540 | Compr + Both Fans Wh: 8943; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19766; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19766; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E540 |  | 17620 | 1940 | 2258 | 160798 |  | 365 | 2.6748 | 56.8 |  |  |  |  | E545 | Compr + Both Fans Wh: 7350; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19475; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19475; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E545 |  | 14301 | 1334 | 1501 | 157761 |  | 87 | 3.2333 | 81.2
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh/h: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2134 | 237 | 25767 |  | 5674 | 0.0094 | 3.539 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.869 | 2002-04-30 | 16 | 2.798 | 2002-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 2181 | 240 | 26033 |  | 5324 | 0.0093 | 3.4985 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.141 | 2002-04-30 | 16 | 2.85 | 2002-12-01 | 14 | 26.89 | 2004-07-20 | 16 | 8.89 | 2001-01-06 | 6 | 0.0188 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.18 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 2134 | 237 | 25760 |  | 5694 | 0.0094 | 3.5381 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 5.143 | 2002-10-02 | 9 | 2.801 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 10.83 | 2001-01-06 | 7 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.41 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
4 | 2128 | 237 | 25704 |  | 5649 | 0.0094 | 3.5403 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 4.109 | 2003-06-17 | 16 | 2.798 | 2002-12-01 | 14 | 31.72 | 2004-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0178 | 2003-10-02 | 9 | 0.0017 | 2001-01-04 | 24 | 78.46 | 2004-10-02 | 9 | 11.97 | 2002-11-06 | 4
5 | 1912 | 215 | 23193 |  | 3830 | 0.0089 | 3.5554 | 63 | 74.8 |  | 0.0103 | 0.0091 | 30 | E340 | 4.621 | 2002-10-02 | 9 | 2.798 | 2002-12-01 | 14 | 31.61 | 2003-07-08 | 16 | 8.89 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.37 | 2004-09-18 | 9 | 11.97 | 2002-11-06 | 4
6 | 2385 | 259 | 27759 |  | 5792 | 0.0092 | 3.4114 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.889 | 2003-04-27 | 5 | 2.798 | 2004-12-01 | 14 | 34.94 | 2003-06-23 | 24 | 8.89 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3550 | 352 | 37789 |  | 9327 | 0.01 | 3.12 | 77 | 76.9 |  | 0.0133 | 0.0105 | 30 | E360 | 4.428 | 2002-10-04 | 24 | 2.799 | 2002-12-01 | 14 | 32.78 | 2002-07-20 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3467 | 332 | 35110 |  | 4165 | 0.0094 | 2.9682 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.088 | 2003-06-17 | 16 | 2.734 | 2002-12-03 | 15 | 27.56 | 2003-09-16 | 16 | 8.89 | 2001-01-06 | 6 | 0.017 | 2002-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2002-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4997 | 469 | 50446 |  | 9939 | 0.0099 | 2.9589 | 84 | 78 |  | 0.0117 | 0.0102 | 30 | E410 | 3.903 | 2002-04-30 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 5130 | 479 | 52337 |  | 11262 | 0.0103 | 2.9902 | 84 | 78 |  | 0.0125 | 0.0106 | 30 | E420 | 3.807 | 2003-05-21 | 15 | 2.798 | 2004-12-01 | 14 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0147 | 2003-04-01 | 21 | 0.0017 | 2001-01-04 | 24 | 74.51 | 2003-04-17 | 7 | 11.97 | 2002-11-06 | 4
11 | 5971 | 537 | 59554 |  | 15842 | 0.0109 | 2.9233 | 88 | 78.6 |  | 0.0148 | 0.0115 | 30 | E430 | 3.805 | 2003-10-24 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0156 | 2002-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2002-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5517 | 498 | 55323 |  | 12293 | 0.0108 | 2.9391 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.774 | 2002-09-27 | 15 | 2.734 | 2002-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.89 | 2001-01-06 | 6 | 0.0138 | 2001-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 69.35 | 2002-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6637 | 597 | 67291 |  | 8816 | 0.0101 | 2.9717 | 88 | 78.7 |  | 0.0115 | 0.0103 | 30 | E500 | 7.367 | 2004-03-11 | 10 | 2.693 | 2002-07-29 | 12 | 25.11 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 7053 | 633 | 70994 |  | 10816 | 0.01 | 2.9503 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 7.367 | 2004-03-11 | 10 | 2.817 | 2004-04-05 | 17 | 25.11 | 2001-04-21 | 3 | 8.17 | 2004-12-20 | 12 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 8422 | 751 | 86616 |  | 10886 | 0.0098 | 3.0144 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 4.896 | 2004-03-16 | 10 | 2.463 | 2004-04-05 | 17 | 16.11 | 2002-08-16 | 16 | 8.11 | 2004-12-20 | 12 | 0.0077 | 2004-07-10 | 16 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8990 | 800 | 94101 |  | 17240 | 0.01 | 3.068 | 90 | 79.1 |  | 0.0144 | 0.0106 | 29.9 | E522 | 6.233 | 2004-03-11 | 10 | 2.572 | 2002-07-29 | 12 | 20.11 | 2001-04-21 | 15 | 8.17 | 2004-12-20 | 12 | 0.0095 | 2003-06-04 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 6276 | 561 | 62111 |  | 15713 | 0.0107 | 2.9007 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 6.325 | 2004-04-12 | 9 | 2.939 | 2003-07-30 | 12 | 35.06 | 2003-04-21 | 16 | 8.17 | 2004-12-20 | 13 | 0.018 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 6080 | 544 | 61185 |  | 17412 | 0.0112 | 2.9496 | 88 | 78.7 |  | 0.0157 | 0.0119 | 29.9 | E530 | 3.981 | 2004-03-11 | 10 | 2.495 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 8.17 | 2004-12-20 | 12 | 0.0081 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 5192 | 481 | 54630 |  | 14113 | 0.011 | 3.084 | 83 | 77.9 |  | 0.0143 | 0.0115 | 29.9 | E540 | 3.456 | 2004-04-30 | 16 | 2.261 | 2003-07-29 | 12 | 15.11 | 2004-05-31 | 16 | 8.11 | 2004-12-20 | 12 | 0.005 | 2003-06-04 | 13 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 5363 | 504 | 58281 |  | 18935 | 0.0114 | 3.1852 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 4.275 | 2004-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-04-21 | 15 | 8.17 | 2004-12-20 | 13 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 4318 | 405 | 45839 |  | 14101 | 0.0113 | 3.1115 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30
22 | 4224 | 399 | 45310 |  | 14694 | 0.0114 | 3.144 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4145 | 395 | 45008 |  | 15027 | 0.0115 | 3.1826 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4287 | 407 | 46825 |  | 16804 | 0.0117 | 3.2014 | 79 | 77.2 |  | 0.0178 | 0.0127 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84215 | 9339 | 11196 | 1124479 |  | 311802 | 0.011 | 3.9136 | 62.3 | 76.9
June 25 |  | 112557 | 10232 | 12347 | 1133063 |  | 315766 | 0.0115 | 2.9505 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64829 | 7468 | 8659 | 796000 |  | 0 | 0.0071 | 3.5988 | 62.3 | 76.9
June 25 |  | 85983 | 8151 | 9494 | 799246 |  | 2 | 0.0078 | 2.7245 | 85.1 | 76.9

## D
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
DOE-2.1E ESTSC 120, 20 Oct 2003, using COIL-BF-FPLR default curve; input revs: 11/11/03 for TAVE and correct OUTSIDE-FAN-ELEC, 06/16/04 FLOOR-WEIGHT = 0.74 (zone air mass)
E300OUT2.XLS, Mar 20, 2002
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34755 | 21573 | 2302 | 10880 | 77291.9355 | 55804.7745 | 21487.161 | 3.2374 | 24.0556 | 0.0092 | 48.28 | 19.8889 | 0.0116 | E300 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2001-09-03 | 15 | 31455 | 2001-07-20 | 15 | 35 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 | 39384 | 25817 | 2687 | 10880 | 97412.0781 | 56312.7168 | 41099.3613 | 3.4175 | 24.0556 | 0.0113 | 58.53 | ODB, OHR |  | E310 | 12595 | 2002-07-20 | 15 | 23119 | 2004-06-04 | 16 | 15270 | 2001-09-03 | 15 | 37033 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 | 38792 | 25294 | 2618 | 10880 | 96493.2096 | 62746.848 | 33746.3616 | 3.4571 | 24.3889 | 0.0101 | 51.25 | from E500 |  | E320 | 12981 | 2002-07-20 | 15 | 31072 | 2002-04-24 | 16 | 31503 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9
E330 | 39438 | 25925 | 2633 | 10880 | 100993.467 | 63327.7722 | 37665.6948 | 3.5364 | 24.2778 | 0.0099 | 50.65 |  |  | E330 | 13407 | 2002-07-20 | 15 | 34490 | 2002-06-14 | 15 | 40809 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9
E340 | 39265 | 25745 | 2640 | 10880 | 99223.143 | 63110.5851 | 36112.5579 | 3.4956 | 24.2778 | 0.0099 | 50.73 |  |  | E340 | 13190 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 36011 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9
E350 | 30548 | 17801 | 1867 | 10880 | 63634.6479 | 47676.5253 | 15958.1226 | 3.2354 | 26.1667 | 0.01 | 45.55 |  |  | E350 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9393 | 2001-09-03 | 15 | 31454 | 2001-07-20 | 15
E360 | 54016 | 38955 | 4181 | 10880 | 159853.809 | 134939.7228 | 24914.0862 | 3.7058 | 25.5556 | 0.0087 | 41.49 |  |  | E360 | 12726 | 2002-07-20 | 15 | 32065 | 2004-04-24 | 16 | 10336 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9
E400 | 30876 | 18131 | 1865 | 10880 | 65025.1143 | 41437.0125 | 23588.1018 | 3.2519 | 24.0556 | 0.01 | 52.25 |  |  | E400 | 11677 | 2004-09-18 | 15 | 23205 | 2002-07-20 | 15 | 32396 | 2003-09-18 | 15 | 49838 | 2003-09-18 | 15
E410 | 31699 | 18850 | 1969 | 10880 | 66843.5067 | 47659.8186 | 19183.6881 | 3.2107 | 24.0556 | 0.0095 | 49.63 |  |  | E410 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E420 | 32910 | 19934 | 2096 | 10880 | 70882.1316 | 50612.2149 | 20269.9167 | 3.2175 | 24.0556 | 0.0094 | 48.97 |  |  | E420 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E430 | 31811 | 18951 | 1980 | 10880 | 67219.2609 | 47454.0624 | 19765.1985 | 3.2115 | 24.0556 | 0.0094 | 49.3 |  |  | E430 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 11101 | 2003-05-21 | 15 | 31455 | 2001-07-20 | 15
E440 | 32973 | 19989 | 2104 | 10880 | 71181.0936 | 50492.0439 | 20689.0497 | 3.2219 | 24.0556 | 0.0093 | 48.57 |  |  | E440 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2003-07-20 | 15
E500 | 22822 | 18478 | 1975 | 2369 | 65992.3443 | 47646.0429 | 18346.3014 | 3.2265 | 20.5556 |  |  |  |  | E500 | 10425 | 2002-07-20 | 15 | 20008 | 2002-09-10 | 16 | 7733 | 2001-09-03 | 15 | 27706 | 2001-08-16 | 16
E500 May-Sep | 17870 | 14506 | 1527 | 1837 | 50690.4726 | 36593.2419 | 14097.2307 | 3.1616 | 25 | 0.0114 | 57.47 |  |  | E510 | 11587 | 2002-07-20 | 15 | 22513 | 2003-07-11 | 15 | 8723 | 2003-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep | 35970 | 28810 | 3061 | 4099 | 114015.3138 | 82303.0662 | 31712.2476 | 3.5774 | 25.1111 | 0.0114 | 57.36 |  |  | E520 | 11014 | 2002-07-20 | 15 | 20154 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-07-23 | 16
E520 | 25390 | 20126 | 2393 | 2871 | 66565.3548 | 48095.6583 | 18469.6965 | 2.956 | 13.7222 |  |  |  |  | E522 | 10966 | 2002-07-20 | 15 | 20135 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27866 | 2002-08-16 | 16
E522 | 24307 | 19418 | 2182 | 2707 | 66371.9088 | 47961.4185 | 18410.4903 | 3.0728 | 17.2222 |  |  |  |  | E525 | 9531 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 | 20421 | 16893 | 1643 | 1885 | 65395.0065 | 47213.4273 | 18181.5792 | 3.528 | 27.2778 |  |  |  |  | E530 | 8055 | 2002-07-20 | 15 | 19575 | 2002-04-24 | 16 | 0 | 0 | 0 | 19575 | 2002-04-24 | 16
E530 | 17537 | 14124 | 1580 | 1833 | 46630.7445 | 46570.0728 | 60.6717 | 2.9694 | 20.5556 |  |  |  |  | E540 | 8939 | 2002-07-20 | 15 | 19766 | 2002-04-24 | 16 | 0 | 0 | 0 | 19766 | 2002-04-24 | 16
E540 | 19874 | 15677 | 1939 | 2258 | 47126.0835 | 47019.102 | 106.9815 | 2.6752 | 13.7222 |  |  |  |  | E545 | 7346 | 2002-07-20 | 15 | 19474 | 2002-04-24 | 16 | 0 | 0 | 0 | 19474 | 2002-04-24 | 16
E545 | 15791 | 12957 | 1333 | 1501 | 46235.9388 | 46210.4391 | 25.4997 | 3.2355 | 27.2778
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
[10 empty] | ewb from hvac2kit |  | OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) | (kg/kg) | (Pa) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1894 | 237 | 7544.9802 | 5886.9135 | 1658.0667 | 0.0094 | 3.5406 | 17.7778 | 23.8333 | 17.34 | 0.0114 | 0.0097 | 101254.8653 | E300 | 3.857 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
2 | 1941 | 241 | 7627.0482 | 6067.17 | 1559.8782 | 0.0093 | 3.4954 | 18.3333 | 23.9444 | 17.29 | 0.0112 | 0.0096 | 101254.8653 | E310 | 4.128 | 2002-04-30 | 16 | 2.851 | 2002-12-01 | 12 | 26.72 | 2002-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0189 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.7 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4
3 | 1894 | 237 | 7546.1526 | 5878.1205 | 1668.0321 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114 | 0.0097 | 101593.5104 | E320 | 4.967 | 2002-10-02 | 9 | 2.805 | 2003-12-01 | 15 | 31.5 | 2003-07-08 | 16 | 10.78 | 2001-01-06 | 7 | 0.0176 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.67 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4
4 | 1890 | 236 | 7528.2735 | 5873.4309 | 1654.8426 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114 | 0.0097 | 101593.5104 | E330 | 5.595 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 32 | 2003-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 13 | 0.0017 | 2001-01-04 | 24 | 77.94 | 2003-09-18 | 9 | 11.97 | 2002-11-06 | 4
5 | 1694 | 215 | 6753.024 | 5671.7781 | 1081.2459 | 0.009 | 3.5375 | 17.2222 | 23.7778 | 16.94 | 0.0103 | 0.0092 | 101593.5104 | E340 | 5.339 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 31.56 | 2003-07-08 | 16 | 8.83 | 2001-01-06 | 6 | 0.0174 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.26 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4
6 | 2133 | 259 | 8185.1106 | 6438.5277 | 1746.5829 | 0.0092 | 3.4219 | 19.4444 | 24.1111 | 17.3 | 0.0113 | 0.0095 | 101593.5104 | E350 | 3.863 | 2004-10-05 | 3 | 2.801 | 2003-12-01 | 12 | 34.94 | 2004-06-24 | 24 | 8.83 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4
7 | 3223 | 353 | 11232.7644 | 8347.7811 | 2884.9833 | 0.0098 | 3.1412 | 25 | 24.9444 | 18.23 | 0.0133 | 0.0103 | 101593.5104 | E360 | 4.427 | 2002-10-04 | 24 | 2.801 | 2003-12-01 | 12 | 32.56 | 2004-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
8 | 3145 | 335 | 10271.6895 | 9069.1002 | 1202.5893 | 0.0094 | 2.9516 | 27.2222 | 25.2778 | 17.78 | 0.0109 | 0.0096 | 101593.5104 | E400 | 4.776 | 2003-09-18 | 15 | 2.735 | 2003-12-03 | 13 | 28.83 | 2002-09-18 | 16 | 8.83 | 2001-01-06 | 6 | 0.017 | 2003-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2003-04-05 | 21 | 11.97 | 2002-11-06 | 4
9 | 4526 | 467 | 14844.0495 | 11875.2396 | 2968.8099 | 0.0099 | 2.973 | 28.8889 | 25.5556 | 18.28 | 0.0117 | 0.0101 | 101593.5104 | E410 | 3.855 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4
10 | 4655 | 478 | 15392.7327 | 12041.1342 | 3351.5985 | 0.0102 | 2.9988 | 28.8889 | 25.5556 | 18.6 | 0.0125 | 0.0105 | 101593.5104 | E420 | 3.759 | 2003-09-27 | 15 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0141 | 2002-04-17 | 3 | 0.0017 | 2001-01-04 | 24 | 71.53 | 2002-04-17 | 3 | 11.97 | 2002-11-06 | 4
11 | 5456 | 536 | 17605.0515 | 12817.5561 | 4787.4954 | 0.0107 | 2.9381 | 31.1111 | 25.8889 | 19.33 | 0.0148 | 0.0113 | 101593.5104 | E430 | 3.759 | 2003-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0156 | 2003-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2003-04-02 | 4 | 11.97 | 2002-11-06 | 4
12 | 5015 | 498 | 16187.6199 | 12610.9206 | 3576.6993 | 0.0108 | 2.9363 | 30.5556 | 25.8333 | 19.23 | 0.0134 | 0.0112 | 101593.5104 | E440 | 3.759 | 2002-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4
13 | 6036 | 600 | 19620.9933 | 17135.2122 | 2485.7811 | 0.0102 | 2.9568 | 31.1111 | 25.9444 | 18.64 | 0.0115 | 0.0104 | 101593.5104 | E500 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0118 | 2004-04-06 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
14 | 6429 | 635 | 20819.1861 | 17639.0511 | 3180.135 | 0.01 | 2.9472 | 31.6667 | 26.0556 | 18.6 | 0.0121 | 0.0103 | 101593.5104 | E510 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 3 | 7.94 | 2003-12-20 | 11 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
15 | 7683 | 754 | 25392.7185 | 22196.7561 | 3195.9624 | 0.0098 | 3.0097 | 32.2222 | 26.1111 | 18.46 | 0.0119 | 0.0101 | 101593.5104 | E520 | 4.652 | 2003-03-16 | 10 | 2.394 | 2004-04-05 | 17 | 15.94 | 2004-07-10 | 16 | 7.89 | 2003-12-20 | 12 | 0.0078 | 2004-03-29 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
16 | 8222 | 803 | 27721.1049 | 22533.2349 | 5187.87 | 0.0098 | 3.0716 | 32.2222 | 26.1667 | 18.76 | 0.0144 | 0.0105 | 101254.8653 | E522 | 5.678 | 2004-03-11 | 10 | 2.562 | 2004-03-31 | 17 | 20.11 | 2003-04-21 | 15 | 7.94 | 2003-12-20 | 11 | 0.0138 | 2004-04-06 | 10 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
17 | 5696 | 556 | 18244.5957 | 13600.1331 | 4644.4626 | 0.0107 | 2.9182 | 31.6667 | 26.0556 | 19.35 | 0.0146 | 0.0113 | 101254.8653 | E525 | 6.031 | 2004-03-16 | 10 | 2.814 | 2004-03-31 | 17 | 35.06 | 2003-04-21 | 16 | 7.94 | 2003-12-20 | 12 | 0.018 | 2002-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
18 | 5531 | 541 | 17977.8747 | 12831.6249 | 5146.2498 | 0.0112 | 2.9608 | 31.1111 | 25.9444 | 19.68 | 0.0157 | 0.0118 | 101254.8653 | E530 | 3.85 | 2004-10-13 | 9 | 2.498 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0081 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
19 | 4689 | 479 | 15914.4507 | 11871.1362 | 4043.3145 | 0.0111 | 3.0794 | 28.3333 | 25.5 | 19.4 | 0.0143 | 0.0116 | 101254.8653 | E540 | 3.455 | 2004-04-30 | 16 | 2.262 | 2012-07-30 | 12 | 15.11 | 2004-05-31 | 16 | 7.89 | 2003-12-20 | 12 | 0.0063 | 2004-04-08 | 8 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
20 | 4855 | 503 | 17120.2641 | 11534.0712 | 5586.1929 | 0.0113 | 3.1953 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104 | E545 | 4.428 | 2004-03-16 | 10 | 2.722 | 2002-07-30 | 12 | 35 | 2004-04-21 | 15 | 7.94 | 2003-12-20 | 12 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0 | system off gives 0.000 | 0 | 0
21 | 3918 | 406 | 13445.0832 | 9302.7009 | 4142.3823 | 0.0113 | 3.1094 | 27.2222 | 25.3333 | 19.76 | 0.0164 | 0.0121 | 101593.5104
22 | 3823 | 399 | 13285.0506 | 8973.8427 | 4311.2079 | 0.0114 | 3.1466 | 26.6667 | 25.2222 | 19.8 | 0.0167 | 0.0122 | 101593.5104
23 | 3748 | 394 | 13192.1379 | 8787.4311 | 4404.7068 | 0.0115 | 3.185 | 26.1111 | 25.1111 | 19.84 | 0.0169 | 0.0123 | 101593.5104
24 | 3880 | 407 | 13754.3037 | 8799.7413 | 4954.5624 | 0.0117 | 3.2084 | 26.1111 | 25.1111 | 20.06 | 0.0178 | 0.0126 | 101593.5104
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3975.1667 | 3119.6667 | 389.0833 | 466.4167 | 13732.9074 | 9925.0255 | 3807.8819 | 0.011 | 3.9139 | 16.8333 | 24.9444
June 25 | 5204.0833 | 4263.4167 | 426.3333 | 514.3333 | 13837.3853 | 9981.0931 | 3856.2923 | 0.0115 | 2.9506 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3061.7917 | 2389.9167 | 311.125 | 360.75 | 9721.3943 | 9721.3943 | 0 | 0.0071 | 3.5991 | 16.8333 | 24.6667
June 25 | 3978.0833 | 3242.9583 | 339.625 | 395.5 | 9760.6941 | 9760.6697 | 0.024425 | 0.0078 | 2.7245 | 29.5 | 24.9444
enter raw doe2 results below
bold entries not changed
tk variable for compr ON
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s; ODB Date: E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor |  | ODB Date: Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Compr + Both Fans Wh: Energy Consumption; Sensible Hour: E v a p o r a t o r C o i l L o a d s
Cases | Total | Compr+cond | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans Wh: Compr + Both Fans; Sensible Date: Sensible; Latent Date: Latent; Sensible + Latent Wh: Sensible + Latent; ODB Date: ODB; Outdoor Humidity Ratio kg/kg: Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (Btu) | (Btu) | (Btu) |  | (°F) | (kg/kg) | (%) | (°F) | (kg/kg) |  | Wh | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | Wh/h | Date | Hour | °F | Date | Hour | kg/kg | Date | Hour
E300 |  | 23875 | 2302 | 10880 | 263705 |  | 73310 | 3.2374 | 75.3 | 0.0092 | 48.28 | 67.8 | 0.0116 | E300 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2001-09-03 | 15 | 31455 | 2001-07-20 | 15 | 95 | 2002-07-20 | 15 | 0.0225 | 2002-10-02 | 9
E310 |  | 28504 | 2687 | 10880 | 332351 |  | 140223 | 3.4175 | 75.3 | 0.0113 | 58.53 |  |  | E310 | 12595 | 2002-07-20 | 15 | 23119 | 2004-06-04 | 16 | 15270 | 2001-09-03 | 15 | 37033 | 2004-09-03 | 16 | from E500 |  |  | from E530
E320 |  | 27912 | 2618 | 10880 | 329216 |  | 115136 | 3.4571 | 75.9 | 0.0101 | 51.25 |  |  | E320 | 12981 | 2002-07-20 | 15 | 31072 | 2002-04-24 | 16 | 31503 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9
E330 |  | 28558 | 2633 | 10880 | 344570 |  | 128508 | 3.5364 | 75.7 | 0.0099 | 50.65 |  |  | E330 | 13407 | 2002-07-20 | 15 | 34490 | 2002-06-14 | 15 | 40809 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9
E340 |  | 28385 | 2640 | 10880 | 338530 |  | 123209 | 3.4956 | 75.7 | 0.0099 | 50.73 |  |  | E340 | 13190 | 2002-07-20 | 15 | 32086 | 2002-05-16 | 16 | 36011 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9
E350 |  | 19668 | 1867 | 10880 | 217109 |  | 54446 | 3.2354 | 79.1 | 0.01 | 45.55 |  |  | E350 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9393 | 2001-09-03 | 15 | 31454 | 2001-07-20 | 15
E360 |  | 43136 | 4181 | 10880 | 545390 |  | 85002 | 3.7058 | 78 | 0.0087 | 41.49 |  |  | E360 | 12726 | 2002-07-20 | 15 | 32065 | 2004-04-24 | 16 | 10336 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9
E400 |  | 19996 | 1865 | 10880 | 221853 |  | 80478 | 3.2519 | 75.3 | 0.01 | 52.25 |  |  | E400 | 11677 | 2004-09-18 | 15 | 23205 | 2002-07-20 | 15 | 32396 | 2003-09-18 | 15 | 49838 | 2003-09-18 | 15
E410 |  | 20819 | 1969 | 10880 | 228057 |  | 65451 | 3.2107 | 75.3 | 0.0095 | 49.63 |  |  | E410 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E420 |  | 22030 | 2096 | 10880 | 241836 |  | 69157 | 3.2175 | 75.3 | 0.0094 | 48.97 |  |  | E420 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9394 | 2003-09-03 | 15 | 31455 | 2001-07-20 | 15
E430 |  | 20931 | 1980 | 10880 | 229339 |  | 67435 | 3.2115 | 75.3 | 0.0094 | 49.3 |  |  | E430 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 11101 | 2003-05-21 | 15 | 31455 | 2001-07-20 | 15
E440 |  | 22093 | 2104 | 10880 | 242856 |  | 70587 | 3.2219 | 75.3 | 0.0093 | 48.57 |  |  | E440 | 11602 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 9391 | 2003-09-03 | 15 | 31455 | 2003-07-20 | 15
E500 |  | 20453 | 1975 | 2369 | 225153 |  | 62594 | 3.2265 | 69 |  |  |  |  | E500 | 10425 | 2002-07-20 | 15 | 20008 | 2002-09-10 | 16 | 7733 | 2001-09-03 | 15 | 27706 | 2001-08-16 | 16
E500 May-Sep |  | 16033 | 1527 | 1837 | 172946 |  | 48097 | 3.1616 | 77 | 0.0114 | 57.47 |  |  | E510 | 11587 | 2002-07-20 | 15 | 22513 | 2003-07-11 | 15 | 8723 | 2003-10-02 | 9 | 31188 | 2001-07-20 | 15
E510 May-Sep |  | 31871 | 3061 | 4099 | 388998 |  | 108196 | 3.5774 | 77.2 | 0.0114 | 57.36 |  |  | E520 | 11014 | 2002-07-20 | 15 | 20154 | 2004-05-26 | 16 | 7785 | 2001-09-03 | 15 | 27878 | 2004-07-23 | 16
E520 |  | 22519 | 2393 | 2871 | 227108 |  | 63015 | 2.956 | 56.7 |  |  |  |  | E522 | 10966 | 2002-07-20 | 15 | 20135 | 2002-07-11 | 16 | 7760 | 2001-09-03 | 15 | 27866 | 2002-08-16 | 16
E522 |  | 21600 | 2182 | 2707 | 226448 |  | 62813 | 3.0728 | 63 |  |  |  |  | E525 | 9531 | 2002-07-20 | 15 | 19850 | 2002-04-24 | 16 | 7663 | 2001-09-03 | 15 | 27466 | 2002-07-08 | 16
E525 |  | 18536 | 1643 | 1885 | 223115 |  | 62032 | 3.528 | 81.1 |  |  |  |  | E530 | Compr + Both Fans Wh: 8055; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19575; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19575; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E530 |  | 15704 | 1580 | 1833 | 159095 |  | 207 | 2.9694 | 69 |  |  |  |  | E540 | Compr + Both Fans Wh: 8939; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19766; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19766; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E540 |  | 17616 | 1939 | 2258 | 160785 |  | 365 | 2.6752 | 56.7 |  |  |  |  | E545 | Compr + Both Fans Wh: 7346; Compr + Both Fans Date: 2002-07-20; Compr + Both Fans Hour: 15; Compr + Both Fans Wh/h: 19474; Sensible Date: 2002-04-24; Sensible Hour: 16; Sensible Wh/h: 0; Sensible + Latent Wh/h: 19474; Sensible + Latent Date: 2002-04-24; Sensible + Latent Hour: 16
E545 |  | 14290 | 1333 | 1501 | 157748 |  | 87 | 3.2355 | 81.1
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [7 empty] | ODB from E500 |  |  | Compr + Both Fans Wh/h: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
OHR from E530
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compr+cond | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. | EHR | Patm | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum |  | Maximum |  |  | Minimum
| (Wh) | (Wh) | (Btu/h) | (Btu/h) | (Btu/h) | (kg/kg) |  | (°F) | (°F) | (°F) | (kg/kg) | (kg/kg) | (in Hg) |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2131 | 237 | 25742 |  | 5657 | 0.0094 | 3.5406 | 64 | 74.9 | 63.212 | 0.0114 | 0.0097 | 29.9 | E300 | 3.857 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E300
2 | 2182 | 241 | 26022 |  | 5322 | 0.0093 | 3.4954 | 65 | 75.1 | enter | 0.0112 | 0.0096 | 29.9 | E310 | 4.128 | 2002-04-30 | 16 | 2.851 | 2002-12-01 | 12 | 26.72 | 2002-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0189 | 2002-10-15 | 9 | 0.0017 | 2001-01-04 | 24 | 100.7 | 2002-10-15 | 9 | 11.97 | 2002-11-06 | 4 | E310
3 | 2131 | 237 | 25746 |  | 5691 | 0.0094 | 3.5411 | 64 | 74.9 | above | 0.0114 | 0.0097 | 30 | E320 | 4.967 | 2002-10-02 | 9 | 2.805 | 2003-12-01 | 15 | 31.5 | 2003-07-08 | 16 | 10.78 | 2001-01-06 | 7 | 0.0176 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 83.67 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4 | E320
4 | 2126 | 236 | 25685 |  | 5646 | 0.0094 | 3.5411 | 64 | 74.9 |  | 0.0114 | 0.0097 | 30 | E330 | 5.595 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 32 | 2003-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0177 | 2002-07-10 | 13 | 0.0017 | 2001-01-04 | 24 | 77.94 | 2003-09-18 | 9 | 11.97 | 2002-11-06 | 4 | E330
5 | 1909 | 215 | 23040 |  | 3689 | 0.009 | 3.5375 | 63 | 74.8 |  | 0.0103 | 0.0092 | 30 | E340 | 5.339 | 2002-10-02 | 9 | 2.801 | 2003-12-01 | 12 | 31.56 | 2003-07-08 | 16 | 8.83 | 2001-01-06 | 6 | 0.0174 | 2002-07-10 | 12 | 0.0017 | 2001-01-04 | 24 | 81.26 | 2003-04-22 | 18 | 11.97 | 2002-11-06 | 4 | E340
6 | 2392 | 259 | 27926 |  | 5959 | 0.0092 | 3.4219 | 67 | 75.4 |  | 0.0113 | 0.0095 | 30 | E350 | 3.863 | 2004-10-05 | 3 | 2.801 | 2003-12-01 | 12 | 34.94 | 2004-06-24 | 24 | 8.83 | 2001-01-06 | 6 | 0.0199 | 2002-08-02 | 22 | 0.0017 | 2001-01-04 | 24 | 81.12 | 2003-08-07 | 21 | 11.97 | 2002-11-06 | 4 | E350
7 | 3576 | 353 | 38324 |  | 9843 | 0.0098 | 3.1412 | 77 | 76.9 |  | 0.0133 | 0.0103 | 30 | E360 | 4.427 | 2002-10-04 | 24 | 2.801 | 2003-12-01 | 12 | 32.56 | 2004-07-20 | 16 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E360
8 | 3480 | 335 | 35045 |  | 4103 | 0.0094 | 2.9516 | 81 | 77.5 |  | 0.0109 | 0.0096 | 30 | E400 | 4.776 | 2003-09-18 | 15 | 2.735 | 2003-12-03 | 13 | 28.83 | 2002-09-18 | 16 | 8.83 | 2001-01-06 | 6 | 0.017 | 2003-04-05 | 21 | 0.0017 | 2001-01-04 | 24 | 85.57 | 2003-04-05 | 21 | 11.97 | 2002-11-06 | 4 | E400
9 | 4993 | 467 | 50645 |  | 10129 | 0.0099 | 2.973 | 84 | 78 |  | 0.0117 | 0.0101 | 30 | E410 | 3.855 | 2002-04-30 | 16 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0169 | 2002-04-02 | 5 | 0.0017 | 2001-01-04 | 24 | 84.79 | 2002-04-02 | 5 | 11.97 | 2002-11-06 | 4 | E410
10 | 5133 | 478 | 52517 |  | 11435 | 0.0102 | 2.9988 | 84 | 78 |  | 0.0125 | 0.0105 | 30 | E420 | 3.759 | 2003-09-27 | 15 | 2.801 | 2003-12-01 | 12 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0141 | 2002-04-17 | 3 | 0.0017 | 2001-01-04 | 24 | 71.53 | 2002-04-17 | 3 | 11.97 | 2002-11-06 | 4 | E420
11 | 5992 | 536 | 60065 |  | 16334 | 0.0107 | 2.9381 | 88 | 78.6 |  | 0.0148 | 0.0113 | 30 | E430 | 3.759 | 2003-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0156 | 2003-04-02 | 4 | 0.0017 | 2001-01-04 | 24 | 78.43 | 2003-04-02 | 4 | 11.97 | 2002-11-06 | 4 | E430
12 | 5513 | 498 | 55229 |  | 12203 | 0.0108 | 2.9363 | 87 | 78.5 |  | 0.0134 | 0.0112 | 30 | E440 | 3.759 | 2002-09-27 | 15 | 2.735 | 2003-12-03 | 13 | 25.11 | 2002-04-22 | 15 | 8.83 | 2001-01-06 | 6 | 0.0137 | 2003-11-16 | 16 | 0.0017 | 2001-01-04 | 24 | 68.85 | 2003-11-16 | 16 | 11.97 | 2002-11-06 | 4 | E440
13 | 6636 | 600 | 66943 |  | 8481 | 0.0102 | 2.9568 | 88 | 78.7 |  | 0.0115 | 0.0104 | 30 | E500 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0118 | 2004-04-06 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E500
14 | 7064 | 635 | 71031 |  | 10850 | 0.01 | 2.9472 | 89 | 78.9 |  | 0.0121 | 0.0103 | 30 | E510 | 5.301 | 2004-10-13 | 9 | 2.652 | 2004-03-30 | 17 | 25.11 | 2001-04-21 | 3 | 7.94 | 2003-12-20 | 11 | 0.0119 | 2001-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E510
15 | 8437 | 754 | 86635 |  | 10904 | 0.0098 | 3.0097 | 90 | 79 |  | 0.0119 | 0.0101 | 30 | E520 | 4.652 | 2003-03-16 | 10 | 2.394 | 2004-04-05 | 17 | 15.94 | 2004-07-10 | 16 | 7.89 | 2003-12-20 | 12 | 0.0078 | 2004-03-29 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E520
16 | 9025 | 803 | 94579 |  | 17700 | 0.0098 | 3.0716 | 90 | 79.1 |  | 0.0144 | 0.0105 | 29.9 | E522 | 5.678 | 2004-03-11 | 10 | 2.562 | 2004-03-31 | 17 | 20.11 | 2003-04-21 | 15 | 7.94 | 2003-12-20 | 11 | 0.0138 | 2004-04-06 | 10 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E522
17 | 6252 | 556 | 62247 |  | 15846 | 0.0107 | 2.9182 | 89 | 78.9 |  | 0.0146 | 0.0113 | 29.9 | E525 | 6.031 | 2004-03-16 | 10 | 2.814 | 2004-03-31 | 17 | 35.06 | 2003-04-21 | 16 | 7.94 | 2003-12-20 | 12 | 0.018 | 2002-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E525
18 | 6072 | 541 | 61337 |  | 17558 | 0.0112 | 2.9608 | 88 | 78.7 |  | 0.0157 | 0.0118 | 29.9 | E530 | 3.85 | 2004-10-13 | 9 | 2.498 | 2002-07-29 | 12 | 25.06 | 2001-04-21 | 16 | 7.94 | 2003-12-20 | 11 | 0.0081 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E530
19 | 5168 | 479 | 54297 |  | 13795 | 0.0111 | 3.0794 | 83 | 77.9 |  | 0.0143 | 0.0116 | 29.9 | E540 | 3.455 | 2004-04-30 | 16 | 2.262 | 2012-07-30 | 12 | 15.11 | 2004-05-31 | 16 | 7.89 | 2003-12-20 | 12 | 0.0063 | 2004-04-08 | 8 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E540
20 | 5358 | 503 | 58411 |  | 19059 | 0.0113 | 3.1953 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | E545 | 4.428 | 2004-03-16 | 10 | 2.722 | 2002-07-30 | 12 | 35 | 2004-04-21 | 15 | 7.94 | 2003-12-20 | 12 | 0.0122 | 2004-07-20 | 15 | system off gives 0.000 |  |  | system off gives 0.000 |  |  | system off gives 0.000 | 0 | 0 | E545
21 | 4324 | 406 | 45872 |  | 14133 | 0.0113 | 3.1094 | 81 | 77.6 |  | 0.0164 | 0.0121 | 30 | [19 empty] | note: RH max may occur when system off
22 | 4222 | 399 | 45326 |  | 14709 | 0.0114 | 3.1466 | 80 | 77.4 |  | 0.0167 | 0.0122 | 30
23 | 4142 | 394 | 45009 |  | 15028 | 0.0115 | 3.185 | 79 | 77.2 |  | 0.0169 | 0.0123 | 30
24 | 4287 | 407 | 46927 |  | 16904 | 0.0117 | 3.2084 | 79 | 77.2 |  | 0.0178 | 0.0126 | 30
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 84210 | 9338 | 11194 | 1124496 |  | 311802 | 0.011 | 3.9139 | 62.3 | 76.9
June 25 |  | 112554 | 10232 | 12344 | 1133051 |  | 315766 | 0.0115 | 2.9506 | 85.1 | 77
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compr+cond | Cond Fan | Indoor Fan | Sens+Lat | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Btu) | (Btu) | (Btu) | (kg/kg) |  | (°F) | (°F)
April 30 |  | 64825 | 7467 | 8658 | 796020 |  | 0 | 0.0071 | 3.5991 | 62.3 | 76.4
June 25 |  | 85982 | 8151 | 9492 | 799238 |  | 2 | 0.0078 | 2.7245 | 85.1 | 76.9

## E
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour | [23 empty] | 7
| 1999-08-16 |  | 15
EnergyPlus {{ engine.config["EnergyPlusVersion"] }}
|  |  | Annual Sums |  |  |  |  | Annual Means |  |  |  | Annual Means |  |  | Annual Hourly Integrated Maxima Consumptions and Loads | [11 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [13 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  | Evaporator Coil Loads
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
CE300 | 35023.7298 | 24161.6379 | Note 1 | 10862.0919 | 78329.9975 | 55166.0635 | 23163.9341 | 3.2419 | 24.0891 | 0.0091654 | 47.9447 | 19.9141 | 0.011608 | CE300 | 11995.7089 | 07/20 | 15:00 | 23463.1755 | 07/20 | 15:00 | 10595.085 | 07/10 | 13:00 | 33057.4738 | 07/20 | 15:00 | 34.775 | 07/20 | 15:00 | 0.021868 | 10/02 | 09:00
CE310 | 39434.1646 | 28572.0727 | Note 1 | 10862.0919 | 97347.6609 | 55065.6279 | 42282.0331 | 3.4071 | 24.0915 | 0.011154 | 57.961 |  |  | CE310 | 12572.0793 | 07/20 | 15:00 | 23145.0651 | 07/11 | 16:00 | 16644.3073 | 08/04 | 15:00 | 37372.5209 | 09/17 | 15:00
CE320 | 39375.0348 | 28512.9429 | Note 1 | 10862.0919 | 97434.8383 | 61751.6548 | 35683.1835 | 3.4172 | 24.2322 | 0.010037 | 51.4531 |  |  | CE320 | 12988.8392 | 07/20 | 15:00 | 31528.7254 | 04/24 | 15:00 | 22756.175 | 10/02 | 10:00 | 40097.0154 | 10/02 | 10:00
CE330 | 40468.7948 | 29606.7029 | Note 1 | 10862.0919 | 103810.929 | 63074.0758 | 40736.8532 | 3.5063 | 24.2953 | 0.0098806 | 50.6065 |  |  | CE330 | 13356.2349 | 07/20 | 15:00 | 34692.1931 | 06/14 | 14:00 | 27596.7005 | 09/18 | 16:00 | 43597.9449 | 10/02 | 09:00
CE340 | 40071.4206 | 29209.3287 | Note 1 | 10862.0919 | 101133.5278 | 62391.3804 | 38742.1474 | 3.4624 | 24.3105 | 0.0099021 | 50.6474 |  |  | CE340 | 13174.9258 | 07/20 | 15:00 | 32737.1011 | 04/24 | 15:00 | 24435.7652 | 10/02 | 10:00 | 41608.4737 | 10/02 | 10:00
CE350 | 31376.2065 | 20514.1146 | Note 1 | 10862.0919 | 66594.5472 | 48335.5891 | 18258.9581 | 3.2463 | 26.2368 | 0.0097964 | 44.5942 |  |  | CE350 | 11995.7017 | 07/20 | 15:00 | 23463.136 | 07/20 | 15:00 | 10595.6426 | 07/10 | 13:00 | 33057.4487 | 07/20 | 15:00
CE360 | 54944.2502 | 44082.1583 | Note 1 | 10862.0919 | 162207.6865 | 134711.1169 | 27496.5697 | 3.6797 | 25.4311 | 0.0086063 | 41.3637 |  |  | CE360 | 12776.4285 | 07/20 | 15:00 | 32409.2976 | 04/24 | 16:00 | 8907.2199 | 10/02 | 10:00 | 38691.4863 | 10/02 | 11:00
CE400 | 31265.6433 | 20403.5514 | Note 1 | 10862.0919 | 66490.4992 | 40599.2192 | 25891.28 | 3.2588 | 24.0905 | 0.010042 | 52.2746 |  |  | CE400 | 11995.6974 | 07/20 | 15:00 | 23463.1222 | 07/20 | 15:00 | 26767.6767 | 09/16 | 15:00 | 41112.206 | 09/16 | 15:00
CE410 | 32010.5061 | 21148.4142 | Note 1 | 10862.0919 | 68071.4219 | 47103.2086 | 20968.2133 | 3.2187 | 24.089 | 0.0094823 | 49.5161 |  |  | CE410 | 11995.7089 | 07/20 | 15:00 | 23463.1755 | 07/20 | 15:00 | 10595.085 | 07/10 | 13:00 | 33057.4738 | 07/20 | 15:00
CE420 | 32978.5453 | 22116.4533 | Note 1 | 10862.0919 | 71248.0904 | 49444.6391 | 21803.4513 | 3.2215 | 24.089 | 0.0093476 | 48.8495 |  |  | CE420 | 11995.7089 | 07/20 | 15:00 | 23463.1755 | 07/20 | 15:00 | 10595.085 | 07/10 | 13:00 | 33057.4738 | 07/20 | 15:00
CE430 | 32085.518 | 21223.4261 | Note 1 | 10862.0919 | 68287.7544 | 46911.71 | 21376.0444 | 3.2176 | 24.089 | 0.009387 | 49.0444 |  |  | CE430 | 11995.7089 | 07/20 | 15:00 | 23463.1755 | 07/20 | 15:00 | 11375.3248 | 10/24 | 13:00 | 33057.4738 | 07/20 | 15:00
CE440 | 33284.8265 | 22422.7346 | Note 1 | 10862.0919 | 72362.1012 | 50001.0328 | 22361.0683 | 3.2272 | 24.0891 | 0.0092307 | 48.2689 |  |  | CE440 | 11995.7089 | 07/20 | 15:00 | 23463.1755 | 07/20 | 15:00 | 10595.085 | 07/10 | 13:00 | 33057.4738 | 07/20 | 15:00
CE500 | 23075.8197 | 20445.2767 | Note 1 | 2630.543 | 65589.3563 | 47357.4403 | 18231.916 | 3.208 | 20.4037 | 0.0091456 | 57.9362 |  |  | CE500 | 10438.5175 | 07/20 | 15:00 | 19795.9105 | 07/20 | 15:00 | 7908.9572 | 06/29 | 16:00 | 27656.4201 | 06/29 | 16:00
CE500 May-Sep | 18030.7145 | 15999.9491 | Note 1 | 2030.7654 | 50355.6741 | 36365.0866 | 13990.5875 | 3.1472 | 24.9827 | 0.010999 | 55.6602 |  |  | CE510 | 11450.7514 | 07/20 | 15:00 | 22227.967 | 07/20 | 16:00 | 9041.0375 | 06/17 | 14:00 | 31194.5493 | 06/17 | 14:00
CE510 May-Sep | 35791.0201 | 31725.1666 | Note 1 | 4065.8535 | 112794.8773 | 81315.4422 | 31479.435 | 3.5554 | 24.9597 | 0.011008 | 55.778 |  |  | CE520 | 11261.8296 | 07/20 | 15:00 | 20012.5751 | 07/30 | 16:00 | 7785.2261 | 06/29 | 16:00 | 27731.0711 | 06/29 | 16:00
CE520 | 25812.8973 | 22672.1954 | Note 1 | 3140.7019 | 66213.2769 | 47983.7484 | 18229.5285 | 2.9205 | 13.6259 | 0.0060157 | 60.9282 |  |  | CE522 | 10902.675 | 07/20 | 15:00 | 19901.8714 | 07/20 | 15:00 | 7850.1656 | 06/29 | 16:00 | 27698.162 | 06/29 | 16:00
CE522 | 24385.5401 | 21506.6752 | Note 1 | 2878.8649 | 65893.8706 | 47663.109 | 18230.7617 | 3.0639 | 17.0327 | 0.0074805 | 59.7074 |  |  | CE525 | 9588.2506 | 07/20 | 15:00 | 19599.0538 | 07/20 | 15:00 | 8006.3955 | 06/29 | 16:00 | 27564.3415 | 06/29 | 16:00
CE525 | 20781.3508 | 18589.1036 | Note 1 | 2192.2472 | 65028.3172 | 46796.3098 | 18232.0073 | 3.4982 | 27.1287 | 0.01338 | 53.7167 |  |  | CE530 | 8293.041 | 07/20 | 15:00 | 19656.1402 | 07/20 | 15:00 | 110.1783 | 03/16 | 10:00 | 19656.1402 | 07/20 | 15:00
CE530 | 17993.9617 | 15872.2483 | Note 1 | 2121.7134 | 46988.5521 | 46988.3103 | 0.24183 | 2.9604 | 20.5951 | 0.0064848 | 47.5315 |  |  | CE540 | 9076.4428 | 07/20 | 15:00 | 19812.465 | 07/20 | 15:00 | 1636.359 | 03/11 | 10:00 | 19812.465 | 07/20 | 15:00
CE540 | 20122.7341 | 17628.9433 | Note 1 | 2493.7908 | 47482.0855 | 47473.2183 | 8.8672 | 2.6934 | 13.8017 | 0.0043402 | 46.1769 |  |  | CE545 | 7767.989 | 07/20 | 15:00 | 19538.7609 | 07/20 | 15:00 | 8.2784e-12 | 05/29 | 13:00 | 19538.7609 | 07/20 | 15:00
CE545 | 16608.6011 | 14743.4176 | Note 1 | 1865.1834 | 46635.6951 | 46635.6951 | 3.5428e-12 | 3.1632 | 27.3219 | 0.0067479 | 38.63
|  |  |  | June 28 Hourly Output - Case CE300 | [10 empty] | Compr + Both Fans Wh: Annual Hourly Integrated Maxima and Minima - COP2 and Zone; Sensible + Latent °C: Annual Hourly Integrated Maxima and Minima - COP2 and Zone
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum* |  | Cases
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 2153.3475 | Note 1 | 7602.8745 | 5807.8573 | 1795.0172 | 0.0092568 | 3.5307 | 17.9875 | 23.945 |  | 0.011202 |  |  | CE300 | 3.9232 | 04/30 | 15:00 | 2.7744 | 06/13 | 17:00 | 25.0033 | 09/23 | 08:00 | 8.7263 | 01/06 | 06:00 | 0.01352 | 11/16 | 17:00 | 0.0019292 | 01/11 | 03:00 | 67.7762 | 11/16 | 17:00 | 14.3878 | 11/06 | 06:00 | CE300
2 | 2166.9933 | Note 1 | 7628.0999 | 5850.1562 | 1777.9436 | 0.0092201 | 3.5201 | 18.1125 | 23.9636 |  | 0.011296 |  |  | CE310 | 4.1954 | 04/30 | 15:00 | 2.8671 | 12/01 | 15:00 | 26.5567 | 07/20 | 16:00 | 8.7262 | 01/06 | 06:00 | 0.015502 | 10/01 | 08:00 | 0.0019435 | 01/05 | 07:00 | 77.9255 | 10/02 | 08:00 | 15.471 | 11/06 | 08:00 | CE310
3 | 2147.8736 | Note 1 | 7579.4624 | 5806.3857 | 1773.0767 | 0.0092267 | 3.5288 | 17.9875 | 23.9451 |  | 0.011199 |  |  | CE320 | 3.9648 | 09/16 | 15:00 | 2.8231 | 03/31 | 15:00 | 31.844 | 07/20 | 15:00 | 7.7562 | 01/06 | 06:00 | 0.017703 | 10/01 | 11:00 | 0.0019351 | 01/11 | 03:00 | 82.7149 | 09/18 | 10:00 | 14.7974 | 11/06 | 06:00 | CE320
4 | 2109.7575 | Note 1 | 7463.8071 | 5740.6566 | 1723.1504 | 0.0091699 | 3.5378 | 17.8 | 23.9169 |  | 0.011061 |  |  | CE330 | 4.0962 | 09/16 | 14:00 | 2.8286 | 03/31 | 15:00 | 31.4963 | 07/20 | 15:00 | 8.7247 | 01/06 | 06:00 | 0.017823 | 07/10 | 12:00 | 0.0019292 | 01/11 | 03:00 | 76.6386 | 09/22 | 20:00 | 14.3879 | 11/06 | 06:00 | CE330
5 | 2031.5836 | Note 1 | 7218.877 | 5611.5024 | 1607.3746 | 0.009048 | 3.5533 | 17.425 | 23.8612 |  | 0.010484 |  |  | CE340 | 4.0147 | 09/16 | 15:00 | 2.8286 | 03/31 | 15:00 | 31.7451 | 07/20 | 15:00 | 8.7247 | 01/06 | 06:00 | 0.017707 | 07/10 | 12:00 | 0.0019292 | 01/11 | 03:00 | 80.5452 | 09/18 | 10:00 | 14.3879 | 11/06 | 06:00 | CE340
6 | 2181.6446 | Note 1 | 7563.2201 | 6012.3325 | 1550.8876 | 0.0089018 | 3.4668 | 18.575 | 24.0335 |  | 0.010648 |  |  | CE350 | 4.3453 | 10/13 | 01:00 | 2.7744 | 06/13 | 17:00 | 35.0021 | 10/01 | 02:00 | 8.7263 | 01/06 | 06:00 | 0.016945 | 10/02 | 01:00 | 0.0019292 | 01/11 | 03:00 | 67.7762 | 11/16 | 17:00 | 14.3878 | 11/06 | 06:00 | CE350
7 | 2926.8472 | Note 1 | 9393.041 | 7528.0125 | 1865.0285 | 0.0091706 | 3.2093 | 22.9 | 24.6841 |  | 0.012288 |  |  | CE360 | 4.4308 | 10/04 | 24:00 | 2.8286 | 03/31 | 15:00 | 32.8198 | 07/10 | 13:00 | 8.7265 | 01/06 | 06:00 | 0.01352 | 11/16 | 17:00 | 0.0019292 | 01/11 | 03:00 | 67.776 | 11/16 | 17:00 | 14.3878 | 11/06 | 06:00 | CE360
8 | 3571.6614 | Note 1 | 10820.4962 | 8751.3077 | 2069.1885 | 0.0094818 | 3.0295 | 26.375 | 25.208 |  | 0.011849 |  |  | CE400 | 4.0961 | 09/16 | 14:00 | 2.7744 | 06/13 | 17:00 | 26.9032 | 09/16 | 16:00 | 8.7263 | 01/06 | 06:00 | 0.016893 | 04/05 | 22:00 | 0.0019292 | 01/11 | 03:00 | 84.6321 | 04/05 | 22:00 | 13.9255 | 11/06 | 06:00 | CE400
9 | 4771.5975 | Note 1 | 14280.6923 | 11758.2673 | 2522.4251 | 0.0096209 | 2.9929 | 28.2625 | 25.4906 |  | 0.01158 |  |  | CE410 | 4.0403 | 04/30 | 15:00 | 2.7744 | 06/13 | 17:00 | 25.0033 | 09/23 | 08:00 | 8.7263 | 01/06 | 06:00 | 0.016431 | 04/06 | 05:00 | 0.0019292 | 01/11 | 03:00 | 82.3688 | 04/06 | 01:00 | 14.1877 | 11/06 | 06:00 | CE410
10 | 5029.2702 | Note 1 | 15005.1999 | 11985.6398 | 3019.5601 | 0.0099775 | 2.9836 | 28.9 | 25.5865 |  | 0.012406 |  |  | CE420 | 3.8446 | 05/21 | 15:00 | 2.7744 | 06/13 | 17:00 | 25.0033 | 09/23 | 08:00 | 8.7263 | 01/06 | 06:00 | 0.014607 | 04/02 | 18:00 | 0.0019292 | 01/11 | 03:00 | 73.2771 | 04/02 | 18:00 | 13.9256 | 11/06 | 06:00 | CE420
11 | 5485.3257 | Note 1 | 16127.9094 | 12473.8609 | 3654.0485 | 0.010392 | 2.9402 | 30.275 | 25.7953 |  | 0.013949 |  |  | CE430 | 3.8044 | 05/21 | 15:00 | 2.7744 | 06/13 | 17:00 | 25.0038 | 04/24 | 20:00 | 8.7263 | 01/06 | 06:00 | 0.016146 | 04/02 | 05:00 | 0.0019292 | 01/11 | 03:00 | 80.716 | 04/02 | 05:00 | 13.9255 | 11/06 | 06:00 | CE430
12 | 5708.5515 | Note 1 | 16742.4591 | 12655.4944 | 4086.9647 | 0.010701 | 2.9329 | 30.7875 | 25.8718 |  | 0.013761 |  |  | CE440 | 3.8044 | 05/21 | 15:00 | 2.7744 | 06/13 | 17:00 | 25.0038 | 04/24 | 20:00 | 8.7263 | 01/06 | 06:00 | 0.01352 | 11/16 | 17:00 | 0.0019292 | 01/11 | 03:00 | 67.7762 | 11/16 | 17:00 | 13.9255 | 11/06 | 06:00 | CE440
13 | 7233.0374 | Note 1 | 21873.9592 | 17378.5032 | 4495.456 | 0.010129 | 3.0242 | 30.9125 | 25.8849 |  | 0.011999 |  |  | CE500 | 4.2343 | 03/16 | 10:00 | 2.6947 | 07/30 | 12:00 | 25.0017 | 04/05 | 19:00 | 8.8363 | 12/21 | 01:00 | 0.01138 | 07/20 | 15:00 | 0.0069608 | 12/20 | 12:00 | 100 | 11/21 | 24:00 | 53.4256 | 04/30 | 04:00 | CE500
14 | 7085.957 | Note 1 | 20933.4385 | 17574.6097 | 3358.8288 | 0.009694 | 2.9542 | 31.475 | 25.9689 |  | 0.011528 |  |  | CE510 | 4.7069 | 10/05 | 01:00 | 2.8993 | 03/31 | 15:00 | 25.0017 | 04/05 | 19:00 | 8.8363 | 12/21 | 01:00 | 0.01139 | 07/20 | 15:00 | 0.0069608 | 12/20 | 12:00 | 100 | 11/21 | 24:00 | 53.5323 | 05/04 | 04:00 | CE510
15 | 8689.9561 | Note 1 | 26432.9109 | 22454.4561 | 3978.4548 | 0.009521 | 3.0418 | 32.0125 | 26.0513 |  | 0.012086 |  |  | CE520 | 3.838 | 04/30 | 15:00 | 2.4618 | 07/30 | 12:00 | 15.2669 | 07/20 | 16:00 | 8.733 | 12/21 | 01:00 | 0.007104 | 07/20 | 16:00 | 0.006466 | 11/10 | 07:00 | 93.6042 | 12/20 | 11:00 | 61.1938 | 11/10 | 04:00 | CE520
16 | 8842.8175 | Note 1 | 26943.3568 | 22527.6692 | 4415.6877 | 0.0096238 | 3.0469 | 32.2 | 26.0827 |  | 0.013492 |  |  | CE522 | 4.0074 | 04/30 | 15:00 | 2.5777 | 07/30 | 12:00 | 20.0027 | 04/17 | 24:00 | 8.7911 | 12/21 | 01:00 | 0.0089745 | 07/20 | 15:00 | 0.0069388 | 12/20 | 12:00 | 100 | 12/16 | 03:00 | 57.8308 | 04/30 | 04:00 | CE522
17 | 5791.0239 | Note 1 | 16525.7603 | 13046.9672 | 3478.7931 | 0.010361 | 2.8537 | 31.8875 | 26.0396 |  | 0.014504 |  |  | CE525 | 4.6776 | 03/16 | 10:00 | 2.9333 | 07/30 | 12:00 | 34.9964 | 03/11 | 12:00 | 8.9123 | 12/21 | 01:00 | 0.017848 | 07/20 | 15:00 | 0.006998 | 12/20 | 12:00 | 100 | 11/12 | 24:00 | 46.1063 | 10/05 | 02:00 | CE525
18 | 5952.6309 | Note 1 | 17405.5618 | 12851.4495 | 4554.1122 | 0.010924 | 2.924 | 31.325 | 25.9556 |  | 0.015288 |  |  | CE530 | 3.9202 | 03/16 | 10:00 | 2.4945 | 07/30 | 12:00 | 25.0027 | 04/05 | 20:00 | 8.9817 | 12/21 | 02:00 | 0.0067904 | 03/11 | 01:00 | 0.0064432 | 10/17 | 10:00 | 91.698 | 12/20 | 11:00 | 32.5613 | 04/18 | 18:00 | CE530
19 | 5617.7336 | Note 1 | 17082.2323 | 12151.7364 | 4930.496 | 0.011075 | 3.0408 | 29.35 | 25.6558 |  | 0.01493 |  |  | CE540 | 3.5169 | 03/16 | 10:00 | 2.2794 | 07/30 | 12:00 | 15.0028 | 04/16 | 01:00 | 8.8775 | 12/21 | 01:00 | 0.0067904 | 03/11 | 01:00 | 0.0038106 | 10/17 | 10:00 | 54.8557 | 12/20 | 11:00 | 35.8475 | 09/28 | 18:00 | CE540
20 | 5315.9924 | Note 1 | 16742.9941 | 11537.4992 | 5205.4948 | 0.011126 | 3.1496 | 27.6125 | 25.3934 |  | 0.01597 |  |  | CE545 | 4.2157 | 03/16 | 10:00 | 2.6585 | 07/30 | 12:00 | 35.0003 | 07/14 | 18:00 | 9.0584 | 12/21 | 02:00 | 0.0067904 | 12/31 | 17:00 | 0.0067904 | 04/01 | 01:00 | 96.074 | 12/20 | 11:00 | 19.2467 | 04/18 | 17:00 | CE545
21 | 4369.5515 | Note 1 | 13611.4239 | 9049.8699 | 4561.554 | 0.011355 | 3.1151 | 27.2 | 25.333 |  | 0.01681 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 4323.8097 | Note 1 | 13561.3024 | 8939.7425 | 4621.5598 | 0.011403 | 3.1364 | 26.8875 | 25.2865 |  | 0.016771
23 | 4215.998 | Note 1 | 13364.985 | 8740.9679 | 4624.0171 | 0.01142 | 3.1701 | 26.325 | 25.2013 |  | 0.016784
24 | 4194.2432 | Note 1 | 13370.4665 | 8661.2371 | 4709.2294 | 0.011476 | 3.1878 | 26.1 | 25.1674 |  | 0.017077
Case CE500 Average Daily Outputs - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4019.3858 | 3501.4974 | Note 1 | 517.8884 | 13653.7633 | 9849.8339 | 3803.9295 | 0.010646 | 3.8588 | 16.8146 | 24.982
June 25 | 5244.3836 | 4677.7875 | Note 1 | 566.5961 | 13734.0071 | 9923.758 | 3810.249 | 0.011144 | 2.9346 | 29.5167 | 24.9831
Case CE 530 Average Daily Outputs - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3131.8977 | 2716.0206 | Note 1 | 415.8771 | 9778.7416 | 9778.7416 | 3.0182e-13 | 0.006466 | 3.4048 | 16.8146 | 25.0003
June 25 | 4090.8917 | 3632.6991 | Note 1 | 458.1925 | 9843.2403 | 9843.2403 | 3.5571e-13 | 0.006466 | 2.7405 | 29.5167 | 25.0003
Note 1 - Condenser fan power included with compressor power; cannot breakout

## F
E300OUT2.XLS, Mar 20, 2002 | [5 empty] | HVAC BESTEST model Cody-Tau, Neural Network + Linear Extrapolation + rint + Enthalpy
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545 | [5 empty] | Output file Name |  | BESTEST300N2_nn_int.xls
CODYRUN results received 07 May 2003
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [15 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity | Relative |  |  | Energy Consumption |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Humidity | Cases |  | Compr + Both Fans |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) | (%) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 34976.411 | 21770.001 | 2326.49 | 10879.92 | 77744.589 | 55209.465 | 22535.143 | 3.2264 | 24.0816 | 0.0091748 | 47.8261 | 19.9145 | 0.011649 | 0.47826 | E300 | 11932 | 1900-07-20 | 15 | 23457 | 1900-07-20 | 15 | 10375 | 1900-09-03 | 15 | 32502 | 1900-07-20 | 15 | 35 | 1900-07-20 | 15 | 0.022406 | 1900-10-02 | 9
E310 | 39519.569 | 25936.821 | 2702.828 | 10879.92 | 97295.866 | 55185.072 | 42110.836 | 3.3972 | 24.0897 | 0.011175 | 57.841 |  |  | 0.57841 | E310 | 12653 | 1900-07-20 | 15 | 23078 | 1900-09-10 | 15 | 16112 | 1900-08-04 | 15 | 37261 | 1900-09-03 | 15
E320 | 39400.815 | 25846.026 | 2674.869 | 10879.92 | 97141.307 | 62008.804 | 35132.592 | 3.406 | 24.3274 | 0.010049 | 51.1034 |  |  | 0.51103 | E320 | 13104 | 1900-07-20 | 15 | 31134 | 1900-06-03 | 16 | 21697 | 1900-09-17 | 12 | 39904 | 1900-09-03 | 16
E330 | 40535.137 | 26927.733 | 2727.484 | 10879.92 | 103712.915 | 62649.459 | 41063.373 | 3.4973 | 24.2955 | 0.0098116 | 50.0848 |  |  | 0.50085 | E330 | 13467 | 1900-07-20 | 15 | 33997 | 1900-04-24 | 16 | 28184 | 1900-09-18 | 15 | 43978 | 1900-10-02 | 9
E340 | 40065.261 | 26472.79 | 2712.551 | 10879.92 | 100676.21 | 62380.56 | 38295.624 | 3.4495 | 24.3089 | 0.0098683 | 50.2967 |  |  | 0.50297 | E340 | 13277 | 1900-07-20 | 15 | 32940 | 1900-04-24 | 16 | 24225 | 1900-09-03 | 17 | 41366 | 1900-09-03 | 15
E350 | 31586.592 | 18738.055 | 1968.617 | 10879.92 | 66860.163 | 48588.802 | 18271.394 | 3.2289 | 26.2686 | 0.0097585 | 44.3162 |  |  | 0.44316 | E350 | 11932 | 1900-07-20 | 15 | 23457 | 1900-07-20 | 15 | 10755 | 1900-10-02 | 8 | 32502 | 1900-07-20 | 15
E360 | 54843.258 | 39697.162 | 4266.176 | 10879.92 | 161200.179 | 134205.707 | 26994.482 | 3.6667 | 25.4809 | 0.0085524 | 40.871 |  |  | 0.40871 | E360 | 12863 | 1900-07-20 | 15 | 31981 | 1900-04-24 | 16 | 8859 | 1900-09-03 | 17 | 38322 | 1900-10-02 | 10
E400 | [14 empty] | E400 | bar: Wh to Sensible + Latent Hour
E410 | [14 empty] | E410 | bar: Wh to Sensible + Latent Hour
E420 | [14 empty] | E420 | bar: Wh to Sensible + Latent Hour
E430 | [14 empty] | E430 | bar: Wh to Sensible + Latent Hour
E440 | [14 empty] | E440 | bar: Wh to Sensible + Latent Hour
E500 | 22322.953 | 17857.852 | 1911.869 | 2553.232 | 63105.366 | 44874.225 | 18231.141 | 3.192 | 21.0978 | 0.010218 | 65.9419 |  |  | 0.65942 | E500 | 10177 | 1900-07-20 | 15 | 18776 | 1900-06-04 | 15 | 7805 | 1900-06-29 | 16 | 26567 | 1900-06-29 | 16
E500 May-Sep | 17434.537 | 13988.512 | 1475.528 | 1970.497 | 48439.57 | 34448.151 | 13991.418 | 3.1324 | 25 | 0.011329 | 57.0722 |  |  | 0.57072 | E510 | 11186 | 1900-07-20 | 15 | 21121 | 1900-06-04 | 13 | 8850 | 1900-06-17 | 14 | 29948 | 1900-06-17 | 14
E510 May-Sep | 34848.637 | 27901.957 | 2974.4 | 3972.28 | 108979.013 | 77498.985 | 31479.856 | 3.5295 | 25 | 0.011328 | 57.0615 |  |  | 0.57062 | E520 | 11044 | 1900-07-20 | 15 | 18969 | 1900-07-20 | 16 | 7726 | 1900-06-30 | 16 | 26675 | 1900-07-20 | 16
E520 | 25131.07 | 19654.972 | 2344.827 | 3131.271 | 63212.102 | 44976.724 | 18235.133 | 2.8733 | 14.1421 | 0.0070234 | 70.2268 |  |  | 0.70227 | E522 | 10639 | 1900-07-20 | 15 | 18785 | 1900-06-04 | 15 | 7743 | 1900-06-29 | 16 | 26514 | 1900-06-29 | 16
E522 | 23619.744 | 18689.799 | 2110.833 | 2819.112 | 63157.03 | 44924.113 | 18233.151 | 3.0363 | 17.729 | 0.0085797 | 68.2314 |  |  | 0.68231 | E525 | 9419 | 1900-07-20 | 15 | 18759 | 1900-06-04 | 15 | 7938 | 1900-06-29 | 16 | 26683 | 1900-06-29 | 16
E525 | 20241.713 | 16506.802 | 1599.203 | 2135.708 | 63001.558 | 44775.105 | 18226.509 | 3.4796 | 27.7709 | 0.01398 | 60.1387 |  |  | 0.60139 | E530 | 7992 | 1900-07-20 | 15 | 18776 | 1900-06-04 | 15 | 179 | 1900-03-11 | 11 | 18776 | 1900-06-04 | 15
E530 | 17442.468 | 13855.928 | 1535.684 | 2050.856 | 44875.414 | 44874.225 | 1.186 | 2.9156 | 21.0978 | 0.0057975 | 41.4516 |  |  | 0.41452 | E540 | 8846 | 1900-07-20 | 15 | 18794 | 1900-06-04 | 15 | 845 | 1900-03-11 | 10 | 18794 | 1900-06-04 | 15
E540 | 19536.572 | 15163.82 | 1872.336 | 2500.416 | 44979.842 | 44976.747 | 3.09 | 2.6403 | 14.1406 | 0.0038546 | 40.0509 |  |  | 0.40051 | E545 | 7351 | 1900-07-20 | 15 | 18759 | 1900-06-04 | 15 | 4 | 1900-07-20 | 15 | 18764 | 1900-07-20 | 15
E545 | 15791.081 | 12750.623 | 1301.791 | 1738.667 | 44775.11 | 44775.105 | 0.004 | 3.1863 | 27.7166 | 0.006749 | 36.8747 |  |  | 0.36875
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [11 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour | MaxRH | MinRH
1 | 1886 | 237 | 7472 | 5788 | 1684 | 0.009276 | 3.5195 | 17.8 | 23.92 | 17.155 | 0.0111 |  |  |  | E300 | 3.8706 | 1900-04-30 | 16 | 2.7856 | 1900-06-13 | 17 | 25.05 | 1900-02-20 | 17 | 8 | 1900-01-05 | 5 | 0.013457 | 1900-11-16 | 16 | 0.001968 | 1900-01-10 | 3 | 68 | 1900-11-16 | 16 | 15 | 1900-11-06 | 5
2 | 1964 | 244 | 7707 | 5961 | 1747 | 0.009302 | 3.4905 | 18.3 | 24 | 17.238 | 0.011462 |  |  |  | E310 | 4.1276 | 1900-04-30 | 15 | 2.8726 | 1900-12-01 | 15 | 26.62 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.015432 | 1900-10-02 | 8 | 0.002019 | 1900-01-04 | 7 | 77 | 1900-06-12 | 8 | 16 | 1900-11-06 | 8
3 | 1881 | 236 | 7445 | 5788 | 1657 | 0.009239 | 3.5168 | 17.8 | 23.92 | 17.12 | 0.0111 |  |  |  | E320 | 3.9433 | 1900-09-16 | 15 | 2.8145 | 1900-03-31 | 15 | 32.32 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017547 | 1900-07-10 | 12 | 0.001968 | 1900-01-10 | 3 | 83 | 1900-09-03 | 17 | 15 | 1900-11-06 | 5
4 | 1878 | 236 | 7432 | 5788 | 1644 | 0.009201 | 3.5156 | 17.8 | 23.92 | 17.102 | 0.0111 |  |  |  | E330 | 4.1219 | 1900-06-17 | 16 | 2.8233 | 1900-03-31 | 15 | 31.9 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017045 | 1900-07-10 | 13 | 0.001968 | 1900-01-10 | 3 | 76 | 1900-06-10 | 18 | 15 | 1900-11-06 | 5
5 | 1756 | 224 | 7000 | 5580 | 1420 | 0.008969 | 3.5354 | 17.2 | 23.83 | 16.787 | 0.01018 |  |  |  | E340 | 4.0172 | 1900-09-16 | 16 | 2.8233 | 1900-03-31 | 15 | 32.15 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.017272 | 1900-07-10 | 13 | 0.001968 | 1900-01-10 | 3 | 80 | 1900-09-03 | 17 | 15 | 1900-11-06 | 5
6 | 2075 | 253 | 7915 | 6341 | 1574 | 0.009012 | 3.3999 | 19.4 | 24.16 | 17.032 | 0.011001 |  |  |  | E350 | 3.9321 | 1900-10-04 | 24 | 2.7859 | 1900-06-13 | 17 | 35 | 1900-04-21 | 1 | 8 | 1900-01-05 | 5 | 0.016479 | 1900-10-02 | 2 | 0.001968 | 1900-01-10 | 3 | 70 | 1900-10-02 | 8 | 15 | 1900-11-06 | 5
7 | 3035 | 334 | 10450 | 8277 | 2173 | 0.00949 | 3.1018 | 25 | 25 | 17.911 | 0.01314 |  |  |  | E360 | 4.432 | 1900-10-04 | 24 | 2.8233 | 1900-03-31 | 15 | 33 | 1900-07-20 | 15 | 8 | 1900-01-05 | 5 | 0.013457 | 1900-11-16 | 16 | 0.001968 | 1900-01-10 | 3 | 68 | 1900-11-16 | 16 | 15 | 1900-11-06 | 5
8 | 3303 | 352 | 10813 | 9038 | 1775 | 0.009314 | 2.9584 | 27.2 | 25.33 | 17.646 | 0.011075 |  |  |  | E400
9 | 4483 | 463 | 14631 | 11971 | 2660 | 0.009708 | 2.9581 | 28.9 | 25.59 | 18.118 | 0.011995 |  |  |  | E410
10 | 4594 | 472 | 15099 | 11971 | 3128 | 0.010041 | 2.9805 | 28.9 | 25.59 | 18.442 | 0.01276 |  |  |  | E420
11 | 5238 | 516 | 16722 | 12731 | 3991 | 0.010588 | 2.9062 | 31.1 | 25.91 | 19.142 | 0.014809 |  |  |  | E430
12 | 5066 | 504 | 16258 | 12559 | 3699 | 0.01058 | 2.9189 | 30.6 | 25.84 | 18.935 | 0.013253 |  |  |  | E440
13 | 6442 | 642 | 21090 | 17422 | 3669 | 0.009975 | 2.9771 | 31.1 | 25.91 | 18.326 | 0.011329 |  |  |  | E500 | 4.1846 | 1900-03-16 | 10 | 2.6665 | 1900-07-30 | 12 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.011713 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-11-14 | 5 | 54 | 1900-10-04 | 24
14 | 6523 | 645 | 21067 | 17629 | 3438 | 0.009778 | 2.939 | 31.7 | 26 | 18.269 | 0.011729 |  |  |  | E510 | 4.6896 | 1900-10-04 | 24 | 2.8817 | 1900-03-31 | 15 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.011716 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-11-14 | 5 | 54 | 1900-10-04 | 23
15 | 8000 | 785 | 26636 | 22491 | 4145 | 0.009579 | 3.032 | 32.2 | 26.08 | 18.239 | 0.012379 |  |  |  | E520 | 3.8017 | 1900-04-30 | 16 | 2.3333 | 1900-01-28 | 10 | 15.98 | 1900-07-20 | 15 | 8.51 | 1900-12-20 | 20 | 0.007566 | 1900-07-20 | 15 | 0.006525 | 1900-11-27 | 23 | 95 | 1900-12-20 | 17 | 61 | 1900-11-27 | 22
16 | 8169 | 799 | 27416 | 22491 | 4925 | 0.009733 | 3.0571 | 32.2 | 26.08 | 18.557 | 0.014232 |  |  |  | E522 | 3.9858 | 1900-04-30 | 16 | 2.4286 | 1900-03-30 | 17 | 20.05 | 1900-03-13 | 22 | 8.54 | 1900-12-20 | 20 | 0.009398 | 1900-07-20 | 15 | 0.006908 | 1900-12-20 | 20 | 100 | 1900-12-15 | 1 | 60 | 1900-10-04 | 23
17 | 5306 | 519 | 16702 | 12939 | 3763 | 0.01044 | 2.8673 | 31.7 | 26 | 19.063 | 0.01473 |  |  |  | E525 | 4.6381 | 1900-03-16 | 10 | 2.8941 | 1900-07-29 | 12 | 35 | 1900-03-11 | 10 | 8.54 | 1900-12-20 | 20 | 0.017626 | 1900-07-20 | 15 | 0.006909 | 1900-12-20 | 20 | 100 | 1900-11-11 | 23 | 44 | 1900-05-04 | 4
18 | 5381 | 528 | 17312 | 12729 | 4582 | 0.010912 | 2.9298 | 31.1 | 25.91 | 19.458 | 0.015684 |  |  |  | E530 | 3.84 | 1900-03-16 | 10 | 2.4733 | 1900-07-29 | 12 | 25.02 | 1900-03-30 | 17 | 8.54 | 1900-12-20 | 20 | 0.005491 | 1900-04-01 | 1 | 0.005454 | 1900-11-01 | 21 | 79 | 1900-12-20 | 8 | 28 | 1900-04-01 | 10
19 | 4791 | 492 | 16232 | 11761 | 4470 | 0.010914 | 3.0725 | 28.3 | 25.5 | 19.199 | 0.014539 |  |  |  | E540 | 3.6667 | 1900-03-11 | 22 | 2.1429 | 1900-04-05 | 20 | 15.05 | 1900-01-27 | 20 | 8.51 | 1900-12-20 | 20 | 0.003256 | 1900-04-01 | 1 | 0.003253 | 1900-04-29 | 23 | 47 | 1900-12-20 | 6 | 31 | 1900-04-01 | 1
20 | 4809 | 498 | 16867 | 11381 | 5486 | 0.011269 | 3.1783 | 27.2 | 25.33 | 19.65 | 0.016878 |  |  |  | E545 | 4.1565 | 1900-03-16 | 10 | 2.692 | 1900-07-29 | 12 | 35 | 1900-03-11 | 10 | 8.54 | 1900-12-20 | 20 | 0.006689 | 1900-04-01 | 1 | 0.006685 | 1900-07-20 | 15 | 97 | 1900-12-20 | 4 | 19 | 1900-04-01 | 10
21 | 3939 | 408 | 13484 | 9036 | 4447 | 0.011348 | 3.1019 | 27.2 | 25.33 | 19.706 | 0.016878 |  |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3852 | 402 | 13322 | 8864 | 4459 | 0.011383 | 3.1316 | 26.7 | 25.25 | 19.697 | 0.016832
23 | 3752 | 395 | 13139 | 8656 | 4482 | 0.011416 | 3.1683 | 26.1 | 25.16 | 19.694 | 0.016889
24 | 3794 | 399 | 13323 | 8656 | 4666 | 0.011507 | 3.1774 | 26.1 | 25.16 | 19.805 | 0.017329
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3901.0417 | 3020.0417 | 377.25 | 503.75 | 13169.5417 | 9365.4583 | 3804.375 | 0.010938 | 3.8372 | 16.8833 | 25
June 25 | 5066.5 | 4105.9583 | 411.3333 | 549.2083 | 13198.0833 | 9387.625 | 3810.4167 | 0.011479 | 2.9213 | 29.5167 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3091.5417 | 2378.4583 | 305.3333 | 407.75 | 9365.4583 | 9365.4583 | 0 | 0.005485 | 3.4604 | 16.8833 | 25
June 25 | 3934.625 | 3165.5833 | 329.25 | 439.7917 | 9387.625 | 9387.625 | 0 | 0.005478 | 2.69 | 29.5167 | 25

## G
E300OUT2.XLS, Mar 20, 2002
Output spreadsheet for HVAC BESTEST, Cases Series: E300 - E545
HOT3000 received 07/21/03
INSTRUCTIONS
1. Use specified units
2. Data entry is restricted to the following ranges:
| B62..L82: |  | Annual Sums, Annual Means, and Other
| M62..N62: |  | Annual Means, E300 Only
| B89..L112: |  | June 28 Hourly Output - Case E300
| B120..L121: |  | Case E500 Average Daily Outputs
| B129..L130: |  | Case E530 Average Daily Outputs
| Q62..AB81: |  | Annual Hourly Integrated Maxima Consumptions and Loads
| AC62..AH62: |  | Annual Hourly Integrated Maxima, Case E300 - Weather Check
| Q89..AN108: |  | Annual Hourly Integrated Maxima and Minima - COP2 and Zone
3. Annual totals are consumption and or loads just for the entire annual simulation. Similarly,
annual means, maxima, and minima are those values which occur for the enitre annual simulation.
"May-Sep" results are taken using May 1 - September 30 data extracted from a full annual
simulation.
4. Output terminology is defined in the output section of the specification for each case where
applicable or in the glossary appendix.
5. Format dates using the appropriate two-digit date followed by a three-letter month code and
two-digit hour code (24 hour clock) as shown below.
MONTH CODES:
| MONTH |  | CODE
| JANUARY |  | Jan
| FEBRUARY |  | Feb
| MARCH |  | Mar
| APRIL |  | Apr
| MAY |  | May
| JUNE |  | Jun
| JULY |  | Jul
| AUGUST |  | Aug
| SEPTEMBER |  | Sep
| OCTOBER |  | Oct
| NOVEMBER |  | Nov
| DECEMBER |  | Dec
For example a maximum value occuring on August 16 during the 15th hour interval (2-3 PM), should
be input as:
| Date |  | Hour
| 1999-08-16 |  | 15
HOT3000 received 07/21/03
|  |  | A n n u a l S u m s |  |  |  |  | A n n u a l M e a n s |  |  |  | Annual Means |  |  | A n n u a l H o u r l y I n t e g r a t e d M a x i m a C o n s u m p t i o n s a n d L o a d s | [12 empty] | E300 Only, Maxima
E 3 0 0 O n l y
[10 empty] | Zone | Zone |  | Outdoor | [14 empty] | Weather Data Checks
| Cooling Energy Consumption |  |  |  | Evaporator Coil Load |  |  |  |  | Humidity | Relative |  | Humidity |  | Energy Consumption |  |  |  |  | E v a p o r a t o r C o i l L o a d s
Cases | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | COP2 | IDB | Ratio | Humidity | ODB | Ratio | Cases | Compr + Both Fans |  |  |  | Sensible |  |  | Latent |  | Sensible + Latent |  |  |  | ODB |  | Outdoor Humidity Ratio
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (°C) | (kg/kg) | (%) | (°C) | (kg/kg) |  | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | Wh | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour
E300 | 35070 | 21876 | 2323 | 10880 | 78257 | 55191 | 23067 | 3.23 | 23.99 | 0.0092 | 47.93 | 19.91 | 0.0116 | E300 | 11548 | 2003-07-20 | 15 | 22908 | 2003-06-04 | 15 | 10392 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15 | 35 | 2003-07-20 | 15 | 0.0223 | 2003-10-02 | 9
E310 | 39608 | 26053 | 2691 | 10880 | 97261 | 55083 | 42178 | 3.38 | 24.01 | 0.0111 | 57.8 |  |  | E310 | 12162 | 2003-08-16 | 16 | 22649 | 2003-06-13 | 16 | 16077 | 2003-09-03 | 16 | 36991 | 2003-09-03 | 16
E320 | 39457 | 25912 | 2681 | 10880 | 96957 | 62734 | 34224 | 3.39 | 24.53 | 0.0099 | 49.94 |  |  | E320 | 12875 | 2003-07-20 | 14 | 30967 | 2003-04-24 | 15 | 21929 | 2003-10-01 | 20 | 39920 | 2003-09-03 | 16
E330 | 40330 | 26775 | 2693 | 10880 | 102008 | 61822 | 40186 | 3.46 | 24.18 | 0.0099 | 50.7 |  |  | E330 | 13335 | 2003-07-20 | 15 | 33421 | 2003-09-09 | 14 | 27488 | 2003-09-18 | 15 | 42415 | 2003-07-10 | 11
E340 | 39947 | 26400 | 2684 | 10880 | 99753 | 61406 | 38346 | 3.42 | 24.21 | 0.0099 | 50.78 |  |  | E340 | 13101 | 2003-07-20 | 14 | 32180 | 2003-04-24 | 15 | 23794 | 2003-10-01 | 20 | 41132 | 2003-09-03 | 16
E350 | 31742 | 18891 | 1970 | 10880 | 67389 | 48768 | 18621 | 3.23 | 26.15 | 0.00977 | 44.56 |  |  | E350 | 11546 | 2003-07-20 | 15 | 22876 | 2003-07-10 | 15 | 11603 | 2003-08-03 | 7 | 32077 | 2003-07-20 | 15
E360 | 55068 | 39941 | 4272 | 10880 | 162168 | 134697 | 27470 | 3.66 | 25.37 | 0.00858 | 41.21 |  |  | E360 | 12762 | 2003-07-20 | 14 | 32179 | 2003-04-24 | 15 | 8934 | 2003-09-03 | 17 | 38451 | 2003-10-02 | 10
E400 | 31413 | 18629 | 1902 | 10880 | 66898 | 41181 | 25717 | 3.26 | 23.99 | 0.01 | 52.01 |  |  | E400 | 11519 | 2003-07-20 | 15 | 22877 | 2003-07-08 | 16 | 26645 | 2003-09-16 | 14 | 40774 | 2003-09-16 | 14
E410 | 31503 | 18685 | 1936 | 10880 | 66175 | 45585 | 20590 | 3.21 | 23.99 | 0.0095 | 49.75 |  |  | E410 | 11549 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10377 | 2003-09-09 | 15 | 32073 | 2003-07-20 | 15
E420 | 33208 | 20214 | 2115 | 10880 | 71803 | 49984 | 21855 | 3.21 | 23.99 | 0.0093 | 48.76 |  |  | E420 | 11548 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10394 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15
E430 | 31818 | 18966 | 1970 | 10880 | 67200 | 46143 | 21057 | 3.21 | 23.99 | 0.0094 | 49.17 |  |  | E430 | 11548 | 2003-07-20 | 15 | 22893 | 2003-07-29 | 15 | 10394 | 2003-09-03 | 15 | 32072 | 2003-07-20 | 15
E440 | 33248 | 20249 | 2120 | 10880 | 72029 | 49785 | 22244 | 3.22 | 23.99 | 0.0092 | 48.23 |  |  | E440 | 11461 | 2003-08-16 | 16 | 22875 | 2003-08-16 | 16 | 10139 | 2003-09-03 | 15 | 31777 | 2003-07-08 | 16
E500 | 23138 | 18522 | 1976 | 2639 | 65614 | 47530 | 18084 | 3.2 | 22.86 | 0.0107 | 63.73 |  |  | E500 | 10274 | 2003-06-04 | 15 | 19818 | 2003-07-29 | 15 | 7762 | 2003-06-29 | 15 | 27555 | 2003-06-29 | 15
E500 May-Sep | 18051 | 14491 | 1524 | 2035 | 50357 | 36480 | 13877 | 3.14 | 25 | 0.0109 | 55.13 |  |  | E510 | 11344 | 2003-07-20 | 14 | 22269 | 2003-07-20 | 14 | 8874 | 2003-06-17 | 13 | 31097 | 2003-06-17 | 13
E510 May-Sep | 35845 | 28721 | 3050 | 4073 | 112781 | 81563 | 31217 | 3.55 | 25 | 0.0109 | 55.24 |  |  | E520 | 10684 | 2003-06-04 | 15 | 20378 | 2003-05-23 | 15 | 7964 | 2003-05-23 | 15 | 28343 | 2003-05-23 | 15
E520 | 25781 | 20185 | 2396 | 3200 | 66146 | 48059 | 18087 | 2.92 | 14.89 | 0.00763 | 72.17 |  |  | E522 | 10747 | 2003-08-16 | 15 | 19920 | 2003-08-16 | 15 | 7745 | 2003-06-29 | 15 | 27636 | 2003-06-29 | 15
E522 | 24360 | 19281 | 2174 | 2904 | 65900 | 47795 | 18104 | 3.07 | 18.7 | 0.00901 | 68.11 |  |  | E525 | 9585 | 2003-08-16 | 15 | 19661 | 2003-06-04 | 15 | 7820 | 2003-06-29 | 15 | 27462 | 2003-06-29 | 15
E525 | 21323 | 17443 | 1663 | 2221 | 65155 | 47110 | 18045 | 3.41 | 30.69 | 0.0151 | 57.37 |  |  | E530 | 8089 | 2003-08-16 | 15 | 19626 | 2003-07-08 | 15 | 35.9 | 2003-11-01 | 20 | 19626 | 2003-07-08 | 15
E530 | 17875 | 14172 | 1585 | 2117 | 47002 | 47002 | 0 | 2.98 | 22.86 | 0.00667 | 39.6 |  |  | E540 | 8985 | 2003-08-16 | 15 | 19799 | 2003-08-16 | 15 | 1181 | 2003-03-11 | 10 | 19799 | 2003-08-16 | 15
E540 | 20164 | 15664 | 1926 | 2573 | 47462 | 47460 | 2 | 2.69 | 14.98 | 0.00463 | 43.82 |  |  | E545 | 7471 | 2003-06-04 | 15 | 19497 | 2003-06-04 | 15 | 0 | 2003-01-01 | 1 | 19497 | 2003-06-04 | 15
E545 | 16339 | 13215 | 1337 | 1786 | 46668 | 46668 | 0 | 3.2 | 30.69 | 0.00722 | 29.2
|  |  |  | J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0 | [10 empty] | Compr + Both Fans Wh: A n n u a l H o u r l y I n t e g r a t e d M a x i m a a n d M i n i m a - C O P 2 a n d Z o n e
| Energy Consumption |  | Evaporator Coil Load |  |  | Zone |  |  |  |  | Outdoor |  |  |  | Compr + Both Fans Hour: C O P 2; Latent Date: Indoor Drybulb Temperature; ODB Date: Humidity Ratio |  | Relative Humidity
Hour | Compressor | Cond Fan | Total | Sensible | Latent | Hum. Rat. | COP2 | ODB | EDB | EWB | Hum. Rat. |  |  | Cases | Compr + Both Fans Date: Maximum; Sensible Date: Minimum; Latent Date: Maximum; Sensible + Latent Date: Minimum*; ODB Date: Maximum; Outdoor Humidity Ratio Date: Minimum* |  | Maximum* |  |  | Minimum*
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg) |  |  |  | COP2 | Date | Hour | COP2 | Date | Hour | °C | Date | Hour | °C | Date | Hour | kg/kg | Date | Hour | kg/kg | Date | Hour | % | Date | Hour | % | Date | Hour
1 | 1942.81 | 240.938 | 7667.56 | 5870.06 | 1797.5 | 0.0092502 | 3.5112 | 17.8 | 23.9367 | 17.3042 | 0.011072 |  |  | E300 | 3.88 | 2003-04-30 | 16 | 2.81 | 2003-06-14 | 12 | 26.19 | 2003-11-03 | 15 | 6.99 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 6 | 67.44 | 2003-11-16 | 16 | 14.94 | 2003-11-06 | 8
2 | 1950.53 | 241.104 | 7674.46 | 5871.7 | 1802.77 | 0.0092582 | 3.5017 | 18.3 | 23.9367 | 17.31 | 0.011432 |  |  | E310 | 4.12 | 2003-04-30 | 15 | 2.87 | 2003-12-01 | 14 | 27.19 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0157 | 2003-10-02 | 8 | 0.00196 | 2003-01-05 | 7 | 78.19 | 2003-10-02 | 8 | 15.93 | 2003-11-06 | 8
3 | 1902.33 | 236.85 | 7527.94 | 5782.88 | 1745.07 | 0.0092068 | 3.5191 | 17.8 | 23.8958 | 17.2367 | 0.011072 |  |  | E320 | 4.38 | 2003-12-18 | 3 | 2.83 | 2003-03-31 | 14 | 31.65 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 81.88 | 2003-09-16 | 20 | 12.92 | 2003-12-20 | 5
4 | 1845.43 | 231.118 | 7317.22 | 5683.06 | 1634.17 | 0.0091047 | 3.5238 | 17.8 | 23.8375 | 17.0785 | 0.011072 |  |  | E330 | 4.05 | 2003-06-17 | 16 | 2.84 | 2003-03-31 | 14 | 31.3 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 78.7 | 2003-09-02 | 12 | 14.94 | 2003-11-06 | 8
5 | 1914.46 | 238.687 | 7514.35 | 5955.01 | 1559.34 | 0.0089519 | 3.4899 | 17.2 | 23.9757 | 17.0075 | 0.010155 |  |  | E340 | 3.95 | 2003-09-16 | 16 | 2.84 | 2003-03-31 | 14 | 31.58 | 2003-07-08 | 15 | 6.99 | 2003-01-06 | 5 | 0.0177 | 2003-07-10 | 12 | 0.00197 | 2003-01-05 | 6 | 80.25 | 2003-09-16 | 20 | 14.94 | 2003-11-06 | 8
6 | 2506.57 | 292.588 | 9222.93 | 7311.79 | 1911.15 | 0.0091583 | 3.2949 | 19.4 | 24.5756 | 17.5412 | 0.01097 |  |  | E350 | 3.88 | 2003-04-30 | 16 | 2.81 | 2003-06-14 | 12 | 35 | 2003-04-21 | 2 | 6.99 | 2003-01-06 | 5 | 0.0166 | 2003-10-02 | 1 | 0.00197 | 2003-01-05 | 6 | 72.65 | 2003-08-03 | 7 | 14.94 | 2003-11-06 | 8
7 | 3170.95 | 342.969 | 10769.5 | 8646.87 | 2122.59 | 0.0094778 | 3.0648 | 25 | 25.1643 | 17.9926 | 0.013099 |  |  | E360 | 4.44 | 2003-10-04 | 24 | 2.84 | 2003-03-31 | 14 | 33.13 | 2003-07-10 | 12 | 6.99 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 6 | 67.44 | 2003-11-16 | 16 | 14.94 | 2003-11-06 | 8
8 | 3433.96 | 360.598 | 11186.4 | 9298.63 | 1887.81 | 0.0093737 | 2.948 | 27.2 | 25.4533 | 17.9591 | 0.011039 |  |  | E400 | 4.05 | 2003-06-17 | 16 | 2.81 | 2003-06-14 | 12 | 26.04 | 2003-08-15 | 15 | 6.99 | 2003-01-06 | 5 | 0.0173 | 2003-04-22 | 6 | 0.00197 | 2003-01-05 | 6 | 86.31 | 2003-04-22 | 6 | 14.57 | 2003-11-06 | 5
9 | 4489.15 | 460.788 | 14744.4 | 11923.2 | 2821.19 | 0.0097161 | 2.9787 | 28.9 | 25.5785 | 18.3251 | 0.011957 |  |  | E410 | 3.84 | 2003-05-21 | 15 | 2.81 | 2003-06-14 | 12 | 26.19 | 2003-11-03 | 15 | 6.99 | 2003-01-06 | 5 | 0.0173 | 2003-04-22 | 6 | 0.00197 | 2003-01-05 | 6 | 86.18 | 2003-04-22 | 6 | 14.58 | 2003-11-06 | 5
10 | 4853.28 | 489.455 | 15882.1 | 12287.1 | 3595.03 | 0.010237 | 2.9726 | 28.9 | 25.7393 | 18.8543 | 0.012719 |  |  | E420 | 3.94 | 2003-05-21 | 13 | 2.81 | 2003-06-14 | 12 | 26.23 | 2003-10-20 | 15 | 6.99 | 2003-01-06 | 5 | 0.0147 | 2003-04-02 | 18 | 0.00197 | 2003-01-05 | 6 | 73.85 | 2003-04-02 | 18 | 14.59 | 2003-11-06 | 5
11 | 5164.22 | 508.218 | 16614.5 | 12561.8 | 4052.76 | 0.010622 | 2.929 | 31.1 | 25.8631 | 19.1876 | 0.014761 |  |  | E430 | 3.93 | 2003-04-30 | 13 | 2.81 | 2003-06-14 | 12 | 26.45 | 2003-10-23 | 15 | 6.99 | 2003-01-06 | 5 | 0.0158 | 2003-04-02 | 5 | 0.00197 | 2003-01-05 | 6 | 78.94 | 2003-04-02 | 5 | 14.58 | 2003-11-06 | 5
12 | 5004.96 | 496.504 | 16029.6 | 12561.3 | 3468.23 | 0.010433 | 2.9137 | 30.6 | 25.8628 | 18.8671 | 0.013211 |  |  | E440 | 3.81 | 2003-04-30 | 15 | 2.81 | 2003-04-08 | 13 | 26.26 | 2003-10-23 | 15 | 7 | 2003-01-06 | 5 | 0.0134 | 2003-11-16 | 16 | 0.00197 | 2003-01-05 | 7 | 67.51 | 2003-11-16 | 16 | 14.54 | 2003-11-06 | 5
13 | 6454.59 | 639.274 | 21179.7 | 17430.7 | 3749.01 | 0.0099715 | 2.9856 | 31.1 | 25.9424 | 18.518 | 0.011293 |  |  | E500 | 4.14 | 2003-04-30 | 16 | 2.71 | 2003-07-29 | 12 | 25 | 2003-03-11 | 11 | 24.04 | 2003-04-15 | 5 | 0.0115 | 2003-03-11 | 10 | 0.0103 | 2003-11-02 | 2 | 60.08 | 2003-04-01 | 5 | 52.83 | 2003-10-05 | 1
14 | 6503.4 | 639.953 | 21055.4 | 17608.6 | 3446.79 | 0.0097436 | 2.9476 | 31.7 | 26.022 | 18.4421 | 0.011692 |  |  | E510 | 4.53 | 2003-05-04 | 3 | 2.9 | 2003-03-31 | 14 | 25 | 2003-04-24 | 12 | 24.04 | 2003-04-15 | 5 | 0.0115 | 2003-03-11 | 10 | 0.0105 | 2003-04-02 | 22 | 57.51 | 2003-04-01 | 5 | 53.15 | 2003-05-04 | 4
15 | 8040.55 | 784.905 | 27069.8 | 22350.4 | 4719.45 | 0.0097834 | 3.0672 | 32.2 | 26.1296 | 18.6471 | 0.01234 |  |  | E520 | 3.84 | 2003-04-30 | 16 | 2.47 | 2003-07-30 | 12 | 18.62 | 2003-06-04 | 16 | 13.57 | 2003-11-01 | 7 | 0.0106 | 2003-01-05 | 16 | 0.00657 | 2003-11-01 | 7 | 71.77 | 2003-08-16 | 17 | 61.9 | 2003-07-20 | 15
16 | 8133.59 | 793.61 | 27623.3 | 22292 | 5331.25 | 0.0098255 | 3.0943 | 32.2 | 26.0323 | 18.7965 | 0.014188 |  |  | E522 | 4 | 2003-04-30 | 16 | 2.59 | 2003-07-29 | 12 | 20.93 | 2003-04-21 | 15 | 15.98 | 2003-04-12 | 19 | 0.0107 | 2003-01-01 | 2 | 0.00783 | 2003-04-02 | 21 | 71.32 | 2003-04-05 | 17 | 57.97 | 2003-10-05 | 1
17 | 5211.79 | 509.581 | 16551 | 12739.1 | 3811.95 | 0.010257 | 2.8928 | 31.7 | 25.943 | 19.1104 | 0.014684 |  |  | E525 | 4.4 | 2003-03-16 | 10 | 2.9 | 2003-07-29 | 12 | 35 | 2003-03-11 | 11 | 33.01 | 2003-04-01 | 8 | 0.0173 | 2003-07-20 | 15 | 0.0154 | 2003-11-02 | 2 | 51.12 | 2003-04-01 | 8 | 44.4 | 2003-10-05 | 1
18 | 5122.29 | 506.956 | 16829.6 | 12180.9 | 4648.77 | 0.010859 | 2.9897 | 31.1 | 25.6955 | 19.3936 | 0.015634 |  |  | E530 | 3.88 | 2003-03-16 | 10 | 2.52 | 2003-07-29 | 12 | 25 | 2003-03-11 | 11 | 24.04 | 2003-04-15 | 5 | 0.00677 | 2003-10-26 | 9 | 0.00663 | 2003-04-01 | 5 | 36.01 | 2003-04-20 | 21 | 33.68 | 2003-04-01 | 13
19 | 4831.72 | 492.97 | 16635.3 | 11540.7 | 5094.59 | 0.011024 | 3.1242 | 28.3 | 25.4093 | 19.5323 | 0.014493 |  |  | E540 | 3.69 | 2003-10-17 | 5 | 2.28 | 2003-07-29 | 12 | 15 | 2003-03-11 | 10 | 14.95 | 2003-12-19 | 1 | 0.00634 | 2003-03-11 | 9 | 0.0042 | 2003-10-15 | 5 | 39.96 | 2003-04-18 | 18 | 39.74 | 2003-10-05 | 1
20 | 4874.85 | 501.239 | 17131.1 | 11359.2 | 5771.92 | 0.011357 | 3.1865 | 27.2 | 25.3281 | 19.7431 | 0.016824 |  |  | E545 | 4.17 | 2003-03-16 | 10 | 2.72 | 2003-07-29 | 12 | 35 | 2003-03-11 | 11 | 33.01 | 2003-04-01 | 8 | 0.00763 | 2003-11-05 | 9 | 0.007 | 2003-04-01 | 8 | 24.14 | 2003-12-24 | 1 | 20.14 | 2003-04-01 | 12
21 | 3935.62 | 405.543 | 13524.8 | 8931.39 | 4593.42 | 0.011378 | 3.1155 | 27.2 | 25.291 | 19.7437 | 0.016824 |  |  | * Note: For Cases E500-E545 only, the following results are extracted from the period April 1 - Dec 31 (using a full annual simulation): minimum IDB, minimum zone humidity ratio, maximum and minimum relative humidity.
22 | 3844.33 | 398.939 | 13355.8 | 8747.22 | 4608.6 | 0.011398 | 3.1475 | 26.7 | 25.2092 | 19.7887 | 0.016777
23 | 3807.46 | 397.275 | 13343.3 | 8646.75 | 4696.56 | 0.01145 | 3.1734 | 26.1 | 25.1645 | 19.8355 | 0.016835
24 | 3664.17 | 385.64 | 12972.7 | 8359.6 | 4613.06 | 0.011462 | 3.2033 | 26.1 | 25.0374 | 19.7678 | 0.017273
C a s e E 5 0 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 4073 | 3159 | 391 | 522 | 13673 | 9902 | 3770 | 0.016 | 3.85 | 16.96 | 25
June 25 | 5230 | 4239 | 424 | 566 | 13727 | 9946 | 3780 | 0.011 | 2.94 | 29.5 | 25
C a s e E 5 3 0 A v e r a g e D a i l y O u t p u t s - f(ODB) sensitivity
| Energy Consumption |  |  |  | Evaporator Coil Load |  |  | Zone
Day | Total | Compressor | Cond Fan | Indoor Fan | Total | Sensible | Latent | Hum Rat | COP2 | ODB | EDB
| (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C)
April 30 | 3144 | 2411 | 314 | 419 | 9798 | 9798 | 0 | 0.00674 | 3.59 | 16.96 | 25
June 25 | 4043 | 3248 | 340 | 454 | 9834 | 9834 | 0 | 0.00674 | 2.74 | 29.5 | 25

## Q
e300results.XLS, July, 2004 | [5 empty] | SEE SHEET 'A' FOR INSTRUCTIONS
Space Cooling Electricity Consumption
Energy Consumption, Total (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 35633.7773 | 34750 | 34755 | 35023.7298 | 34976.411 | 35070 | 34750 | 35633.7773 | 2.523% | 0
E310 | 39973.3798 | 39379 | 39384 | 39434.1646 | 39519.569 | 39608 | 39379 | 39973.3798 | 1.503% | 0
E320 | 40059.657 | 38745 | 38792 | 39375.0348 | 39400.815 | 39457 | 38745 | 40059.657 | 3.345% | 0
E330 | 40963.3004 | 39708 | 39438 | 40468.7948 | 40535.137 | 40330 | 39438 | 40963.3004 | 3.79% | 0
E340 | 40619.2951 | 39358 | 39265 | 40071.4206 | 40065.261 | 39947 | 39265 | 40619.2951 | 3.395% | 0
E350 | 32236.9795 | 30547 | 30548 | 31376.2065 | 31586.592 | 31742 | 30547 | 32236.9795 | 5.392% | 0
E360 | 55298.7917 | 54064 | 54016 | 54944.2502 | 54843.258 | 55068 | 54016 | 55298.7917 | 2.345% | 0
E400 | 32045.1536 | 30846 | 30876 | 31265.6433 |  | 31413 | 30846 | 32045.1536 | 3.832% | 0
E410 | 32078.4319 | 31668 | 31699 | 32010.5061 |  | 31503 | 31503 | 32078.4319 | 1.81% | 0
E420 | 33387.0076 | 32530 | 32910 | 32978.5453 |  | 33208 | 32530 | 33387.0076 | 2.597% | 0
E430 | 32538.0313 | 31932 | 31811 | 32085.518 |  | 31818 | 31811 | 32538.0313 | 2.269% | 0
E440 | 33691.321 | 33032 | 32973 | 33284.8265 |  | 33248 | 32973 | 33691.321 | 2.161% | 0
E500 | 22337.887 | 22817 | 22822 | 23075.8197 | 22322.953 | 23138 | 22322.953 | 23138 | 3.582% | 0
E500 May-Sep | 17390.8511 | 17872 | 17870 | 18030.7145 | 17434.537 | 18051 | 17390.8511 | 18051 | 3.714% | 0
E510 May-Sep | 34608.7754 | 35971 | 35970 | 35791.0201 | 34848.637 | 35845 | 34608.7754 | 35971 | 3.837% | 0
E520 | 24986.582 | 25389 | 25390 | 25812.8973 | 25131.07 | 25781 | 24986.582 | 25812.8973 | 3.251% | 0
E522 | 23544.1607 | 24293 | 24307 | 24385.5401 | 23619.744 | 24360 | 23544.1607 | 24385.5401 | 3.493% | 0
E525 | 20320.874 | 20408 | 20421 | 20781.3508 | 20241.713 | 21323 | 20241.713 | 21323 | 5.253% | 0
E530 | 17281.271 | 17540 | 17537 | 17993.9617 | 17442.468 | 17875 | 17281.271 | 17993.9617 | 4.047% | 0
E540 | 19430.3785 | 19878 | 19874 | 20122.7341 | 19536.572 | 20164 | 19430.3785 | 20164 | 3.699% | 0
E545 | 15687.0796 | 15802 | 15791 | 16608.6011 | 15791.081 | 16339 | 15687.0796 | 16608.6011 | 5.758% | 0
Energy Consumption, Compressor (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 22353.5343 | 21569 | 21573 |  | 21770.001 | 21876 | 21569 | 22353.5343 | 3.594% | 0
E310 | 26339.6254 | 25813 | 25817 |  | 25936.821 | 26053 | 25813 | 26339.6254 | 2.026% | 0
E320 | 26433.1374 | 25250 | 25294 |  | 25846.026 | 25912 | 25250 | 26433.1374 | 4.595% | 0
E330 | 27299.7321 | 26172 | 25925 |  | 26927.733 | 26775 | 25925 | 27299.7321 | 5.164% | 0
E340 | 26962.9373 | 25829 | 25745 |  | 26472.79 | 26400 | 25745 | 26962.9373 | 4.634% | 0
E350 | 19316.8404 | 17802 | 17801 |  | 18738.055 | 18891 | 17801 | 19316.8404 | 8.189% | 0
E360 | 40105.8399 | 38999 | 38955 |  | 39697.162 | 39941 | 38955 | 40105.8399 | 2.911% | 0
E400 | 19178.9487 | 18106 | 18131 |  |  | 18629 | 18106 | 19178.9487 | 5.796% | 0
E410 | 19204.4944 | 18823 | 18850 |  |  | 18685 | 18685 | 19204.4944 | 2.75% | 0
E420 | 20358.5854 | 19596 | 19934 |  |  | 20214 | 19596 | 20358.5854 | 3.808% | 0
E430 | 19598.6211 | 19059 | 18951 |  |  | 18966 | 18951 | 19598.6211 | 3.383% | 0
E440 | 20629.1333 | 20042 | 19989 |  |  | 20249 | 19989 | 20629.1333 | 3.165% | 0
E500 | 17854.2956 | 18473 | 18478 |  | 17857.852 | 18522 | 17854.2956 | 18522 | 3.661% | 0
E500 May-Sep | 13942.1479 | 14508 | 14506 |  | 13988.512 | 14491 | 13942.1479 | 14508 | 3.961% | 0
E510 May-Sep | 27747.879 | 28811 | 28810 |  | 27901.957 | 28721 | 27747.879 | 28811 | 3.744% | 0
E520 | 19521.2767 | 20121 | 20126 |  | 19654.972 | 20185 | 19521.2767 | 20185 | 3.332% | 0
E522 | 18620.3108 | 19407 | 19418 |  | 18689.799 | 19281 | 18620.3108 | 19418 | 4.18% | 0
E525 | 16557.8748 | 16880 | 16893 |  | 16506.802 | 17443 | 16506.802 | 17443 | 5.554% | 0
E530 | 13656.9951 | 14127 | 14124 |  | 13855.928 | 14172 | 13656.9951 | 14172 | 3.682% | 0
E540 | 15020.7433 | 15680 | 15677 |  | 15163.82 | 15664 | 15020.7433 | 15680 | 4.269% | 0
E545 | 12621.8685 | 12967 | 12957 |  | 12750.623 | 13215 | 12621.8685 | 13215 | 4.597% | 0
e300results.xls q:a06..m55; 07/19/04
Space Cooling Electricity Consumption
Energy Consumption, Supply Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E310 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E320 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E330 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E340 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E350 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E360 | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 10862.0919 | 10880 | 0.1646% | 0
E400 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 0.1647% | 0
E410 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 0.1647% | 0
E420 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 0.1647% | 0
E430 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 0.1647% | 0
E440 | 10879.92 | 10880 | 10880 | 10862.0919 |  | 10880 | 10862.0919 | 10880 | 0.1647% | 0
E500 | 2563.8216 | 2369 | 2369 | 2630.543 | 2553.232 | 2639 | 2369 | 2639 | 10.71% | 0
E500 May-Sep | 1972.0485 | 1837 | 1837 | 2030.7654 | 1970.497 | 2035 | 1837 | 2035 | 10.17% | 0
E510 May-Sep | 3923.2198 | 4099 | 4099 | 4065.8535 | 3972.28 | 4073 | 3923.2198 | 4099 | 4.352% | 0
E520 | 3125.1884 | 2874 | 2871 | 3140.7019 | 3131.271 | 3200 | 2871 | 3200 | 10.76% | 0
E522 | 2815.5716 | 2704 | 2707 | 2878.8649 | 2819.112 | 2904 | 2704 | 2904 | 7.131% | 0
E525 | 2151.7702 | 1886 | 1885 | 2192.2472 | 2135.708 | 2221 | 1885 | 2221 | 16.16% | 0
E530 | 2072.4451 | 1833 | 1833 | 2121.7134 | 2050.856 | 2117 | 1833 | 2121.7134 | 14.4% | 0
E540 | 2521.5317 | 2258 | 2258 | 2493.7908 | 2500.416 | 2573 | 2258 | 2573 | 12.94% | 0
E545 | 1752.7588 | 1501 | 1501 | 1865.1834 | 1738.667 | 1786 | 1501 | 1865.1834 | 21.54% | 0
Energy Consumption, Condenser Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 2400.3229 | 2301 | 2302 |  | 2326.49 | 2323 | 2301 | 2400.3229 | 4.262% | 0
E310 | 2753.8345 | 2686 | 2687 |  | 2702.828 | 2691 | 2686 | 2753.8345 | 2.509% | 0
E320 | 2746.5996 | 2615 | 2618 |  | 2674.869 | 2681 | 2615 | 2746.5996 | 4.934% | 0
E330 | 2783.6483 | 2656 | 2633 |  | 2727.484 | 2693 | 2633 | 2783.6483 | 5.582% | 0
E340 | 2776.4378 | 2649 | 2640 |  | 2712.551 | 2684 | 2640 | 2776.4378 | 5.068% | 0
E350 | 2040.2191 | 1865 | 1867 |  | 1968.617 | 1970 | 1865 | 2040.2191 | 9.022% | 0
E360 | 4313.0318 | 4185 | 4181 |  | 4266.176 | 4272 | 4181 | 4313.0318 | 3.111% | 0
E400 | 1986.2848 | 1860 | 1865 |  |  | 1902 | 1860 | 1986.2848 | 6.635% | 0
E410 | 1994.0175 | 1965 | 1969 |  |  | 1936 | 1936 | 1994.0175 | 2.951% | 0
E420 | 2148.5022 | 2054 | 2096 |  |  | 2115 | 2054 | 2148.5022 | 4.493% | 0
E430 | 2059.4903 | 1993 | 1980 |  |  | 1970 | 1970 | 2059.4903 | 4.473% | 0
E440 | 2182.2678 | 2110 | 2104 |  |  | 2120 | 2104 | 2182.2678 | 3.676% | 0
E500 | 1919.7698 | 1975 | 1975 |  | 1911.869 | 1976 | 1911.869 | 1976 | 3.286% | 0
E500 May-Sep | 1476.6547 | 1527 | 1527 |  | 1475.528 | 1524 | 1475.528 | 1527 | 3.418% | 0
E510 May-Sep | 2937.6766 | 3061 | 3061 |  | 2974.4 | 3050 | 2937.6766 | 3061 | 4.088% | 0
E520 | 2340.1169 | 2394 | 2393 |  | 2344.827 | 2396 | 2340.1169 | 2396 | 2.354% | 0
E522 | 2108.2783 | 2182 | 2182 |  | 2110.833 | 2174 | 2108.2783 | 2182 | 3.427% | 0
E525 | 1611.2289 | 1642 | 1643 |  | 1599.203 | 1663 | 1599.203 | 1663 | 3.91% | 0
E530 | 1551.8309 | 1580 | 1580 |  | 1535.684 | 1585 | 1535.684 | 1585 | 3.148% | 0
E540 | 1888.1035 | 1940 | 1939 |  | 1872.336 | 1926 | 1872.336 | 1940 | 3.537% | 0
E545 | 1312.4522 | 1334 | 1333 |  | 1301.791 | 1337 | 1301.791 | 1337 | 2.66% | 0
e300results.xls q:a56..m105; 07/19/04
Weather Data Checks, E300 Only
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
Annual Mean Output
ODB | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91 | 19.8889 | 19.9145 | 0.1284% | 0
OHR | 0.011643 | 0.0116 | 0.0116 | 0.011608 | 0.011649 | 0.0116 | 0.0116 | 0.011649 | 0.4189% | 0
Annual Hourly Integrated Maxima
ODB | 34.7 | 35 | 35 | 34.775 | 35 | 35 | 34.7 | 35 | 0.8593% | 0
OHR | 0.021878 | 0.0225 | 0.0225 | 0.021868 | 0.022406 | 0.0223 | 0.021868 | 0.0225 | 2.842% | 0
e300results.xls q:a109..m119; 07/19/04
Space Cooling Coil Loads
Total Sensible + Latent (kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 80426.8675 | 77283.4356 | 77291.9355 | 78329.9975 | 77744.589 | 78257 | 77283.4356 | 80426.8675 | 4.019% | 0
E310 | 99342.1316 | 97394.7852 | 97412.0781 | 97347.6609 | 97295.866 | 97261 | 97261 | 99342.1316 | 2.131% | 0
E320 | 99791.678 | 96356.3319 | 96493.2096 | 97434.8383 | 97141.307 | 96957 | 96356.3319 | 99791.678 | 3.528% | 0
E330 | 105012.8715 | 100729.9701 | 100993.467 | 103810.929 | 103712.915 | 102008 | 100729.9701 | 105012.8715 | 4.17% | 0
E340 | 102727.9789 | 99027.6453 | 99223.143 | 101133.5278 | 100676.21 | 99753 | 99027.6453 | 102727.9789 | 3.685% | 0
E350 | 69387.9976 | 63736.3536 | 63634.6479 | 66594.5472 | 66860.163 | 67389 | 63634.6479 | 69387.9976 | 8.682% | 0
E360 | 162974.0626 | 159807.2061 | 159853.809 | 162207.6865 | 161200.179 | 162168 | 159807.2061 | 162974.0626 | 1.962% | 0
E400 | 68792.8221 | 64917.5466 | 65025.1143 | 66490.4992 |  | 66898 | 64917.5466 | 68792.8221 | 5.834% | 0
E410 | 68672.8538 | 66779.6109 | 66843.5067 | 68071.4219 |  | 66175 | 66175 | 68672.8538 | 3.711% | 0
E420 | 72609.3074 | 69610.9569 | 70882.1316 | 71248.0904 |  | 71803 | 69610.9569 | 72609.3074 | 4.209% | 0
E430 | 69756.312 | 67640.7387 | 67219.2609 | 68287.7544 |  | 67200 | 67200 | 69756.312 | 3.758% | 0
E440 | 73711.3635 | 71380.1085 | 71181.0936 | 72362.1012 |  | 72029 | 71181.0936 | 73711.3635 | 3.508% | 0
E500 | 63357.1063 | 65995.8615 | 65992.3443 | 65589.3563 | 63105.366 | 65614 | 63105.366 | 65995.8615 | 4.451% | 0
E500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50355.6741 | 48439.57 | 50357 | 48439.57 | 50692.8174 | 4.522% | 0
E510 May-Sep | 108974.3099 | 114017.9517 | 114015.3138 | 112794.8773 | 108979.013 | 112781 | 108974.3099 | 114017.9517 | 4.506% | 0
E520 | 63421.5444 | 66571.2168 | 66565.3548 | 66213.2769 | 63212.102 | 66146 | 63212.102 | 66571.2168 | 5.14% | 0
E522 | 63389.2228 | 66373.0812 | 66371.9088 | 65893.8706 | 63157.03 | 65900 | 63157.03 | 66373.0812 | 4.934% | 0
E525 | 63292.9454 | 65399.1099 | 65395.0065 | 65028.3172 | 63001.558 | 65155 | 63001.558 | 65399.1099 | 3.715% | 0
E530 | 45045.848 | 46634.2617 | 46630.7445 | 46988.5521 | 44875.414 | 47002 | 44875.414 | 47002 | 4.603% | 0
E540 | 45112.827 | 47129.8938 | 47126.0835 | 47482.0855 | 44979.842 | 47462 | 44979.842 | 47482.0855 | 5.376% | 0
E545 | 44981.3517 | 46239.7491 | 46235.9388 | 46635.6951 | 44775.11 | 46668 | 44775.11 | 46668 | 4.122% | 0
Sensible Coil Load (kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 56661.7484 | 55796.8608 | 55804.7745 | 55166.0635 | 55209.465 | 55191 | 55166.0635 | 56661.7484 | 2.688% | 0
E310 | 56256.3775 | 56300.9928 | 56312.7168 | 55065.6279 | 55185.072 | 55083 | 55065.6279 | 56312.7168 | 2.239% | 0
E320 | 62859.2053 | 62697.021 | 62746.848 | 61751.6548 | 62008.804 | 62734 | 61751.6548 | 62859.2053 | 1.773% | 0
E330 | 63083.3765 | 63311.0655 | 63327.7722 | 63074.0758 | 62649.459 | 61822 | 61822 | 63327.7722 | 2.395% | 0
E340 | 63032.6061 | 63053.4306 | 63110.5851 | 62391.3804 | 62380.56 | 61406 | 61406 | 63110.5851 | 2.725% | 0
E350 | 50370.8304 | 47684.439 | 47676.5253 | 48335.5891 | 48588.802 | 48768 | 47676.5253 | 50370.8304 | 5.547% | 0
E360 | 134976.8351 | 134919.792 | 134939.7228 | 134711.1169 | 134205.707 | 134697 | 134205.707 | 134976.8351 | 0.5723% | 0
E400 | 41952.3595 | 41419.1334 | 41437.0125 | 40599.2192 |  | 41181 | 40599.2192 | 41952.3595 | 3.275% | 0
E410 | 45676.6456 | 47658.6462 | 47659.8186 | 47103.2086 |  | 45585 | 45585 | 47659.8186 | 4.439% | 0
E420 | 50389.8247 | 49666.0881 | 50612.2149 | 49444.6391 |  | 49984 | 49444.6391 | 50612.2149 | 2.334% | 0
E430 | 47863.3462 | 47731.335 | 47454.0624 | 46911.71 |  | 46143 | 46143 | 47863.3462 | 3.643% | 0
E440 | 50876.0725 | 50592.5772 | 50492.0439 | 50001.0328 |  | 49785 | 49785 | 50876.0725 | 2.167% | 0
E500 | 45043.8 | 47649.8532 | 47646.0429 | 47357.4403 | 44874.225 | 47530 | 44874.225 | 47649.8532 | 5.946% | 0
E500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36365.0866 | 34448.151 | 36480 | 34443.2344 | 36595.5867 | 6.009% | 0
E510 May-Sep | 77489.4321 | 82305.7041 | 82303.0662 | 81315.4422 | 77498.985 | 81563 | 77489.4321 | 82305.7041 | 5.989% | 0
E520 | 45109.6141 | 48101.5203 | 48095.6583 | 47983.7484 | 44976.724 | 48059 | 44976.724 | 48101.5203 | 6.641% | 0
E522 | 45076.0312 | 47962.2978 | 47961.4185 | 47663.109 | 44924.113 | 47795 | 44924.113 | 47962.2978 | 6.478% | 0
E525 | 44979.0103 | 47217.5307 | 47213.4273 | 46796.3098 | 44775.105 | 47110 | 44775.105 | 47217.5307 | 5.27% | 0
E530 | 45045.848 | 46573.59 | 46570.0728 | 46988.3103 | 44874.225 | 47002 | 44874.225 | 47002 | 4.608% | 0
E540 | 45111.8473 | 47022.9123 | 47019.102 | 47473.2183 | 44976.747 | 47460 | 44976.747 | 47473.2183 | 5.368% | 0
E545 | 44981.3517 | 46214.2494 | 46210.4391 | 46635.6951 | 44775.105 | 46668 | 44775.105 | 46668 | 4.123% | 0
Latent Coil Load(kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 23765.119 | 21486.5748 | 21487.161 | 23163.9341 | 22535.143 | 23067 | 21486.5748 | 23765.119 | 10.09% | 0
E310 | 43085.7541 | 41093.7924 | 41099.3613 | 42282.0331 | 42110.836 | 42178 | 41093.7924 | 43085.7541 | 4.746% | 0
E320 | 36932.4726 | 33659.3109 | 33746.3616 | 35683.1835 | 35132.592 | 34224 | 33659.3109 | 36932.4726 | 9.38% | 0
E330 | 41929.495 | 37418.9046 | 37665.6948 | 40736.8532 | 41063.373 | 40186 | 37418.9046 | 41929.495 | 11.32% | 0
E340 | 39695.3729 | 35974.2147 | 36112.5579 | 38742.1474 | 38295.624 | 38346 | 35974.2147 | 39695.3729 | 9.828% | 0
E350 | 19017.1672 | 16051.9146 | 15958.1226 | 18258.9581 | 18271.394 | 18621 | 15958.1226 | 19017.1672 | 17.29% | 0
E360 | 27997.2274 | 24887.4141 | 24914.0862 | 27496.5697 | 26994.482 | 27470 | 24887.4141 | 27997.2274 | 11.68% | 0
E400 | 26840.4626 | 23498.4132 | 23588.1018 | 25891.28 |  | 25717 | 23498.4132 | 26840.4626 | 13.31% | 0
E410 | 22996.2083 | 19120.9647 | 19183.6881 | 20968.2133 |  | 20590 | 19120.9647 | 22996.2083 | 18.84% | 0
E420 | 22219.4827 | 19944.8688 | 20269.9167 | 21803.4513 |  | 21855 | 19944.8688 | 22219.4827 | 10.72% | 0
E430 | 21892.9657 | 19909.4037 | 19765.1985 | 21376.0444 |  | 21057 | 19765.1985 | 21892.9657 | 10.23% | 0
E440 | 22835.291 | 20787.5313 | 20689.0497 | 22361.0683 |  | 22244 | 20689.0497 | 22835.291 | 9.853% | 0
E500 | 18313.3062 | 18346.0083 | 18346.3014 | 18231.916 | 18231.141 | 18084 | 18084 | 18346.3014 | 1.437% | 0
E500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13990.5875 | 13991.418 | 13877 | 13877 | 14097.2307 | 1.572% | 0
E510 May-Sep | 31484.8778 | 31712.2476 | 31712.2476 | 31479.435 | 31479.856 | 31217 | 31217 | 31712.2476 | 1.572% | 0
E520 | 18311.9303 | 18469.6965 | 18469.6965 | 18229.5285 | 18235.133 | 18087 | 18087 | 18469.6965 | 2.091% | 0
E522 | 18313.1916 | 18410.7834 | 18410.4903 | 18230.7617 | 18233.151 | 18104 | 18104 | 18410.7834 | 1.678% | 0
E525 | 18313.9351 | 18181.5792 | 18181.5792 | 18232.0073 | 18226.509 | 18045 | 18045 | 18313.9351 | 1.478% | 0
E530 | 5.6053e-13 | 60.6717 | 60.6717 | 0.24183 | 1.186 | 0 | 0 | 60.6717 | 296.5% | 0
E540 | 0.97976 | 106.9815 | 106.9815 | 8.8672 | 3.09 | 2 | 0.97976 | 106.9815 | 277.9% | 0
E545 | -3.3573e-14 | 25.4997 | 25.4997 | 3.5428e-12 | 0.004 | 0 | -3.3573e-14 | 25.4997 | 300% | 0
e300results.xls q:a125..m198; 07/19/04
Various Annual Means (COP2, IDB)
COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 3.2491 | 3.2377 | 3.2374 | 3.2419 | 3.2264 | 3.23 | 3.2264 | 3.2491 | 0.7006% | 0
E310 | 3.4146 | 3.4175 | 3.4175 | 3.4071 | 3.3972 | 3.38 | 3.38 | 3.4175 | 1.101% | 0
E320 | 3.4199 | 3.458 | 3.4571 | 3.4172 | 3.406 | 3.39 | 3.39 | 3.458 | 1.985% | 0
E330 | 3.4907 | 3.4942 | 3.5364 | 3.5063 | 3.4973 | 3.46 | 3.46 | 3.5364 | 2.185% | 0
E340 | 3.4543 | 3.4773 | 3.4956 | 3.4624 | 3.4495 | 3.42 | 3.42 | 3.4956 | 2.186% | 0
E350 | 3.2489 | 3.2408 | 3.2354 | 3.2463 | 3.2289 | 3.23 | 3.2289 | 3.2489 | 0.6185% | 0
E360 | 3.669 | 3.7006 | 3.7058 | 3.6797 | 3.6667 | 3.66 | 3.66 | 3.7058 | 1.245% | 0
E400 | 3.2503 | 3.2514 | 3.2519 | 3.2588 |  | 3.26 | 3.2503 | 3.26 | 0.2988% | 0
E410 | 3.2395 | 3.2124 | 3.2107 | 3.2187 |  | 3.21 | 3.21 | 3.2395 | 0.917% | 0
E420 | 3.2261 | 3.2153 | 3.2175 | 3.2215 |  | 3.21 | 3.21 | 3.2261 | 0.4992% | 0
E430 | 3.2208 | 3.213 | 3.2115 | 3.2176 |  | 3.21 | 3.21 | 3.2208 | 0.3358% | 0
E440 | 3.2313 | 3.2223 | 3.2219 | 3.2272 |  | 3.22 | 3.22 | 3.2313 | 0.3516% | 0
E500 | 3.2041 | 3.2275 | 3.2265 | 3.208 | 3.192 | 3.2 | 3.192 | 3.2275 | 1.105% | 0
E500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1472 | 3.1324 | 3.14 | 3.1324 | 3.1616 | 0.9288% | 0
E510 May-Sep | 3.5513 | 3.5774 | 3.5774 | 3.5554 | 3.5295 | 3.55 | 3.5295 | 3.5774 | 1.346% | 0
E520 | 2.9011 | 2.9567 | 2.956 | 2.9205 | 2.8733 | 2.92 | 2.8733 | 2.9567 | 2.857% | 0
E522 | 3.0581 | 3.0744 | 3.0728 | 3.0639 | 3.0363 | 3.07 | 3.0363 | 3.0744 | 1.244% | 0
E525 | 3.4835 | 3.5309 | 3.528 | 3.4982 | 3.4796 | 3.41 | 3.41 | 3.5309 | 3.465% | 0
E530 | 2.9618 | 2.969 | 2.9694 | 2.9604 | 2.9156 | 2.98 | 2.9156 | 2.98 | 2.177% | 0
E540 | 2.668 | 2.6748 | 2.6752 | 2.6934 | 2.6403 | 2.69 | 2.6403 | 2.6934 | 1.988% | 0
E545 | 3.2281 | 3.2333 | 3.2355 | 3.1632 | 3.1863 | 3.2 | 3.1632 | 3.2355 | 2.257% | 0
IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 23.6243 | 24.0556 | 24.0556 | 24.0891 | 24.0816 | 23.99 | 23.6243 | 24.0891 | 1.938% | 0
E310 | 23.7556 | 24.1111 | 24.0556 | 24.0915 | 24.0897 | 24.01 | 23.7556 | 24.1111 | 1.48% | 0
E320 | 23.9005 | 24.3889 | 24.3889 | 24.2322 | 24.3274 | 24.53 | 23.9005 | 24.53 | 2.591% | 0
E330 | 23.8797 | 24.2778 | 24.2778 | 24.2953 | 24.2955 | 24.18 | 23.8797 | 24.2955 | 1.718% | 0
E340 | 23.8756 | 24.2778 | 24.2778 | 24.3105 | 24.3089 | 24.21 | 23.8756 | 24.3105 | 1.796% | 0
E350 | 25.6595 | 26.1667 | 26.1667 | 26.2368 | 26.2686 | 26.15 | 25.6595 | 26.2686 | 2.333% | 0
E360 | 25.3649 | 25.6111 | 25.5556 | 25.4311 | 25.4809 | 25.37 | 25.3649 | 25.6111 | 0.9665% | 0
E400 | 24.1263 | 24.0556 | 24.0556 | 24.0905 |  | 23.99 | 23.99 | 24.1263 | 0.5664% | 0
E410 | 24.1221 | 24.0556 | 24.0556 | 24.089 |  | 23.99 | 23.99 | 24.1221 | 0.5492% | 0
E420 | 23.9262 | 24.0556 | 24.0556 | 24.089 |  | 23.99 | 23.9262 | 24.089 | 0.6779% | 0
E430 | 23.9916 | 24.0556 | 24.0556 | 24.089 |  | 23.99 | 23.99 | 24.089 | 0.412% | 0
E440 | 23.9118 | 24.0556 | 24.0556 | 24.0891 |  | 23.99 | 23.9118 | 24.0891 | 0.7381% | 0
E500 | 20.2342 | 20.6667 | 20.5556 | 20.4037 | 21.0978 | 22.86 | 20.2342 | 22.86 | 12.52% | 0
E500 May-Sep | 24.5723 | 25 | 25 | 24.9827 | 25 | 25 | 24.5723 | 25 | 1.716% | 0
E510 May-Sep | 25.8168 | 25.1111 | 25.1111 | 24.9597 | 25 | 25 | 24.9597 | 25.8168 | 3.406% | 0
E520 | 13.5171 | 13.7778 | 13.7222 | 13.6259 | 14.1421 | 14.89 | 13.5171 | 14.89 | 9.844% | 0
E522 | 16.9456 | 17.2778 | 17.2222 | 17.0327 | 17.729 | 18.7 | 16.9456 | 18.7 | 10.03% | 0
E525 | 26.8443 | 27.3889 | 27.2778 | 27.1287 | 27.7709 | 30.69 | 26.8443 | 30.69 | 13.81% | 0
E530 | 20.0253 | 20.6111 | 20.5556 | 20.5951 | 21.0978 | 22.86 | 20.0253 | 22.86 | 13.53% | 0
E540 | 13.2893 | 13.7778 | 13.7222 | 13.8017 | 14.1406 | 14.98 | 13.2893 | 14.98 | 12.12% | 0
E545 | 26.6052 | 27.3333 | 27.2778 | 27.3219 | 27.7166 | 30.69 | 26.6052 | 30.69 | 14.68% | 0
e300results.xls q:a205..m254; 07/19/04
Various Annual Means (Humidity Ratio, Zone Relative Humidity)
Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 0.0090691 | 0.0092 | 0.0092 | 0.0091654 | 0.0091748 | 0.0092 | 0.0090691 | 0.0092 | 1.428% | 0
E310 | 0.011071 | 0.0113 | 0.0113 | 0.011154 | 0.011175 | 0.0111 | 0.011071 | 0.0113 | 2.049% | 0
E320 | 0.009988 | 0.0101 | 0.0101 | 0.010037 | 0.010049 | 0.0099 | 0.0099 | 0.0101 | 1.994% | 0
E330 | 0.0097409 | 0.0099 | 0.0099 | 0.0098806 | 0.0098116 | 0.0099 | 0.0097409 | 0.0099 | 1.614% | 0
E340 | 0.0097914 | 0.0099 | 0.0099 | 0.0099021 | 0.0098683 | 0.0099 | 0.0097914 | 0.0099021 | 1.121% | 0
E350 | 0.0097059 | 0.01 | 0.01 | 0.0097964 | 0.0097585 | 0.00977 | 0.0097059 | 0.01 | 2.989% | 0
E360 | 0.0084995 | 0.0087 | 0.0087 | 0.0086063 | 0.0085524 | 0.00858 | 0.0084995 | 0.0087 | 2.33% | 0
E400 | 0.0098011 | 0.01 | 0.01 | 0.010042 |  | 0.01 | 0.0098011 | 0.010042 | 2.415% | 0
E410 | 0.0097405 | 0.0095 | 0.0095 | 0.0094823 |  | 0.0095 | 0.0094823 | 0.0097405 | 2.705% | 0
E420 | 0.0092639 | 0.0094 | 0.0094 | 0.0093476 |  | 0.0093 | 0.0092639 | 0.0094 | 1.457% | 0
E430 | 0.0093103 | 0.0094 | 0.0094 | 0.009387 |  | 0.0094 | 0.0093103 | 0.0094 | 0.9566% | 0
E440 | 0.0091578 | 0.0093 | 0.0093 | 0.0092307 |  | 0.0092 | 0.0091578 | 0.0093 | 1.539% | 0
E500 | 0.0097753 |  |  | 0.0091456 | 0.010218 | 0.0107 | 0.0091456 | 0.0107 | 15.61% | 0
E500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.010999 | 0.011329 | 0.0109 | 0.0109 | 0.0114 | 4.474% | 0
E510 May-Sep | 0.011395 | 0.0114 | 0.0114 | 0.011008 | 0.011328 | 0.0109 | 0.0109 | 0.0114 | 4.449% | 0
E520 | 0.0066924 |  |  | 0.0060157 | 0.0070234 | 0.00763 | 0.0060157 | 0.00763 | 23.6% | 0
E522 | 0.0081904 |  |  | 0.0074805 | 0.0085797 | 0.00901 | 0.0074805 | 0.00901 | 18.39% | 0
E525 | 0.013713 |  |  | 0.01338 | 0.01398 | 0.0151 | 0.01338 | 0.0151 | 12.25% | 0
E530 | 0.0062265 |  |  | 0.0064848 | 0.0057975 | 0.00667 | 0.0057975 | 0.00667 | 13.86% | 0
E540 | 0.0044601 |  |  | 0.0043402 | 0.0038546 | 0.00463 | 0.0038546 | 0.00463 | 17.94% | 0
E545 | 0.0062265 |  |  | 0.0067479 | 0.006749 | 0.00722 | 0.0062265 | 0.00722 | 14.75% | 0
Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
E300 | 48.6149 | 48.26 | 48.28 | 47.9447 | 47.8261 | 47.93 | 47.8261 | 48.6149 | 1.638% | 0
E310 | 58.3307 | 58.51 | 58.53 | 57.961 | 57.841 | 57.8 | 57.8 | 58.53 | 1.255% | 0
E320 | 52.0053 | 51.21 | 51.25 | 51.4531 | 51.1034 | 49.94 | 49.94 | 52.0053 | 4.037% | 0
E330 | 50.8445 | 50.58 | 50.65 | 50.6065 | 50.0848 | 50.7 | 50.0848 | 50.8445 | 1.502% | 0
E340 | 51.085 | 50.69 | 50.73 | 50.6474 | 50.2967 | 50.78 | 50.2967 | 51.085 | 1.555% | 0
E350 | 45.484 | 45.45 | 45.55 | 44.5942 | 44.3162 | 44.56 | 44.3162 | 45.55 | 2.742% | 0
E360 | 41.0335 | 41.49 | 41.49 | 41.3637 | 40.871 | 41.21 | 40.871 | 41.49 | 1.501% | 0
E400 | 50.7709 | 52.21 | 52.25 | 52.2746 |  | 52.01 | 50.7709 | 52.2746 | 2.897% | 0
E410 | 50.4971 | 49.65 | 49.63 | 49.5161 |  | 49.75 | 49.5161 | 50.4971 | 1.969% | 0
E420 | 48.7794 | 49.14 | 48.97 | 48.8495 |  | 48.76 | 48.76 | 49.14 | 0.7771% | 0
E430 | 48.8219 | 49.17 | 49.3 | 49.0444 |  | 49.17 | 48.8219 | 49.3 | 0.9736% | 0
E440 | 48.3298 | 48.46 | 48.57 | 48.2689 |  | 48.23 | 48.23 | 48.57 | 0.7029% | 0
E500 | 66.5261 |  |  | 57.9362 | 65.9419 | 63.73 | 57.9362 | 66.5261 | 13.52% | 0
E500 May-Sep | 57.0476 | 57.47 | 57.47 | 55.6602 | 57.0722 | 55.13 | 55.13 | 57.47 | 4.131% | 0
E510 May-Sep | 54.7001 | 57.36 | 57.36 | 55.778 | 57.0615 | 55.24 | 54.7001 | 57.36 | 4.729% | 0
E520 | 69.8745 |  |  | 60.9282 | 70.2268 | 72.17 | 60.9282 | 72.17 | 16.46% | 0
E522 | 68.6774 |  |  | 59.7074 | 68.2314 | 68.11 | 59.7074 | 68.6774 | 13.55% | 0
E525 | 61.4674 |  |  | 53.7167 | 60.1387 | 57.37 | 53.7167 | 61.4674 | 13.32% | 0
E530 | 46.7299 |  |  | 47.5315 | 41.4516 | 39.6 | 39.6 | 47.5315 | 18.1% | 0
E540 | 48.521 |  |  | 46.1769 | 40.0509 | 43.82 | 40.0509 | 48.521 | 18.97% | 0
E545 | 36.6249 |  |  | 38.63 | 36.8747 | 29.2 | 29.2 | 38.63 | 26.69% | 0
e300results.xls q:a255..m304; 07/19/04
f(ODB) Sensitivity E500 and E530, April 30 and June 25
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
Energy Consumption, Compr. + Both Fans (Wh,e)
E500Apr30 | 3892.9389 | 3975.4583 | 3975.1667 | 4019.3858 | 3901.0417 | 4073 | 3892.9389 | 4073 | 4.532% | 0
E500Jun25 | 5044.9219 | 5204.3333 | 5204.0833 | 5244.3836 | 5066.5 | 5230 | 5044.9219 | 5244.3836 | 3.861% | 0
Del E500 | 1151.9831 | 1228.875 | 1228.9167 | 1224.9978 | 1165.4583 | 1157 | 1151.9831 | 1228.9167 | 6.449% | 0
E530Apr30 | 3022.7732 | 3062 | 3061.7917 | 3131.8977 | 3091.5417 | 3144 | 3022.7732 | 3144 | 3.929% | 0
E530Jun25 | 3894.1233 | 3978.2083 | 3978.0833 | 4090.8917 | 3934.625 | 4043 | 3894.1233 | 4090.8917 | 4.936% | 0
Del E530 | 871.3501 | 916.2083 | 916.2917 | 958.994 | 843.0833 | 899 | 843.0833 | 958.994 | 12.87% | 0
Energy Consumption, Compressor (Wh,e)
E500Apr30 | 3014.619 | 3119.8333 | 3119.6667 |  | 3020.0417 | 3159 | 3014.619 | 3159 | 4.678% | 0
E500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 |  | 4105.9583 | 4239 | 4083.8829 | 4263.5417 | 4.287% | 0
Del E500 | 1069.2639 | 1143.7083 | 1143.75 |  | 1085.9167 | 1080 | 1069.2639 | 1143.75 | 6.744% | 0
E530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 |  | 2378.4583 | 2411 | 2311.4724 | 2411 | 4.189% | 0
E530Jun25 | 3118.0954 | 3243 | 3242.9583 |  | 3165.5833 | 3248 | 3118.0954 | 3248 | 4.055% | 0
Del E530 | 806.623 | 852.9583 | 853.0417 |  | 787.125 | 837 | 787.125 | 853.0417 | 7.967% | 0
Energy Consumption, Condenser Fan (Wh,e)
E500Apr30 | 376.0762 | 389.125 | 389.0833 |  | 377.25 | 391 | 376.0762 | 391 | 3.881% | 0
E500Jun25 | 411.4946 | 426.3333 | 426.3333 |  | 411.3333 | 424 | 411.3333 | 426.3333 | 3.572% | 0
Del E500 | 35.4184 | 37.2083 | 37.25 |  | 34.0833 | 33 | 33 | 37.25 | 12.01% | 0
E530Apr30 | 304.5625 | 311.1667 | 311.125 |  | 305.3333 | 314 | 304.5625 | 314 | 3.052% | 0
E530Jun25 | 332.2771 | 339.625 | 339.625 |  | 329.25 | 340 | 329.25 | 340 | 3.198% | 0
Del E530 | 27.7146 | 28.4583 | 28.5 |  | 23.9167 | 26 | 23.9167 | 28.5 | 17.03% | 0
Energy Consumption, Supply Fan (Wh,e)
E500Apr30 | 502.2437 | 466.5 | 466.4167 | 517.8884 | 503.75 | 522 | 466.4167 | 522 | 11.2% | 0
E500Jun25 | 549.5444 | 514.4583 | 514.3333 | 566.5961 | 549.2083 | 566 | 514.3333 | 566.5961 | 9.618% | 0
Del E500 | 47.3007 | 47.9583 | 47.9167 | 48.7076 | 45.4583 | 44 | 44 | 48.7076 | 10.04% | 0
E530Apr30 | 406.7383 | 360.7917 | 360.75 | 415.8771 | 407.75 | 419 | 360.75 | 419 | 14.74% | 0
E530Jun25 | 443.7507 | 395.5833 | 395.5 | 458.1925 | 439.7917 | 454 | 395.5 | 458.1925 | 14.54% | 0
Del E530 | 37.0125 | 34.7917 | 34.75 | 42.3155 | 32.0417 | 35 | 32.0417 | 42.3155 | 28.55% | 0
Sensible + Latent Coil Load (Wh,th)
E500Apr30 | 13185.6871 | 13732.6998 | 13732.9074 | 13653.7633 | 13169.5417 | 13673 | 13169.5417 | 13732.9074 | 4.165% | 0
E500Jun25 | 13188.0504 | 13837.5319 | 13837.3853 | 13734.0071 | 13198.0833 | 13727 | 13188.0504 | 13837.5319 | 4.78% | 0
Del E500 | 2.3633 | 104.8321 | 104.4779 | 80.2437 | 28.5417 | 54 | 2.3633 | 104.8321 | 164.2% | 0
E530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 9353.1633 | 9798 | 4.623% | 0
E530Jun25 | 9376.2963 | 9760.7918 | 9760.6941 | 9843.2403 | 9387.625 | 9834 | 9376.2963 | 9843.2403 | 4.834% | 0
Del E530 | 23.1329 | 39.6418 | 39.2998 | 64.4987 | 22.1667 | 36 | 22.1667 | 64.4987 | 113% | 0
Sensible Coil Load (Wh,th)
E500Apr30 | 9374.7971 | 9924.8179 | 9925.0255 | 9849.8339 | 9365.4583 | 9902 | 9365.4583 | 9925.0255 | 5.755% | 0
E500Jun25 | 9377.6867 | 9981.2396 | 9981.0931 | 9923.758 | 9387.625 | 9946 | 9377.6867 | 9981.2396 | 6.18% | 0
Del E500 | 2.8896 | 56.4217 | 56.0676 | 73.9242 | 22.1667 | 44 | 2.8896 | 73.9242 | 166.8% | 0
E530Apr30 | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 9353.1633 | 9798 | 4.623% | 0
E530Jun25 | 9376.2963 | 9760.7674 | 9760.6697 | 9843.2403 | 9387.625 | 9834 | 9376.2963 | 9843.2403 | 4.834% | 0
Del E530 | 23.1329 | 39.6174 | 39.2754 | 64.4987 | 22.1667 | 36 | 22.1667 | 64.4987 | 113% | 0
Latent Coil Load (Wh,th)
E500Apr30 | 3810.89 | 3807.8819 | 3807.8819 | 3803.9295 | 3804.375 | 3770 | 3770 | 3810.89 | 1.076% | 0
E500Jun25 | 3810.3637 | 3856.2923 | 3856.2923 | 3810.249 | 3810.4167 | 3780 | 3780 | 3856.2923 | 1.997% | 0
Del E500 | -0.52625 | 48.4104 | 48.4104 | 6.3196 | 6.0417 | 10 | -0.52625 | 48.4104 | 247.5% | 0
E530Apr30 | -5.4771e-13 | 0 | 0 | 3.0182e-13 | 0 | 0 | -5.4771e-13 | 3.0182e-13 | -2073% | 0
E530Jun25 | 7.2905e-13 | 0.024425 | 0.024425 | 3.5571e-13 | 0 | 0 | 0 | 0.024425 | 300% | 0
Del E530 | 1.2768e-12 | 0.024425 | 0.024425 | 5.3896e-14 | 0 | 0 | 0 | 0.024425 | 300% | 0
e300results.xls q:a316..m69; 07/19/04
f(ODB) Sensitivity E500 and E530, April 30 and June 25
Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min) | Your
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean | Software
Humidity Ratio (kg/kg)
E500Apr30 | 0.010675 | 0.011 | 0.011 | 0.010646 | 0.010938 | 0.016 | 0.010646 | 0.016 | 45.72% | 0
E500Jun25 | 0.011168 | 0.0115 | 0.0115 | 0.011144 | 0.011479 | 0.011 | 0.011 | 0.0115 | 4.425% | 0
Del E500 | 0.00049288 | 0.0005 | 0.0005 | 0.0004979 | 0.00054117 | -0.005 | -0.005 | 0.00054117 | -1347% | 0
E530Apr30 | 0.006208 | 0.0071 | 0.0071 | 0.006466 | 0.005485 | 0.00674 | 0.005485 | 0.0071 | 24.78% | 0
E530Jun25 | 0.006208 | 0.0078 | 0.0078 | 0.006466 | 0.005478 | 0.00674 | 0.005478 | 0.0078 | 34.41% | 0
Del E530 | 0 | 0.0007 | 0.0007 | 8.0838e-16 | -7e-06 | 0 | -7e-06 | 0.0007 | 304.5% | 0
COP2
E500Apr30 | 3.8448 | 3.9136 | 3.9139 | 3.8588 | 3.8372 | 3.85 | 3.8372 | 3.9139 | 1.983% | 0
E500Jun25 | 2.9313 | 2.9505 | 2.9506 | 2.9346 | 2.9213 | 2.94 | 2.9213 | 2.9506 | 0.9971% | 0
Del E500 | -0.9135 | -0.9631 | -0.96334 | -0.92417 | -0.91589 | -0.91 | -0.96334 | -0.91 | -5.726% | 0
E530Apr30 | 3.5431 | 3.5988 | 3.5991 | 3.4048 | 3.4604 | 3.59 | 3.4048 | 3.5991 | 5.501% | 0
E530Jun25 | 2.7197 | 2.7245 | 2.7245 | 2.7405 | 2.69 | 2.74 | 2.69 | 2.7405 | 1.852% | 0
Del E530 | -0.82341 | -0.87433 | -0.87464 | -0.66433 | -0.7704 | -0.85 | -0.87464 | -0.66433 | -25.98% | 0
ODB (°C)
E500Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 16.7917 | 16.96 | 0.9989% | 0
E500Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 29.5 | 29.5167 | 0.05648% | 0
Del E500 | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 12.54 | 12.725 | 1.462% | 0
E530Apr30 | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 16.7917 | 16.96 | 0.9989% | 0
E530Jun25 | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 29.5 | 29.5167 | 0.05648% | 0
Del E530 | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 12.54 | 12.725 | 1.462% | 0
EDB (°C)
E500Apr30 | 24.6411 | 24.9444 | 24.9444 | 24.982 | 25 | 25 | 24.6411 | 25 | 1.44% | 0
E500Jun25 | 24.5478 | 25 | 25 | 24.9831 | 25 | 25 | 24.5478 | 25 | 1.815% | 0
Del E500 | -0.093296 | 0.055556 | 0.055556 | 0.001091 | 0 | 0 | -0.093296 | 0.055556 | 4724% | 0
E530Apr30 | 24.365 | 24.9444 | 24.6667 | 25.0003 | 25 | 25 | 24.365 | 25.0003 | 2.558% | 0
E530Jun25 | 24.3537 | 24.9444 | 24.9444 | 25.0003 | 25 | 25 | 24.3537 | 25.0003 | 2.6% | 0
Del E530 | -0.011358 | 0 | 0.27778 | 3.6047e-05 | 0 | 0 | -0.011358 | 0.27778 | 651.1% | 0
e300results.xls q:a370..m402; 07/19/04

## R
e300results.XLS, Jul, 2004
Hourly Integrated Maxima (Total Cooling System Energy Consumption and Total Coil Load)
Energy Consumption, Compressor + Both Fans (Wh,e) | [18 empty] | Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7089 | 07/20 | 15:00 | 11932 | 1900-07-20 | 15 | 11548 | 2003-07-20 | 15 | 11548 | 11995.7089 | 3.823% | #REF! | 0 | 0 | 0
E310 | 12594.4016 | 20-Jul | 15 | 12583 | 2002-07-20 | 15 | 12595 | 2002-07-20 | 15 | 12572.0793 | 07/20 | 15:00 | 12653 | 1900-07-20 | 15 | 12162 | 2003-08-16 | 16 | 12162 | 12653 | 3.92% |  | 0 | 0 | 0
E320 | 13028.1986 | 20-Jul | 15 | 12916 | 2002-07-20 | 15 | 12981 | 2002-07-20 | 15 | 12988.8392 | 07/20 | 15:00 | 13104 | 1900-07-20 | 15 | 12875 | 2003-07-20 | 14 | 12875 | 13104 | 1.764% |  | 0 | 0 | 0
E330 | 13346.701 | 20-Jul | 15 | 13212 | 2002-07-20 | 15 | 13407 | 2002-07-20 | 15 | 13356.2349 | 07/20 | 15:00 | 13467 | 1900-07-20 | 15 | 13335 | 2003-07-20 | 15 | 13212 | 13467 | 1.91% |  | 0 | 0 | 0
E340 | 13180.9018 | 20-Jul | 15 | 13158 | 2002-07-20 | 15 | 13190 | 2002-07-20 | 15 | 13174.9258 | 07/20 | 15:00 | 13277 | 1900-07-20 | 15 | 13101 | 2003-07-20 | 14 | 13101 | 13277 | 1.335% |  | 0 | 0 | 0
E350 | 11626.889 | 20-Jul | 15 | 11654 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7017 | 07/20 | 15:00 | 11932 | 1900-07-20 | 15 | 11546 | 2003-07-20 | 15 | 11546 | 11995.7017 | 3.835% |  | 0 | 0 | 0
E360 | 12769.5022 | 20-Jul | 15 | 12736 | 2002-07-20 | 15 | 12726 | 2002-07-20 | 15 | 12776.4285 | 07/20 | 15:00 | 12863 | 1900-07-20 | 15 | 12762 | 2003-07-20 | 14 | 12726 | 12863 | 1.073% |  | 0 | 0 | 0
E400 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11677 | 2004-09-18 | 15 | 11995.6974 | 07/20 | 15:00 |  |  |  | 11519 | 2003-07-20 | 15 | 11519 | 11995.6974 | 4.082% |  | 0 | 0 | 0
E410 | 11627.8677 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7089 | [5 empty] | 11549 | 2003-07-20 | 15 | 11549 | 11995.7089 | 3.829% |  | 0 | 0 | 0
E420 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7089 | 07/20 | 15:00 |  |  |  | 11548 | 2003-07-20 | 15 | 11548 | 11995.7089 | 3.837% |  | 0 | 0 | 0
E430 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7089 | 07/20 | 15:00 |  |  |  | 11548 | 2003-07-20 | 15 | 11548 | 11995.7089 | 3.837% |  | 0 | 0 | 0
E440 | 11626.0371 | 20-Jul | 15 | 11564 | 2002-07-20 | 15 | 11602 | 2002-07-20 | 15 | 11995.7089 | 07/20 | 15:00 |  |  |  | 11461 | 2003-08-16 | 16 | 11461 | 11995.7089 | 4.59% |  | 0 | 0 | 0
E500 | 10166.4831 | 20-Jul | 15 | 10431 | 2002-07-20 | 15 | 10425 | 2002-07-20 | 15 | 10438.5175 | 07/20 | 15:00 | 10177 | 1900-07-20 | 15 | 10274 | 2003-06-04 | 15 | 10166.4831 | 10438.5175 | 2.636% |  | 0 | 0 | 0
E510 | 11204.8968 | 20-Jul | 15 | 11590 | 2002-07-20 | 15 | 11587 | 2002-07-20 | 15 | 11450.7514 | 07/20 | 15:00 | 11186 | 1900-07-20 | 15 | 11344 | 2003-07-20 | 14 | 11186 | 11590 | 3.546% |  | 0 | 0 | 0
E520 | 11035.3898 | 20-Jul | 15 | 10989 | 2002-07-20 | 15 | 11014 | 2002-07-20 | 15 | 11261.8296 | 07/20 | 15:00 | 11044 | 1900-07-20 | 15 | 10684 | 2003-06-04 | 15 | 10684 | 11261.8296 | 5.251% |  | 0 | 0 | 0
E522 | 10430.7791 | 20-Jul | 15 | 10972 | 2002-07-20 | 15 | 10966 | 2002-07-20 | 15 | 10902.675 | 07/20 | 15:00 | 10639 | 1900-07-20 | 15 | 10747 | 2003-08-16 | 15 | 10430.7791 | 10972 | 5.022% |  | 0 | 0 | 0
E525 | 9366.7481 | 20-Jul | 15 | 9538 | 2002-07-20 | 15 | 9531 | 2002-07-20 | 15 | 9588.2506 | 07/20 | 15:00 | 9419 | 1900-07-20 | 15 | 9585 | 2003-08-16 | 15 | 9366.7481 | 9588.2506 | 2.33% |  | 0 | 0 | 0
E530 | 8028.3285 | 20-Jul | 15 | 8059 | 2002-07-20 | 15 | 8055 | 2002-07-20 | 15 | 8293.041 | 07/20 | 15:00 | 7992 | 1900-07-20 | 15 | 8089 | 2003-08-16 | 15 | 7992 | 8293.041 | 3.723% |  | 0 | 0 | 0
E540 | 8698.9562 | 20-Jul | 15 | 8943 | 2002-07-20 | 15 | 8939 | 2002-07-20 | 15 | 9076.4428 | 07/20 | 15:00 | 8846 | 1900-07-20 | 15 | 8985 | 2003-08-16 | 15 | 8698.9562 | 9076.4428 | 4.234% |  | 0 | 0 | 0
E545 | 7204.827 | 20-Jul | 15 | 7350 | 2002-07-20 | 15 | 7346 | 2002-07-20 | 15 | 7767.989 | 07/20 | 15:00 | 7351 | 1900-07-20 | 15 | 7471 | 2003-06-04 | 15 | 7204.827 | 7767.989 | 7.595% |  | 0 | 0 | 0
Senstible + Latent Coil Load (Wh,th) | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 | 32502 | 1900-07-20 | 15 | 32072 | 2003-07-20 | 15 | 31401 | 33057.4738 | 5.159% |  | 0 | 0 | 0
E310 | 37328 | 03-Sep | 15 | 36750 | 2004-09-03 | 16 | 37033 | 2004-09-03 | 16 | 37372.5209 | 09/17 | 15:00 | 37261 | 1900-09-03 | 15 | 36991 | 2003-09-03 | 16 | 36750 | 37372.5209 | 1.677% |  | 0 | 0 | 0
E320 | 40317.6 | 03-Sep | 16 | 53813 | 2002-10-02 | 9 | 53823 | 2002-10-02 | 9 | 40097.0154 | 10/02 | 10:00 | 39904 | 1900-09-03 | 16 | 39920 | 2003-09-03 | 16 | 39904 | 53823 | 31.18% |  | 0 | 0 | 0
E330 | 43492 | 02-Oct | 9 | 43628 | 2002-10-02 | 9 | 64572 | 2002-10-02 | 9 | 43597.9449 | 10/02 | 09:00 | 43978 | 1900-10-02 | 9 | 42415 | 2003-07-10 | 11 | 42415 | 64572 | 47.2% |  | 0 | 0 | 0
E340 | 41651.7 | 02-Oct | 10 | 50819 | 2002-10-02 | 9 | 59549 | 2002-10-02 | 9 | 41608.4737 | 10/02 | 10:00 | 41366 | 1900-09-03 | 15 | 41132 | 2003-09-03 | 16 | 41132 | 59549 | 40.02% |  | 0 | 0 | 0
E350 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31454 | 2001-07-20 | 15 | 33057.4487 | 07/20 | 15:00 | 32502 | 1900-07-20 | 15 | 32077 | 2003-07-20 | 15 | 31401 | 33057.4487 | 5.161% |  | 0 | 0 | 0
E360 | 38857.16 | 02-Oct | 10 | 40613 | 2002-10-02 | 9 | 41019 | 2002-10-02 | 9 | 38691.4863 | 10/02 | 11:00 | 38322 | 1900-10-02 | 10 | 38451 | 2003-10-02 | 10 | 38322 | 41019 | 6.858% |  | 0 | 0 | 0
E400 | 41178.6 | 16-Sep | 15 | 40543 | 2002-09-18 | 14 | 49838 | 2003-09-18 | 15 | 41112.206 | 09/16 | 15:00 |  |  |  | 40774 | 2003-09-16 | 14 | 40543 | 49838 | 21.77% |  | 0 | 0 | 0
E410 | 32091.73 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | [6 empty] | 32073 | 2003-07-20 | 15 | 31401 | 32091.73 | 2.175% |  | 0 | 0 | 0
E420 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 |  |  |  | 32072 | 2003-07-20 | 15 | 31401 | 33057.4738 | 5.171% |  | 0 | 0 | 0
E430 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2001-07-20 | 15 | 33057.4738 | 07/20 | 15:00 |  |  |  | 32072 | 2003-07-20 | 15 | 31401 | 33057.4738 | 5.171% |  | 0 | 0 | 0
E440 | 32174.05 | 08-Jul | 15 | 31401 | 2001-07-20 | 15 | 31455 | 2003-07-20 | 15 | 33057.4738 | 07/20 | 15:00 |  |  |  | 31777 | 2003-07-08 | 16 | 31401 | 33057.4738 | 5.181% |  | 0 | 0 | 0
E500 | 27485.51 | 28-Oct | 15 | 27707 | 2001-08-16 | 16 | 27706 | 2001-08-16 | 16 | 27656.4201 | 06/29 | 16:00 | 26567 | 1900-06-29 | 16 | 27555 | 2003-06-29 | 15 | 26567 | 27707 | 4.154% |  | 0 | 0 | 0
E510 | 30593.05 | 29-Apr | 19 | 31188 | 2001-07-20 | 15 | 31188 | 2001-07-20 | 15 | 31194.5493 | 06/17 | 14:00 | 29948 | 1900-06-17 | 14 | 31097 | 2003-06-17 | 13 | 29948 | 31194.5493 | 4.038% |  | 0 | 0 | 0
E520 | 27329.6 | 28-Sep | 15 | 27878 | 2004-08-14 | 16 | 27878 | 2004-07-23 | 16 | 27731.0711 | 06/29 | 16:00 | 26675 | 1900-07-20 | 16 | 28343 | 2003-05-23 | 15 | 26675 | 28343 | 6.035% |  | 0 | 0 | 0
E522 | 27383.59 | 12-Mai | 15 | 27868 | 2002-08-16 | 16 | 27866 | 2002-08-16 | 16 | 27698.162 | 06/29 | 16:00 | 26514 | 1900-06-29 | 16 | 27636 | 2003-06-29 | 15 | 26514 | 27868 | 4.925% |  | 0 | 0 | 0
E525 | 27739.77 | 26-Jul | 16 | 27466 | 2002-07-08 | 16 | 27466 | 2002-07-08 | 16 | 27564.3415 | 06/29 | 16:00 | 26683 | 1900-06-29 | 16 | 27462 | 2003-06-29 | 15 | 26683 | 27739.77 | 3.857% |  | 0 | 0 | 0
E530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19656.1402 | 07/20 | 15:00 | 18776 | 1900-06-04 | 15 | 19626 | 2003-07-08 | 15 | 18776 | 19834.1 | 5.424% |  | 0 | 0 | 0
E540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19812.465 | 07/20 | 15:00 | 18794 | 1900-06-04 | 15 | 19799 | 2003-08-16 | 15 | 18794 | 19812.465 | 5.2% |  | 0 | 0 | 0
E545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19538.7609 | 07/20 | 15:00 | 18764 | 1900-07-20 | 15 | 19497 | 2003-06-04 | 15 | 18764 | 20075.2 | 6.734% |  | 0 | 0 | 0
Hourly Integrated Maxima (Sensible Coil Load and Latent Coil Load)
Sensible Coil Load (Wh,th) | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 | 23457 | 1900-07-20 | 15 | 22908 | 2003-06-04 | 15 | 22908 | 23463.1755 | 2.388% |  | 0 | 0 | 0
E310 | 23094.3 | 10-Sep | 15 | 23080 | 2004-09-10 | 16 | 23119 | 2004-06-04 | 16 | 23145.0651 | 07/11 | 16:00 | 23078 | 1900-09-10 | 15 | 22649 | 2003-06-13 | 16 | 22649 | 23145.0651 | 2.154% |  | 0 | 0 | 0
E320 | 31315.6 | 24-Apr | 16 | 31119 | 2004-04-24 | 16 | 31072 | 2002-04-24 | 16 | 31528.7254 | 04/24 | 15:00 | 31134 | 1900-06-03 | 16 | 30967 | 2003-04-24 | 15 | 30967 | 31528.7254 | 1.801% |  | 0 | 0 | 0
E330 | 33226.1 | 14-Jun | 14 | 33410 | 2002-06-14 | 14 | 34490 | 2002-06-14 | 15 | 34692.1931 | 06/14 | 14:00 | 33997 | 1900-04-24 | 16 | 33421 | 2003-09-09 | 14 | 33226.1 | 34692.1931 | 4.328% |  | 0 | 0 | 0
E340 | 32828.9 | 24-Apr | 15 | 32086 | 2002-05-16 | 16 | 32086 | 2002-05-16 | 16 | 32737.1011 | 04/24 | 15:00 | 32940 | 1900-04-24 | 16 | 32180 | 2003-04-24 | 15 | 32086 | 32940 | 2.63% |  | 0 | 0 | 0
E350 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.136 | 07/20 | 15:00 | 23457 | 1900-07-20 | 15 | 22876 | 2003-07-10 | 15 | 22876 | 23463.136 | 2.526% |  | 0 | 0 | 0
E360 | 32060.7 | 24-Apr | 16 | 32111 | 2003-04-24 | 16 | 32065 | 2004-04-24 | 16 | 32409.2976 | 04/24 | 16:00 | 31981 | 1900-04-24 | 16 | 32179 | 2003-04-24 | 15 | 31981 | 32409.2976 | 1.333% |  | 0 | 0 | 0
E400 | 23277.5 | 29-Jul | 15 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1222 | 07/20 | 15:00 |  |  |  | 22877 | 2003-07-08 | 16 | 22877 | 23463.1222 | 2.526% |  | 0 | 0 | 0
E410 | 23265.7 | 10-Sep | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | [6 empty] | 22893 | 2003-07-29 | 15 | 22893 | 23265.7 | 1.611% |  | 0 | 0 | 0
E420 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 |  |  |  | 22893 | 2003-07-29 | 15 | 22893 | 23463.1755 | 2.457% |  | 0 | 0 | 0
E430 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 |  |  |  | 22893 | 2003-07-29 | 15 | 22893 | 23463.1755 | 2.457% |  | 0 | 0 | 0
E440 | 23277.4 | 20-Jul | 16 | 23203 | 2002-07-20 | 15 | 23205 | 2002-07-20 | 15 | 23463.1755 | 07/20 | 15:00 |  |  |  | 22875 | 2003-08-16 | 16 | 22875 | 23463.1755 | 2.535% |  | 0 | 0 | 0
E500 | 19549.2 | 28-Oct | 15 | 20009 | 2003-06-04 | 16 | 20008 | 2002-09-10 | 16 | 19795.9105 | 07/20 | 15:00 | 18776 | 1900-06-04 | 15 | 19818 | 2003-07-29 | 15 | 18776 | 20009 | 6.272% |  | 0 | 0 | 0
E510 | 21729.2 | 29-Apr | 19 | 22513 | 2002-07-11 | 15 | 22513 | 2003-07-11 | 15 | 22227.967 | 07/20 | 16:00 | 21121 | 1900-06-04 | 13 | 22269 | 2003-07-20 | 14 | 21121 | 22513 | 6.309% |  | 0 | 0 | 0
E520 | 19415.9 | 28-Sep | 15 | 20159 | 2004-05-26 | 16 | 20154 | 2004-05-26 | 16 | 20012.5751 | 07/30 | 16:00 | 18969 | 1900-07-20 | 16 | 20378 | 2003-05-23 | 15 | 18969 | 20378 | 7.099% |  | 0 | 0 | 0
E522 | 19488.8 | 12-Mai | 15 | 20137 | 2002-07-11 | 16 | 20135 | 2002-07-11 | 16 | 19901.8714 | 07/20 | 15:00 | 18785 | 1900-06-04 | 15 | 19920 | 2003-08-16 | 15 | 18785 | 20137 | 6.853% |  | 0 | 0 | 0
E525 | 19702.7 | 26-Jul | 16 | 19850 | 2002-04-24 | 16 | 19850 | 2002-04-24 | 16 | 19599.0538 | 07/20 | 15:00 | 18759 | 1900-06-04 | 15 | 19661 | 2003-06-04 | 15 | 18759 | 19850 | 5.575% |  | 0 | 0 | 0
E530 | 19834.1 | 29-Mai | 15 | 19576 | 2002-04-24 | 16 | 19575 | 2002-04-24 | 16 | 19656.1402 | 07/20 | 15:00 | 18776 | 1900-06-04 | 15 | 19626 | 2003-07-08 | 15 | 18776 | 19834.1 | 5.424% |  | 0 | 0 | 0
E540 | 19575 | 30-Aug | 16 | 19766 | 2002-04-24 | 16 | 19766 | 2002-04-24 | 16 | 19812.465 | 07/20 | 15:00 | 18794 | 1900-06-04 | 15 | 19799 | 2003-08-16 | 15 | 18794 | 19812.465 | 5.2% |  | 0 | 0 | 0
E545 | 20075.2 | 17-Jun | 16 | 19475 | 2002-04-24 | 16 | 19474 | 2002-04-24 | 16 | 19538.7609 | 07/20 | 15:00 | 18759 | 1900-06-04 | 15 | 19497 | 2003-06-04 | 15 | 18759 | 20075.2 | 6.76% |  | 0 | 0 | 0
Latent Coil Load (Wh,th) | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9394 | 2001-09-03 | 15 | 10595.085 | 07/10 | 13:00 | 10375 | 1900-09-03 | 15 | 10392 | 2003-09-03 | 15 | 9304 | 10595.085 | 12.98% |  | 0 | 0 | 0
E310 | 15907 | 03-Sep | 15 | 15139 | 2001-09-03 | 15 | 15270 | 2001-09-03 | 15 | 16644.3073 | 08/04 | 15:00 | 16112 | 1900-08-04 | 15 | 16077 | 2003-09-03 | 16 | 15139 | 16644.3073 | 9.492% |  | 0 | 0 | 0
E320 | 23147.3 | 02-Oct | 10 | 31497 | 2002-10-02 | 9 | 31503 | 2002-10-02 | 9 | 22756.175 | 10/02 | 10:00 | 21697 | 1900-09-17 | 12 | 21929 | 2003-10-01 | 20 | 21697 | 31503 | 38.57% |  | 0 | 0 | 0
E330 | 27825.2 | 18-Sep | 16 | 26941 | 2003-09-18 | 15 | 40809 | 2002-10-02 | 9 | 27596.7005 | 09/18 | 16:00 | 28184 | 1900-09-18 | 15 | 27488 | 2003-09-18 | 15 | 26941 | 40809 | 46.53% |  | 0 | 0 | 0
E340 | 24848.3 | 02-Oct | 9 | 30451 | 2002-10-02 | 9 | 36011 | 2002-10-02 | 9 | 24435.7652 | 10/02 | 10:00 | 24225 | 1900-09-03 | 17 | 23794 | 2003-10-01 | 20 | 23794 | 36011 | 44.76% |  | 0 | 0 | 0
E350 | 9751.26 | 01-Oct | 13 | 9303 | 2001-09-03 | 15 | 9393 | 2001-09-03 | 15 | 10595.6426 | 07/10 | 13:00 | 10755 | 1900-10-02 | 8 | 11603 | 2003-08-03 | 7 | 9303 | 11603 | 22.48% |  | 0 | 0 | 0
E360 | 9275.16 | 02-Oct | 10 | 10026 | 2002-10-02 | 9 | 10336 | 2002-10-02 | 9 | 8907.2199 | 10/02 | 10:00 | 8859 | 1900-09-03 | 17 | 8934 | 2003-09-03 | 17 | 8859 | 10336 | 15.73% |  | 0 | 0 | 0
E400 | 27075.3 | 16-Sep | 15 | 25578 | 2002-09-18 | 14 | 32396 | 2003-09-18 | 15 | 26767.6767 | 09/16 | 15:00 |  |  |  | 26645 | 2003-09-16 | 14 | 25578 | 32396 | 24.62% |  | 0 | 0 | 0
E410 | 11138.9 | 16-Sep | 15 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | [6 empty] | 10377 | 2003-09-09 | 15 | 9304 | 11138.9 | 18.25% |  | 0 | 0 | 0
E420 | 9751.04 | 01-Oct | 13 | 9304 | 2001-09-03 | 15 | 9394 | 2003-09-03 | 15 | 10595.085 | 07/10 | 13:00 |  |  |  | 10394 | 2003-09-03 | 15 | 9304 | 10595.085 | 13.06% |  | 0 | 0 | 0
E430 | 9635.7 | 03-Sep | 16 | 11105 | 2004-10-24 | 14 | 11101 | 2003-05-21 | 15 | 11375.3248 | 10/24 | 13:00 |  |  |  | 10394 | 2003-09-03 | 15 | 9635.7 | 11375.3248 | 16.22% |  | 0 | 0 | 0
E440 | 9635.7 | 03-Sep | 16 | 9304 | 2001-09-03 | 15 | 9391 | 2003-09-03 | 15 | 10595.085 | 07/10 | 13:00 |  |  |  | 10139 | 2003-09-03 | 15 | 9304 | 10595.085 | 13.16% |  | 0 | 0 | 0
E500 | 7965.46 | 06-Oct | 15 | 7733 | 2001-09-03 | 15 | 7733 | 2001-09-03 | 15 | 7908.9572 | 06/29 | 16:00 | 7805 | 1900-06-29 | 16 | 7762 | 2003-06-29 | 15 | 7733 | 7965.46 | 2.973% |  | 0 | 0 | 0
E510 | 8892.56 | 15-Sep | 11 | 8723 | 2002-10-02 | 9 | 8723 | 2003-10-02 | 9 | 9041.0375 | 06/17 | 14:00 | 8850 | 1900-06-17 | 14 | 8874 | 2003-06-17 | 13 | 8723 | 9041.0375 | 3.593% |  | 0 | 0 | 0
E520 | 7913.7 | 28-Sep | 15 | 7785 | 2001-09-03 | 15 | 7785 | 2001-09-03 | 15 | 7785.2261 | 06/29 | 16:00 | 7726 | 1900-06-30 | 16 | 7964 | 2003-05-23 | 15 | 7726 | 7964 | 3.041% |  | 0 | 0 | 0
E522 | 7906.7 | 02-Mai | 15 | 7760 | 2001-09-03 | 15 | 7760 | 2001-09-03 | 15 | 7850.1656 | 06/29 | 16:00 | 7743 | 1900-06-29 | 16 | 7745 | 2003-06-29 | 15 | 7743 | 7906.7 | 2.1% |  | 0 | 0 | 0
E525 | 8037.07 | 26-Jul | 16 | 7663 | 2001-09-03 | 15 | 7663 | 2001-09-03 | 15 | 8006.3955 | 06/29 | 16:00 | 7938 | 1900-06-29 | 16 | 7820 | 2003-06-29 | 15 | 7663 | 8037.07 | 4.762% |  | 0 | 0 | 0
E530 | 1.6431e-11 | 18-Jun | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 110.1783 | 03/16 | 10:00 | 179 | 1900-03-11 | 11 | 35.9 | 2003-11-01 | 20 | 0 | 179 | 330.4% |  | 0 | 0 | 0
E540 | 627.186 | 11-Mar | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 1636.359 | 03/11 | 10:00 | 845 | 1900-03-11 | 10 | 1181 | 2003-03-11 | 10 | 0 | 1636.359 | 228.9% |  | 0 | 0 | 0
E545 | 1.8119e-11 | 01-Jul | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2784e-12 | 05/29 | 13:00 | 4 | 1900-07-20 | 15 | 0 | 2003-01-01 | 1 | 0 | 4 | 600% |  | 0 | 0 | 0
e300results.xls r:a07..w102; 08/19/04
Hourly Integrated Maxima and Minima (COP2)
Maximum COP2 | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 4.1683 | 16-Apr | 3 | 3.869 | 2002-04-30 | 16 | 3.857 | 2002-04-30 | 16 | 3.9232 | 04/30 | 15:00 | 3.8706 | 1900-04-30 | 16 | 3.88 | 2003-04-30 | 16 | 3.857 | 4.1683 | 7.926% |  | 0 | 0 | 0
E310 | 4.1433 | 30-Apr | 15 | 4.141 | 2002-04-30 | 16 | 4.128 | 2002-04-30 | 16 | 4.1954 | 04/30 | 15:00 | 4.1276 | 1900-04-30 | 15 | 4.12 | 2003-04-30 | 15 | 4.12 | 4.1954 | 1.821% |  | 0 | 0 | 0
E320 | 4.1683 | 16-Apr | 3 | 5.143 | 2002-10-02 | 9 | 4.967 | 2002-10-02 | 9 | 3.9648 | 09/16 | 15:00 | 3.9433 | 1900-09-16 | 15 | 4.38 | 2003-12-18 | 3 | 3.9433 | 5.143 | 27.1% |  | 0 | 0 | 0
E330 | 4.1683 | 16-Apr | 3 | 4.109 | 2003-06-17 | 16 | 5.595 | 2002-10-02 | 9 | 4.0962 | 09/16 | 14:00 | 4.1219 | 1900-06-17 | 16 | 4.05 | 2003-06-17 | 16 | 4.05 | 5.595 | 35.46% |  | 0 | 0 | 0
E340 | 4.1683 | 16-Apr | 3 | 4.621 | 2002-10-02 | 9 | 5.339 | 2002-10-02 | 9 | 4.0147 | 09/16 | 15:00 | 4.0172 | 1900-09-16 | 16 | 3.95 | 2003-09-16 | 16 | 3.95 | 5.339 | 31.92% |  | 0 | 0 | 0
E350 | 4.1683 | 16-Apr | 3 | 3.889 | 2003-04-27 | 5 | 3.863 | 2004-10-05 | 3 | 4.3453 | 10/13 | 01:00 | 3.9321 | 1900-10-04 | 24 | 3.88 | 2003-04-30 | 16 | 3.863 | 4.3453 | 12.02% |  | 0 | 0 | 0
E360 | 4.401 | 05-Oct | 1 | 4.428 | 2002-10-04 | 24 | 4.427 | 2002-10-04 | 24 | 4.4308 | 10/04 | 24:00 | 4.432 | 1900-10-04 | 24 | 4.44 | 2003-10-04 | 24 | 4.401 | 4.44 | 0.8819% |  | 0 | 0 | 0
E400 | 4.0769 | 16-Sep | 15 | 4.088 | 2003-06-17 | 16 | 4.776 | 2003-09-18 | 15 | 4.0961 | 09/16 | 14:00 |  |  |  | 4.05 | 2003-06-17 | 16 | 4.05 | 4.776 | 17.21% |  | 0 | 0 | 0
E410 | 3.8879 | 30-Apr | 15 | 3.903 | 2002-04-30 | 15 | 3.855 | 2002-04-30 | 16 | [6 empty] | 3.84 | 2003-05-21 | 15 | 3.84 | 3.903 | 1.627% |  | 0 | 0 | 0
E420 | 3.7813 | 27-Sep | 16 | 3.807 | 2003-05-21 | 15 | 3.759 | 2003-09-27 | 15 | 3.8446 | 05/21 | 15:00 |  |  |  | 3.94 | 2003-05-21 | 13 | 3.759 | 3.94 | 4.73% |  | 0 | 0 | 0
E430 | 3.7813 | 27-Sep | 16 | 3.805 | 2003-10-24 | 15 | 3.759 | 2003-09-27 | 15 | 3.8044 | 05/21 | 15:00 |  |  |  | 3.93 | 2003-04-30 | 13 | 3.759 | 3.93 | 4.481% |  | 0 | 0 | 0
E440 | 3.8835 | 12-Dez | 7 | 3.774 | 2002-09-27 | 15 | 3.759 | 2002-09-27 | 15 | 3.8044 | 05/21 | 15:00 |  |  |  | 3.81 | 2003-04-30 | 15 | 3.759 | 3.8835 | 3.27% |  | 0 | 0 | 0
E500 | 4.2751 | 13-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.2343 | 03/16 | 10:00 | 4.1846 | 1900-03-16 | 10 | 4.14 | 2003-04-30 | 16 | 4.14 | 7.367 | 65.63% |  | 0 | 0 | 0
E510 | 4.6925 | 05-Oct | 1 | 7.367 | 2004-03-11 | 10 | 5.301 | 2004-10-13 | 9 | 4.7069 | 10/05 | 01:00 | 4.6896 | 1900-10-04 | 24 | 4.53 | 2003-05-04 | 3 | 4.53 | 7.367 | 54.41% |  | 0 | 0 | 0
E520 | 3.8137 | 30-Apr | 15 | 4.896 | 2004-03-16 | 10 | 4.652 | 2003-03-16 | 10 | 3.838 | 04/30 | 15:00 | 3.8017 | 1900-04-30 | 16 | 3.84 | 2003-04-30 | 16 | 3.8017 | 4.896 | 26.43% |  | 0 | 0 | 0
E522 | 3.9855 | 16-Mar | 10 | 6.233 | 2004-03-11 | 10 | 5.678 | 2004-03-11 | 10 | 4.0074 | 04/30 | 15:00 | 3.9858 | 1900-04-30 | 16 | 4 | 2003-04-30 | 16 | 3.9855 | 6.233 | 48.35% |  | 0 | 0 | 0
E525 | 4.7178 | 13-Oct | 1 | 6.325 | 2004-04-12 | 9 | 6.031 | 2004-03-16 | 10 | 4.6776 | 03/16 | 10:00 | 4.6381 | 1900-03-16 | 10 | 4.4 | 2003-03-16 | 10 | 4.4 | 6.325 | 37.51% |  | 0 | 0 | 0
E530 | 4.0061 | 02-Nov | 1 | 3.981 | 2004-03-11 | 10 | 3.85 | 2004-10-13 | 9 | 3.9202 | 03/16 | 10:00 | 3.84 | 1900-03-16 | 10 | 3.88 | 2003-03-16 | 10 | 3.84 | 4.0061 | 4.243% |  | 0 | 0 | 0
E540 | 3.456 | 30-Apr | 15 | 3.456 | 2004-04-30 | 16 | 3.455 | 2004-04-30 | 16 | 3.5169 | 03/16 | 10:00 | 3.6667 | 1900-03-11 | 22 | 3.69 | 2003-10-17 | 5 | 3.455 | 3.69 | 6.638% |  | 0 | 0 | 0
E545 | 4.2505 | 16-Mar | 10 | 4.275 | 2004-03-16 | 10 | 4.428 | 2004-03-16 | 10 | 4.2157 | 03/16 | 10:00 | 4.1565 | 1900-03-16 | 10 | 4.17 | 2003-03-16 | 10 | 4.1565 | 4.428 | 6.39% |  | 0 | 0 | 0
Minimum COP2 | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 2.7931 | 24-Apr | 17 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 2.7856 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 2.7744 | 2.81 | 1.274% |  | 0 | 0 | 0
E310 | 2.8652 | 01-Dec | 15 | 2.85 | 2002-12-01 | 14 | 2.851 | 2002-12-01 | 12 | 2.8671 | 12/01 | 15:00 | 2.8726 | 1900-12-01 | 15 | 2.87 | 2003-12-01 | 14 | 2.85 | 2.8726 | 0.791% |  | 0 | 0 | 0
E320 | 2.8252 | 31-Mar | 14 | 2.801 | 2002-12-01 | 14 | 2.805 | 2003-12-01 | 15 | 2.8231 | 03/31 | 15:00 | 2.8145 | 1900-03-31 | 15 | 2.83 | 2003-03-31 | 14 | 2.801 | 2.83 | 1.03% |  | 0 | 0 | 0
E330 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.798 | 2.84 | 1.49% |  | 0 | 0 | 0
E340 | 2.8252 | 31-Mar | 14 | 2.798 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.798 | 2.84 | 1.49% |  | 0 | 0 | 0
E350 | 2.7904 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 | 2.7859 | 1900-06-13 | 17 | 2.81 | 2003-06-14 | 12 | 2.7744 | 2.81 | 1.275% |  | 0 | 0 | 0
E360 | 2.8252 | 31-Mar | 14 | 2.799 | 2002-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.8286 | 03/31 | 15:00 | 2.8233 | 1900-03-31 | 15 | 2.84 | 2003-03-31 | 14 | 2.799 | 2.84 | 1.454% |  | 0 | 0 | 0
E400 | 2.7819 | 31-Mar | 19 | 2.734 | 2002-12-03 | 15 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.734 | 2.81 | 2.747% |  | 0 | 0 | 0
E410 | 2.7858 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | [6 empty] | 2.81 | 2003-06-14 | 12 | 2.7858 | 2.81 | 0.8635% |  | 0 | 0 | 0
E420 | 2.7931 | 24-Apr | 17 | 2.798 | 2004-12-01 | 14 | 2.801 | 2003-12-01 | 12 | 2.7744 | 06/13 | 17:00 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.7744 | 2.81 | 1.274% |  | 0 | 0 | 0
E430 | 2.7711 | 30-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 |  |  |  | 2.81 | 2003-06-14 | 12 | 2.734 | 2.81 | 2.749% |  | 0 | 0 | 0
E440 | 2.7825 | 31-Mar | 19 | 2.734 | 2002-12-03 | 13 | 2.735 | 2003-12-03 | 13 | 2.7744 | 06/13 | 17:00 |  |  |  | 2.81 | 2003-04-08 | 13 | 2.734 | 2.81 | 2.746% |  | 0 | 0 | 0
E500 | 2.6852 | 30-Jul | 12 | 2.693 | 2002-07-29 | 12 | 2.652 | 2004-03-30 | 17 | 2.6947 | 07/30 | 12:00 | 2.6665 | 1900-07-30 | 12 | 2.71 | 2003-07-29 | 12 | 2.652 | 2.71 | 2.161% |  | 0 | 0 | 0
E510 | 2.888 | 31-Mar | 15 | 2.817 | 2004-04-05 | 17 | 2.652 | 2004-03-30 | 17 | 2.8993 | 03/31 | 15:00 | 2.8817 | 1900-03-31 | 15 | 2.9 | 2003-03-31 | 14 | 2.652 | 2.9 | 8.733% |  | 0 | 0 | 0
E520 | 2.4417 | 30-Jul | 12 | 2.463 | 2004-04-05 | 17 | 2.394 | 2004-04-05 | 17 | 2.4618 | 07/30 | 12:00 | 2.3333 | 1900-01-28 | 10 | 2.47 | 2003-07-30 | 12 | 2.3333 | 2.47 | 5.63% |  | 0 | 0 | 0
E522 | 2.5689 | 08-Jul | 17 | 2.572 | 2002-07-29 | 12 | 2.562 | 2004-03-31 | 17 | 2.5777 | 07/30 | 12:00 | 2.4286 | 1900-03-30 | 17 | 2.59 | 2003-07-29 | 12 | 2.4286 | 2.59 | 6.331% |  | 0 | 0 | 0
E525 | 2.9111 | 14-Jul | 17 | 2.939 | 2003-07-30 | 12 | 2.814 | 2004-03-31 | 17 | 2.9333 | 07/30 | 12:00 | 2.8941 | 1900-07-29 | 12 | 2.9 | 2003-07-29 | 12 | 2.814 | 2.939 | 4.312% |  | 0 | 0 | 0
E530 | 2.5013 | 30-Jul | 12 | 2.495 | 2002-07-29 | 12 | 2.498 | 2002-07-29 | 12 | 2.4945 | 07/30 | 12:00 | 2.4733 | 1900-07-29 | 12 | 2.52 | 2003-07-29 | 12 | 2.4733 | 2.52 | 1.871% |  | 0 | 0 | 0
E540 | 2.253 | 30-Jul | 12 | 2.261 | 2003-07-29 | 12 | 2.262 | 2012-07-30 | 12 | 2.2794 | 07/30 | 12:00 | 2.1429 | 1900-04-05 | 20 | 2.28 | 2003-07-29 | 12 | 2.1429 | 2.28 | 6.105% |  | 0 | 0 | 0
E545 | 2.7325 | 14-Jul | 17 | 2.72 | 2003-07-29 | 12 | 2.722 | 2002-07-30 | 12 | 2.6585 | 07/30 | 12:00 | 2.692 | 1900-07-29 | 12 | 2.72 | 2003-07-29 | 12 | 2.6585 | 2.7325 | 2.733% |  | 0 | 0 | 0
Hourly Integrated Maxima and Minima (IDB)
Maximum IDB (°C) | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0033 | 09/23 | 08:00 | 25.05 | 1900-02-20 | 17 | 26.19 | 2003-11-03 | 15 | 25.0033 | 26.1999 | 4.703% |  | 0 | 0 | 0
E310 | 27.0778 | 20-Jul | 15 | 26.89 | 2004-07-20 | 16 | 26.72 | 2002-07-20 | 16 | 26.5567 | 07/20 | 16:00 | 26.62 | 1900-07-20 | 15 | 27.19 | 2003-07-08 | 15 | 26.5567 | 27.19 | 2.359% |  | 0 | 0 | 0
E320 | 32.3604 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.5 | 2003-07-08 | 16 | 31.844 | 07/20 | 15:00 | 32.32 | 1900-07-20 | 15 | 31.65 | 2003-07-08 | 15 | 31.5 | 32.3604 | 2.699% |  | 0 | 0 | 0
E330 | 32.2321 | 20-Jul | 15 | 31.72 | 2004-07-08 | 16 | 32 | 2003-07-20 | 16 | 31.4963 | 07/20 | 15:00 | 31.9 | 1900-07-20 | 15 | 31.3 | 2003-07-08 | 15 | 31.3 | 32.2321 | 2.933% |  | 0 | 0 | 0
E340 | 32.3066 | 20-Jul | 15 | 31.61 | 2003-07-08 | 16 | 31.56 | 2003-07-08 | 16 | 31.7451 | 07/20 | 15:00 | 32.15 | 1900-07-20 | 15 | 31.58 | 2003-07-08 | 15 | 31.56 | 32.3066 | 2.346% |  | 0 | 0 | 0
E350 | 34.5841 | 01-Oct | 24 | 34.94 | 2003-06-23 | 24 | 34.94 | 2004-06-24 | 24 | 35.0021 | 10/01 | 02:00 | 35 | 1900-04-21 | 1 | 35 | 2003-04-21 | 2 | 34.5841 | 35.0021 | 1.197% |  | 0 | 0 | 0
E360 | 33.7585 | 10-Jul | 13 | 32.78 | 2002-07-20 | 15 | 32.56 | 2004-07-20 | 16 | 32.8198 | 07/10 | 13:00 | 33 | 1900-07-20 | 15 | 33.13 | 2003-07-10 | 12 | 32.56 | 33.7585 | 3.631% |  | 0 | 0 | 0
E400 | 27.1148 | 16-Sep | 15 | 27.56 | 2003-09-16 | 16 | 28.83 | 2002-09-18 | 16 | 26.9032 | 09/16 | 16:00 |  |  |  | 26.04 | 2003-08-15 | 15 | 26.04 | 28.83 | 10.22% |  | 0 | 0 | 0
E410 | 26.8256 | 23-Oct | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | [6 empty] | 26.19 | 2003-11-03 | 15 | 25.11 | 26.8256 | 6.647% |  | 0 | 0 | 0
E420 | 26.1999 | 07-Jul | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0033 | 09/23 | 08:00 |  |  |  | 26.23 | 2003-10-20 | 15 | 25.0033 | 26.23 | 4.805% |  | 0 | 0 | 0
E430 | 27.1992 | 01-Nov | 16 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0038 | 04/24 | 20:00 |  |  |  | 26.45 | 2003-10-23 | 15 | 25.0038 | 27.1992 | 8.518% |  | 0 | 0 | 0
E440 | 27.0452 | 28-Apr | 15 | 25.11 | 2002-04-22 | 15 | 25.11 | 2002-04-22 | 15 | 25.0038 | 04/24 | 20:00 |  |  |  | 26.26 | 2003-10-23 | 15 | 25.0038 | 27.0452 | 7.942% |  | 0 | 0 | 0
E500 | 25.8054 | 30-Apr | 15 | 25.11 | 2001-04-21 | 16 | 25.11 | 2001-04-21 | 16 | 25.0017 | 04/05 | 19:00 | 25.02 | 1900-03-30 | 17 | 25 | 2003-03-11 | 11 | 25 | 25.8054 | 3.199% |  | 0 | 0 | 0
E510 | 26.1003 | 09-Jul | 15 | 25.11 | 2001-04-21 | 3 | 25.11 | 2001-04-21 | 3 | 25.0017 | 04/05 | 19:00 | 25.02 | 1900-03-30 | 17 | 25 | 2003-04-24 | 12 | 25 | 26.1003 | 4.362% |  | 0 | 0 | 0
E520 | 16.1232 | 15-Aug | 15 | 16.11 | 2002-08-16 | 16 | 15.94 | 2004-07-10 | 16 | 15.2669 | 07/20 | 16:00 | 15.98 | 1900-07-20 | 15 | 18.62 | 2003-06-04 | 16 | 15.2669 | 18.62 | 20.52% |  | 0 | 0 | 0
E522 | 21.0091 | 16-Jul | 15 | 20.11 | 2001-04-21 | 15 | 20.11 | 2003-04-21 | 15 | 20.0027 | 04/17 | 24:00 | 20.05 | 1900-03-13 | 22 | 20.93 | 2003-04-21 | 15 | 20.0027 | 21.0091 | 4.941% |  | 0 | 0 | 0
E525 | 36.08 | 10-Mai | 16 | 35.06 | 2003-04-21 | 16 | 35.06 | 2003-04-21 | 16 | 34.9964 | 03/11 | 12:00 | 35 | 1900-03-11 | 10 | 35 | 2003-03-11 | 11 | 34.9964 | 36.08 | 3.078% |  | 0 | 0 | 0
E530 | 26.116 | 04-Jun | 15 | 25.06 | 2001-04-21 | 16 | 25.06 | 2001-04-21 | 16 | 25.0027 | 04/05 | 20:00 | 25.02 | 1900-03-30 | 17 | 25 | 2003-03-11 | 11 | 25 | 26.116 | 4.427% |  | 0 | 0 | 0
E540 | 16.1465 | 21-Sep | 16 | 15.11 | 2004-05-31 | 16 | 15.11 | 2004-05-31 | 16 | 15.0028 | 04/16 | 01:00 | 15.05 | 1900-01-27 | 20 | 15 | 2003-03-11 | 10 | 15 | 16.1465 | 7.525% |  | 0 | 0 | 0
E545 | 35.6715 | 20-Jul | 15 | 35 | 2003-04-21 | 15 | 35 | 2004-04-21 | 15 | 35.0003 | 07/14 | 18:00 | 35 | 1900-03-11 | 10 | 35 | 2003-03-11 | 11 | 35 | 35.6715 | 1.912% |  | 0 | 0 | 0
Minimum IDB (°C) | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E310 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7262 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E320 | 7.93 | 06-Jan | 6 | 10.83 | 2001-01-06 | 7 | 10.78 | 2001-01-06 | 7 | 7.7562 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 10.83 | 44.07% |  | 0 | 0 | 0
E330 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7247 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E340 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7247 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E350 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E360 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7265 | 01/06 | 06:00 | 8 | 1900-01-05 | 5 | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.09% |  | 0 | 0 | 0
E400 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 22.97% |  | 0 | 0 | 0
E410 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | [6 empty] | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 23.28% |  | 0 | 0 | 0
E420 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 22.97% |  | 0 | 0 | 0
E430 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 |  |  |  | 6.99 | 2003-01-06 | 5 | 6.99 | 8.89 | 22.97% |  | 0 | 0 | 0
E440 | 7.93 | 06-Jan | 6 | 8.89 | 2001-01-06 | 6 | 8.83 | 2001-01-06 | 6 | 8.7263 | 01/06 | 06:00 |  |  |  | 7 | 2003-01-06 | 5 | 7 | 8.89 | 22.84% |  | 0 | 0 | 0
E500 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8363 | 12/21 | 01:00 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 146.5% |  | 0 | 0 | 0
E510 | 8.427 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.8363 | 12/21 | 01:00 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 146.5% |  | 0 | 0 | 0
E520 | 8.3053 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.733 | 12/21 | 01:00 | 8.51 | 1900-12-20 | 20 | 13.57 | 2003-11-01 | 7 | 7.89 | 13.57 | 61.83% |  | 0 | 0 | 0
E522 | 8.4141 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.7911 | 12/21 | 01:00 | 8.54 | 1900-12-20 | 20 | 15.98 | 2003-04-12 | 19 | 7.94 | 15.98 | 83.41% |  | 0 | 0 | 0
E525 | 8.4442 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 8.9123 | 12/21 | 01:00 | 8.54 | 1900-12-20 | 20 | 33.01 | 2003-04-01 | 8 | 7.94 | 33.01 | 200.5% |  | 0 | 0 | 0
E530 | 8.4215 | 20-Dec | 22 | 8.17 | 2004-12-20 | 12 | 7.94 | 2003-12-20 | 11 | 8.9817 | 12/21 | 02:00 | 8.54 | 1900-12-20 | 20 | 24.04 | 2003-04-15 | 5 | 7.94 | 24.04 | 146.2% |  | 0 | 0 | 0
E540 | 8.2278 | 20-Dec | 22 | 8.11 | 2004-12-20 | 12 | 7.89 | 2003-12-20 | 12 | 8.8775 | 12/21 | 01:00 | 8.51 | 1900-12-20 | 20 | 14.95 | 2003-12-19 | 1 | 7.89 | 14.95 | 74.89% |  | 0 | 0 | 0
E545 | 8.4486 | 20-Dec | 22 | 8.17 | 2004-12-20 | 13 | 7.94 | 2003-12-20 | 12 | 9.0584 | 12/21 | 02:00 | 8.54 | 1900-12-20 | 20 | 33.01 | 2003-04-01 | 8 | 7.94 | 33.01 | 200.1% |  | 0 | 0 | 0
e300results.xls r:a111..aa204; 07/19/04
Hourly Integrated Maxima and Minima (Zone Humidity Ratio)
Maximum Humidity Ratio | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 0.013284 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 | 0.013457 | 1900-11-16 | 16 | 0.0134 | 2003-11-16 | 16 | 0.013284 | 0.0138 | 3.812% |  | 0 | 0 | 0
E310 | 0.01575 | 01-Oct | 23 | 0.0188 | 2002-10-15 | 9 | 0.0189 | 2002-10-15 | 9 | 0.015502 | 10/01 | 08:00 | 0.015432 | 1900-10-02 | 8 | 0.0157 | 2003-10-02 | 8 | 0.015432 | 0.0189 | 20.79% |  | 0 | 0 | 0
E320 | 0.018017 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0176 | 2002-07-10 | 12 | 0.017703 | 10/01 | 11:00 | 0.017547 | 1900-07-10 | 12 | 0.0177 | 2003-07-10 | 12 | 0.017547 | 0.018017 | 2.653% |  | 0 | 0 | 0
E330 | 0.017651 | 10-Jul | 12 | 0.0178 | 2003-10-02 | 9 | 0.0177 | 2002-07-10 | 13 | 0.017823 | 07/10 | 12:00 | 0.017045 | 1900-07-10 | 13 | 0.0177 | 2003-07-10 | 12 | 0.017045 | 0.017823 | 4.418% |  | 0 | 0 | 0
E340 | 0.017871 | 10-Jul | 13 | 0.0177 | 2002-07-10 | 12 | 0.0174 | 2002-07-10 | 12 | 0.017707 | 07/10 | 12:00 | 0.017272 | 1900-07-10 | 13 | 0.0177 | 2003-07-10 | 12 | 0.017272 | 0.017871 | 3.404% |  | 0 | 0 | 0
E350 | 0.016758 | 01-Oct | 24 | 0.0199 | 2002-08-02 | 22 | 0.0199 | 2002-08-02 | 22 | 0.016945 | 10/02 | 01:00 | 0.016479 | 1900-10-02 | 2 | 0.0166 | 2003-10-02 | 1 | 0.016479 | 0.0199 | 19.26% |  | 0 | 0 | 0
E360 | 0.013433 | 10-Jul | 13 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 | 0.013457 | 1900-11-16 | 16 | 0.0134 | 2003-11-16 | 16 | 0.0134 | 0.0138 | 2.952% |  | 0 | 0 | 0
E400 | 0.016944 | 05-Apr | 22 | 0.017 | 2002-04-05 | 21 | 0.017 | 2003-04-05 | 21 | 0.016893 | 04/05 | 22:00 |  |  |  | 0.0173 | 2003-04-22 | 6 | 0.016893 | 0.0173 | 2.389% |  | 0 | 0 | 0
E410 | 0.016835 | 05-Apr | 22 | 0.0169 | 2002-04-02 | 5 | 0.0169 | 2002-04-02 | 5 | [6 empty] | 0.0173 | 2003-04-22 | 6 | 0.016835 | 0.0173 | 2.735% |  | 0 | 0 | 0
E420 | 0.014297 | 02-Apr | 10 | 0.0147 | 2003-04-01 | 21 | 0.0141 | 2002-04-17 | 3 | 0.014607 | 04/02 | 18:00 |  |  |  | 0.0147 | 2003-04-02 | 18 | 0.0141 | 0.0147 | 4.143% |  | 0 | 0 | 0
E430 | 0.016231 | 02-Apr | 5 | 0.0156 | 2002-04-02 | 4 | 0.0156 | 2003-04-02 | 4 | 0.016146 | 04/02 | 05:00 |  |  |  | 0.0158 | 2003-04-02 | 5 | 0.0156 | 0.016231 | 3.972% |  | 0 | 0 | 0
E440 | 0.013313 | 16-Nov | 17 | 0.0138 | 2001-11-16 | 16 | 0.0137 | 2003-11-16 | 16 | 0.01352 | 11/16 | 17:00 |  |  |  | 0.0134 | 2003-11-16 | 16 | 0.013313 | 0.0138 | 3.596% |  | 0 | 0 | 0
E500 | 0.01172 | 11-Jul | 15 | 0.0119 | 2004-07-20 | 15 | 0.0118 | 2004-04-06 | 10 | 0.01138 | 07/20 | 15:00 | 0.011713 | 1900-07-20 | 15 | 0.0115 | 2003-03-11 | 10 | 0.01138 | 0.0119 | 4.459% |  | 0 | 0 | 0
E510 | 0.011871 | 07-Sep | 15 | 0.0119 | 2001-07-20 | 15 | 0.0119 | 2001-07-20 | 15 | 0.01139 | 07/20 | 15:00 | 0.011716 | 1900-07-20 | 15 | 0.0115 | 2003-03-11 | 10 | 0.01139 | 0.0119 | 4.356% |  | 0 | 0 | 0
E520 | 0.0075403 | 07-Sep | 15 | 0.0077 | 2004-07-10 | 16 | 0.0078 | 2004-03-29 | 10 | 0.007104 | 07/20 | 16:00 | 0.007566 | 1900-07-20 | 15 | 0.0106 | 2003-01-05 | 16 | 0.007104 | 0.0106 | 43.42% |  | 0 | 0 | 0
E522 | 0.0094264 | 20-Jul | 16 | 0.0095 | 2003-06-04 | 15 | 0.0138 | 2004-04-06 | 10 | 0.0089745 | 07/20 | 15:00 | 0.009398 | 1900-07-20 | 15 | 0.0107 | 2003-01-01 | 2 | 0.0089745 | 0.0138 | 46.85% |  | 0 | 0 | 0
E525 | 0.017932 | 10-Mai | 16 | 0.018 | 2004-07-20 | 15 | 0.018 | 2002-07-20 | 15 | 0.017848 | 07/20 | 15:00 | 0.017626 | 1900-07-20 | 15 | 0.0173 | 2003-07-20 | 15 | 0.0173 | 0.018 | 3.936% |  | 0 | 0 | 0
E530 | 0.0069892 | 01-Jan | 1 | 0.0081 | 2001-07-20 | 15 | 0.0081 | 2004-07-20 | 15 | 0.0067904 | 03/11 | 01:00 | 0.005491 | 1900-04-01 | 1 | 0.00677 | 2003-10-26 | 9 | 0.005491 | 0.0081 | 37.06% |  | 0 | 0 | 0
E540 | 0.006084 | 01-Jan | 1 | 0.005 | 2003-06-04 | 13 | 0.0063 | 2004-04-08 | 8 | 0.0067904 | 03/11 | 01:00 | 0.003256 | 1900-04-01 | 1 | 0.00634 | 2003-03-11 | 9 | 0.003256 | 0.0067904 | 62.8% |  | 0 | 0 | 0
E545 | 0.0069892 | 01-Jan | 1 | 0.0122 | 2004-07-20 | 15 | 0.0122 | 2004-07-20 | 15 | 0.0067904 | 12/31 | 17:00 | 0.006689 | 1900-04-01 | 1 | 0.00763 | 2003-11-05 | 9 | 0.006689 | 0.0122 | 62.98% |  | 0 | 0 | 0
Minimum Humidity Ratio | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.54% |  | 0 | 0 | 0
E310 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019435 | 01/05 | 07:00 | 0.002019 | 1900-01-04 | 7 | 0.00196 | 2003-01-05 | 7 | 0.0017 | 0.002019 | 17.09% |  | 0 | 0 | 0
E320 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019351 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.53% |  | 0 | 0 | 0
E330 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.54% |  | 0 | 0 | 0
E340 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.54% |  | 0 | 0 | 0
E350 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.54% |  | 0 | 0 | 0
E360 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 | 0.001968 | 1900-01-10 | 3 | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.54% |  | 0 | 0 | 0
E400 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.71% |  | 0 | 0 | 0
E410 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | [6 empty] | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.9% |  | 0 | 0 | 0
E420 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.71% |  | 0 | 0 | 0
E430 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 |  |  |  | 0.00197 | 2003-01-05 | 6 | 0.0017 | 0.00197 | 14.71% |  | 0 | 0 | 0
E440 | 0.0018769 | 11-Jan | 3 | 0.0017 | 2001-01-04 | 24 | 0.0017 | 2001-01-04 | 24 | 0.0019292 | 01/11 | 03:00 |  |  |  | 0.00197 | 2003-01-05 | 7 | 0.0017 | 0.00197 | 14.71% |  | 0 | 0 | 0
E500 | 0.0068276 | 20-Dec | 22 | [6 empty] | 0.0069608 | 12/20 | 12:00 | 0.006908 | 1900-12-20 | 20 | 0.0103 | 2003-11-02 | 2 | 0.0068276 | 0.0103 | 44.81% |  | 0 | 0 | 0
E510 | 0.0068276 | 20-Dec | 22 | [6 empty] | 0.0069608 | 12/20 | 12:00 | 0.006908 | 1900-12-20 | 20 | 0.0105 | 2003-04-02 | 22 | 0.0068276 | 0.0105 | 47.09% |  | 0 | 0 | 0
E520 | 0.006103 | 26-Nov | 2 | [6 empty] | 0.006466 | 11/10 | 07:00 | 0.006525 | 1900-11-27 | 23 | 0.00657 | 2003-11-01 | 7 | 0.006103 | 0.00657 | 7.279% |  | 0 | 0 | 0
E522 | 0.0068215 | 20-Dec | 22 | [6 empty] | 0.0069388 | 12/20 | 12:00 | 0.006908 | 1900-12-20 | 20 | 0.00783 | 2003-04-02 | 21 | 0.0068215 | 0.00783 | 14.16% |  | 0 | 0 | 0
E525 | 0.0068356 | 20-Dec | 22 | [6 empty] | 0.006998 | 12/20 | 12:00 | 0.006909 | 1900-12-20 | 20 | 0.0154 | 2003-11-02 | 2 | 0.0068356 | 0.0154 | 94.78% |  | 0 | 0 | 0
E530 | 0.006208 | 01-Apr | 1 | [6 empty] | 0.0064432 | 10/17 | 10:00 | 0.005454 | 1900-11-01 | 21 | 0.00663 | 2003-04-01 | 5 | 0.005454 | 0.00663 | 19.02% |  | 0 | 0 | 0
E540 | 0.0041096 | 05-Oct | 3 | [6 empty] | 0.0038106 | 10/17 | 10:00 | 0.003253 | 1900-04-29 | 23 | 0.0042 | 2003-10-15 | 5 | 0.003253 | 0.0042 | 24.64% |  | 0 | 0 | 0
E545 | 0.006208 | 01-Apr | 1 | [6 empty] | 0.0067904 | 04/01 | 01:00 | 0.006685 | 1900-07-20 | 15 | 0.007 | 2003-04-01 | 8 | 0.006208 | 0.007 | 11.87% |  | 0 | 0 | 0
Hourly Integrated Maxima and Minima (Relative Humidity)
Maximum Relative Humidity | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | NREL | Date | Hour | NREL | Date | Hour | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.7762 | 11/16 | 17:00 | 68 | 1900-11-16 | 16 | 67.44 | 2003-11-16 | 16 | 67.44 | 69.35 | 2.794% |  | 0 | 0 | 0
E310 | 77.7029 | 02-Oct | 4 | 100.18 | 2002-10-15 | 9 | 100.7 | 2002-10-15 | 9 | 77.9255 | 10/02 | 08:00 | 77 | 1900-06-12 | 8 | 78.19 | 2003-10-02 | 8 | 77 | 100.7 | 27.79% |  | 0 | 0 | 0
E320 | 81.8358 | 18-Sep | 10 | 83.41 | 2004-10-02 | 9 | 83.67 | 2003-04-22 | 18 | 82.7149 | 09/18 | 10:00 | 83 | 1900-09-03 | 17 | 81.88 | 2003-09-16 | 20 | 81.8358 | 83.67 | 2.217% |  | 0 | 0 | 0
E330 | 76.6591 | 22-Sep | 20 | 78.46 | 2004-10-02 | 9 | 77.94 | 2003-09-18 | 9 | 76.6386 | 09/22 | 20:00 | 76 | 1900-06-10 | 18 | 78.7 | 2003-09-02 | 12 | 76 | 78.7 | 3.488% |  | 0 | 0 | 0
E340 | 79.9293 | 18-Sep | 10 | 81.37 | 2004-09-18 | 9 | 81.26 | 2003-04-22 | 18 | 80.5452 | 09/18 | 10:00 | 80 | 1900-09-03 | 17 | 80.25 | 2003-09-16 | 20 | 79.9293 | 81.37 | 1.788% |  | 0 | 0 | 0
E350 | 68.7892 | 16-Nov | 17 | 81.12 | 2003-08-07 | 21 | 81.12 | 2003-08-07 | 21 | 67.7762 | 11/16 | 17:00 | 70 | 1900-10-02 | 8 | 72.65 | 2003-08-03 | 7 | 67.7762 | 81.12 | 18.14% |  | 0 | 0 | 0
E360 | 68.7892 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.776 | 11/16 | 17:00 | 68 | 1900-11-16 | 16 | 67.44 | 2003-11-16 | 16 | 67.44 | 69.35 | 2.794% |  | 0 | 0 | 0
E400 | 83.7534 | 05-Apr | 22 | 85.57 | 2002-04-05 | 21 | 85.57 | 2003-04-05 | 21 | 84.6321 | 04/05 | 22:00 |  |  |  | 86.31 | 2003-04-22 | 6 | 83.7534 | 86.31 | 3.002% |  | 0 | 0 | 0
E410 | 83.2247 | 05-Apr | 22 | 84.79 | 2002-04-02 | 5 | 84.79 | 2002-04-02 | 5 | [6 empty] | 86.18 | 2003-04-22 | 6 | 83.2247 | 86.18 | 3.487% |  | 0 | 0 | 0
E420 | 70.8411 | 02-Apr | 10 | 74.51 | 2003-04-17 | 7 | 71.53 | 2002-04-17 | 3 | 73.2771 | 04/02 | 18:00 |  |  |  | 73.85 | 2003-04-02 | 18 | 70.8411 | 74.51 | 5.04% |  | 0 | 0 | 0
E430 | 80.7087 | 02-Apr | 5 | 78.43 | 2002-04-02 | 4 | 78.43 | 2003-04-02 | 4 | 80.716 | 04/02 | 05:00 |  |  |  | 78.94 | 2003-04-02 | 5 | 78.43 | 80.716 | 2.877% |  | 0 | 0 | 0
E440 | 68.7242 | 16-Nov | 17 | 69.35 | 2002-11-16 | 16 | 68.85 | 2003-11-16 | 16 | 67.7762 | 11/16 | 17:00 |  |  |  | 67.51 | 2003-11-16 | 16 | 67.51 | 69.35 | 2.688% |  | 0 | 0 | 0
E500 | 100 | 21-Nov | 24 | [6 empty] | 100 | 11/21 | 24:00 | 100 | 1900-11-14 | 5 | 60.08 | 2003-04-01 | 5 | 60.08 | 100 | 44.35% |  | 0 | 0 | 0
E510 | 100 | 21-Nov | 24 | [6 empty] | 100 | 11/21 | 24:00 | 100 | 1900-11-14 | 5 | 57.51 | 2003-04-01 | 5 | 57.51 | 100 | 47.54% |  | 0 | 0 | 0
E520 | 90.2299 | 20-Dec | 22 | [6 empty] | 93.6042 | 12/20 | 11:00 | 95 | 1900-12-20 | 17 | 71.77 | 2003-08-16 | 17 | 71.77 | 95 | 26.5% |  | 0 | 0 | 0
E522 | 100 | 18-Dec | 8 | [6 empty] | 100 | 12/16 | 03:00 | 100 | 1900-12-15 | 1 | 71.32 | 2003-04-05 | 17 | 71.32 | 100 | 30.9% |  | 0 | 0 | 0
E525 | 100 | 12-Nov | 20 | [6 empty] | 100 | 11/12 | 24:00 | 100 | 1900-11-11 | 23 | 51.12 | 2003-04-01 | 8 | 51.12 | 100 | 55.68% |  | 0 | 0 | 0
E530 | 91.0445 | 20-Dec | 22 | [6 empty] | 91.698 | 12/20 | 11:00 | 79 | 1900-12-20 | 8 | 36.01 | 2003-04-20 | 21 | 36.01 | 91.698 | 74.81% |  | 0 | 0 | 0
E540 | 61.275 | 20-Dec | 22 | [6 empty] | 54.8557 | 12/20 | 11:00 | 47 | 1900-12-20 | 6 | 39.96 | 2003-04-18 | 18 | 39.96 | 61.275 | 41.98% |  | 0 | 0 | 0
E545 | 90.8772 | 20-Dec | 22 | [6 empty] | 96.074 | 12/20 | 11:00 | 97 | 1900-12-20 | 4 | 24.14 | 2003-12-24 | 1 | 24.14 | 97 | 94.6% |  | 0 | 0 | 0
Minimum Relative Humidity | HOT3000 Min: Statistics, All Results
| TRNSYS |  |  | DOE-2.2 |  |  | DOE21E-E |  |  | Energy+ |  |  | CODYRUN |  |  | HOT3000 |  |  |  |  | (Max-Min)
| TUD | Date | Hour | [6 empty] | GARD | Date | Hour | UR | Date | Hour | NRCan | Date | Hour | Min | Max | /Mean |  | Your Software | Date | Hour
E300 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 22.28% |  | 0 | 0 | 0
E310 | 13.3898 | 06-Nov | 6 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 15.471 | 11/06 | 08:00 | 16 | 1900-11-06 | 8 | 15.93 | 2003-11-06 | 8 | 11.97 | 16 | 28.54% |  | 0 | 0 | 0
E320 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.7974 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 12.92 | 2003-12-20 | 5 | 11.97 | 15 | 22.73% |  | 0 | 0 | 0
E330 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3879 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 22.28% |  | 0 | 0 | 0
E340 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3879 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 22.28% |  | 0 | 0 | 0
E350 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 22.28% |  | 0 | 0 | 0
E360 | 13.3312 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 14.3878 | 11/06 | 06:00 | 15 | 1900-11-06 | 5 | 14.94 | 2003-11-06 | 8 | 11.97 | 15 | 22.28% |  | 0 | 0 | 0
E400 | 13.209 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 |  |  |  | 14.57 | 2003-11-06 | 5 | 11.97 | 14.57 | 19.8% |  | 0 | 0 | 0
E410 | 13.2091 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | HOT3000 NRCan: 14.58; HOT3000 Date: 2003-11-06; HOT3000 Hour: 5; HOT3000 Min: 11.97; HOT3000 Max: 14.58; (Max-Min) /Mean: 20.18% |  | 0 | 0 | 0
E420 | 13.2099 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9256 | 11/06 | 06:00 |  |  |  | 14.59 | 2003-11-06 | 5 | 11.97 | 14.59 | 19.95% |  | 0 | 0 | 0
E430 | 13.2078 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 |  |  |  | 14.58 | 2003-11-06 | 5 | 11.97 | 14.58 | 19.88% |  | 0 | 0 | 0
E440 | 13.2069 | 06-Nov | 5 | 11.97 | 2002-11-06 | 4 | 11.97 | 2002-11-06 | 4 | 13.9255 | 11/06 | 06:00 |  |  |  | 14.54 | 2003-11-06 | 5 | 11.97 | 14.54 | 19.58% |  | 0 | 0 | 0
E500 | 53.4054 | 30-Apr | 15 | [6 empty] | 53.4256 | 04/30 | 04:00 | 54 | 1900-10-04 | 24 | 52.83 | 2003-10-05 | 1 | 52.83 | 54 | 2.19% |  | 0 | 0 | 0
E510 | 52.0879 | 04-Oct | 23 | [6 empty] | 53.5323 | 05/04 | 04:00 | 54 | 1900-10-04 | 23 | 53.15 | 2003-05-04 | 4 | 52.0879 | 54 | 3.595% |  | 0 | 0 | 0
E520 | 61.2679 | 25-Nov | 24 | [6 empty] | 61.1938 | 11/10 | 04:00 | 61 | 1900-11-27 | 22 | 61.9 | 2003-07-20 | 15 | 61 | 61.9 | 1.467% |  | 0 | 0 | 0
E522 | 58.5054 | 30-Apr | 15 | [6 empty] | 57.8308 | 04/30 | 04:00 | 60 | 1900-10-04 | 23 | 57.97 | 2003-10-05 | 1 | 57.8308 | 60 | 3.703% |  | 0 | 0 | 0
E525 | 45.5284 | 30-Apr | 15 | [6 empty] | 46.1063 | 10/05 | 02:00 | 44 | 1900-05-04 | 4 | 44.4 | 2003-10-05 | 1 | 44 | 46.1063 | 4.68% |  | 0 | 0 | 0
E530 | 29.5934 | 04-Jun | 15 | [6 empty] | 32.5613 | 04/18 | 18:00 | 28 | 1900-04-01 | 10 | 33.68 | 2003-04-01 | 13 | 28 | 33.68 | 18.35% |  | 0 | 0 | 0
E540 | 36.4749 | 21-Sep | 16 | [6 empty] | 35.8475 | 09/28 | 18:00 | 31 | 1900-04-01 | 1 | 39.74 | 2003-10-05 | 1 | 31 | 39.74 | 24.44% |  | 0 | 0 | 0
E545 | 17.1244 | 20-Jul | 15 | [6 empty] | 19.2467 | 04/18 | 17:00 | 19 | 1900-04-01 | 10 | 20.14 | 2003-04-01 | 12 | 17.1244 | 20.14 | 15.97% |  | 0 | 0 | 0
e300results.xls r:a215..aa308; 07/19/04

## S
e300results.XLS, Jul, 2004 | [5 empty] | SEE SHEET 'A' FOR INSTRUCTIONS
J u n e 2 8 H o u r l y O u t p u t - C a s e E 3 0 0
TRNSYS-TUD | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 2055.7697 | 256.5326 | 8131.73 | 6189.34 | 1942.39 | 0.0090778 | 3.5167 | 18.05 | 23.4068 | 16.9641 | 0.011255
2 | 2053.6706 | 256.5271 | 8115.8 | 6201.56 | 1914.24 | 0.0090138 | 3.513 | 18.05 | 23.3748 | 16.9046 | 0.011255
3 | 2054.4923 | 256.5356 | 8127.89 | 6194.38 | 1933.51 | 0.0090644 | 3.517 | 18.05 | 23.3833 | 16.9418 | 0.011255
4 | 1830.0824 | 229.5857 | 7224.15 | 5548.55 | 1675.6 | 0.0089864 | 3.5074 | 17.8 | 23.3739 | 16.8619 | 0.011075
5 | 2029.3426 | 256.394 | 8104.85 | 6318.9 | 1785.95 | 0.0088405 | 3.5458 | 17.5 | 23.3503 | 16.6966 | 0.01061
6 | 1839.4317 | 229.5597 | 7130.87 | 5686.24 | 1444.63 | 0.0086578 | 3.4465 | 18.3 | 23.4171 | 16.5734 | 0.010568
7 | 2667.2444 | 308.5446 | 9711.38 | 7596.88 | 2114.5 | 0.0091531 | 3.2635 | 22.2 | 24.0395 | 17.3192 | 0.012071
8 | 3552.7185 | 384.0455 | 12121.31 | 9558.23 | 2563.08 | 0.0095303 | 3.079 | 26.1 | 24.5724 | 17.7945 | 0.012173
9 | 4364.7758 | 458.1014 | 14555.62 | 11757.9 | 2797.72 | 0.0096727 | 3.018 | 28.05 | 25.0937 | 17.973 | 0.011538
10 | 4441.0633 | 457.9932 | 14639.38 | 11506.4 | 3132.98 | 0.010058 | 2.9882 | 28.9 | 25.2815 | 18.3972 | 0.012388
11 | 4999.595 | 506.3045 | 16374.09 | 12342.2 | 4031.89 | 0.010408 | 2.9739 | 30 | 25.3592 | 18.8246 | 0.013776
12 | 5316.7711 | 529.3648 | 17248.4 | 12810 | 4438.4 | 0.010684 | 2.9504 | 30.85 | 25.5877 | 19.1202 | 0.014041
13 | 6188.5477 | 616.6094 | 20498.21 | 16816.1 | 3682.11 | 0.010087 | 3.0122 | 30.85 | 26.53 | 18.8377 | 0.012315
14 | 6210.9293 | 616.1242 | 20234.06 | 17283.5 | 2950.56 | 0.0097987 | 2.9638 | 31.4 | 26.5617 | 18.5548 | 0.011543
15 | 7922.4534 | 781.0016 | 26687.28 | 22882.4 | 3804.88 | 0.0095792 | 3.0663 | 31.95 | 26.7812 | 18.5486 | 0.012069
16 | 7964.823 | 781.0124 | 26722.68 | 22284.7 | 4437.98 | 0.0096663 | 3.0555 | 32.2 | 26.5632 | 18.673 | 0.013324
17 | 5420.7775 | 529.4985 | 17231.33 | 13048.3 | 4183.03 | 0.01077 | 2.8959 | 31.95 | 26.198 | 19.4032 | 0.014505
18 | 5409.9868 | 529.3784 | 17505.88 | 12720.6 | 4785.28 | 0.011184 | 2.9474 | 31.4 | 26.2263 | 19.7724 | 0.015234
19 | 5260.0345 | 529.2289 | 17661.69 | 12490.8 | 5170.89 | 0.011131 | 3.0508 | 29.7 | 25.7001 | 19.5753 | 0.015134
20 | 4880.3429 | 506.2207 | 16989.81 | 11655.3 | 5334.51 | 0.010991 | 3.1541 | 27.75 | 25.1673 | 19.3718 | 0.015748
21 | 3938.7143 | 409.0843 | 13539.94 | 8882.19 | 4657.75 | 0.01114 | 3.1142 | 27.2 | 24.6544 | 19.438 | 0.016886
22 | 3923.9563 | 409.5326 | 13564.54 | 8880.28 | 4684.26 | 0.011177 | 3.1302 | 26.95 | 24.7445 | 19.4846 | 0.016863
23 | 4122.5716 | 433.8551 | 14531.34 | 9449.35 | 5081.99 | 0.011176 | 3.1892 | 26.4 | 24.6707 | 19.4693 | 0.016867
24 | 3877.3845 | 409.5808 | 13691.76 | 8806.54 | 4885.22 | 0.011275 | 3.1938 | 26.1 | 24.7257 | 19.5725 | 0.017112
DOE-2.2 | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 1897 | 237 | 7552.3077 | 5889.2583 | 1663.0494 | 0.0094 | 3.539 | 17.7778 | 23.8333 | 17.34 | 0.0114
2 | 1941 | 240 | 7630.2723 | 6069.8079 | 1560.4644 | 0.0093 | 3.4985 | 18.3333 | 23.9444 | 17.29 | 0.0112
3 | 1897 | 237 | 7550.256 | 5881.3446 | 1668.9114 | 0.0094 | 3.5381 | 17.7778 | 23.8333 | 17.34 | 0.0114
4 | 1891 | 237 | 7533.8424 | 5878.1205 | 1655.7219 | 0.0094 | 3.5403 | 17.7778 | 23.8333 | 17.34 | 0.0114
5 | 1697 | 215 | 6797.8683 | 5675.2953 | 1122.573 | 0.0089 | 3.5554 | 17.2222 | 23.7778 | 16.85 | 0.0103
6 | 2126 | 259 | 8136.1629 | 6438.5277 | 1697.6352 | 0.0092 | 3.4114 | 19.4444 | 24.1111 | 17.3 | 0.0113
7 | 3198 | 352 | 11075.9559 | 8342.2122 | 2733.7437 | 0.01 | 3.12 | 25 | 24.9444 | 18.39 | 0.0133
8 | 3135 | 332 | 10290.741 | 9069.9795 | 1220.7615 | 0.0094 | 2.9682 | 27.2222 | 25.2778 | 17.78 | 0.0109
9 | 4528 | 469 | 14785.7226 | 11872.6017 | 2913.1209 | 0.0099 | 2.9589 | 28.8889 | 25.5556 | 18.36 | 0.0117
10 | 4651 | 479 | 15339.9747 | 12039.0825 | 3300.8922 | 0.0103 | 2.9902 | 28.8889 | 25.5556 | 18.68 | 0.0125
11 | 5434 | 537 | 17455.2774 | 12811.9872 | 4643.2902 | 0.0109 | 2.9233 | 31.1111 | 25.8889 | 19.48 | 0.0148
12 | 5019 | 498 | 16215.1713 | 12612.093 | 3603.0783 | 0.0108 | 2.9391 | 30.5556 | 25.8333 | 19.23 | 0.0134
13 | 6040 | 597 | 19722.9921 | 17139.0225 | 2583.9696 | 0.0101 | 2.9717 | 31.1111 | 25.9444 | 18.56 | 0.0115
14 | 6420 | 633 | 20808.3414 | 17638.1718 | 3170.1696 | 0.01 | 2.9503 | 31.6667 | 26.0556 | 18.6 | 0.0121
15 | 7671 | 751 | 25387.1496 | 22196.463 | 3190.6866 | 0.0098 | 3.0144 | 32.2222 | 26.1111 | 18.46 | 0.0119
16 | 8190 | 800 | 27581.0031 | 22527.9591 | 5053.044 | 0.01 | 3.068 | 32.2222 | 26.1667 | 18.84 | 0.0144
17 | 5715 | 561 | 18204.7341 | 13599.2538 | 4605.4803 | 0.0107 | 2.9007 | 31.6667 | 26.0556 | 19.35 | 0.0146
18 | 5536 | 544 | 17933.3235 | 12829.8663 | 5103.4572 | 0.0112 | 2.9496 | 31.1111 | 25.9444 | 19.75 | 0.0157
19 | 4711 | 481 | 16012.053 | 11875.5327 | 4136.5203 | 0.011 | 3.084 | 28.3333 | 25.5 | 19.32 | 0.0143
20 | 4859 | 504 | 17082.1611 | 11532.3126 | 5549.8485 | 0.0114 | 3.1852 | 27.2222 | 25.3333 | 19.76 | 0.0164
21 | 3913 | 405 | 13435.4109 | 9302.4078 | 4133.0031 | 0.0113 | 3.1115 | 27.2222 | 25.3333 | 19.76 | 0.0164
22 | 3825 | 399 | 13280.361 | 8973.5496 | 4306.8114 | 0.0114 | 3.144 | 26.6667 | 25.2222 | 19.8 | 0.0167
23 | 3750 | 395 | 13191.8448 | 8787.4311 | 4404.4137 | 0.0115 | 3.1826 | 26.1111 | 25.1111 | 19.84 | 0.0169
24 | 3880 | 407 | 13724.4075 | 8799.1551 | 4925.2524 | 0.0117 | 3.2014 | 26.1111 | 25.1111 | 20.14 | 0.0178
e300results.xls s:a03..n62; 07/19/04
J u n e 2 8 H o u r l y O u t p u t (Ctd.) - C a s e E 3 0 0
DOE-2.1E-E | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 1894 | 237 | 7544.9802 | 5886.9135 | 1658.0667 | 0.0094 | 3.5406 | 17.7778 | 23.8333 | 17.34 | 0.0114
2 | 1941 | 241 | 7627.0482 | 6067.17 | 1559.8782 | 0.0093 | 3.4954 | 18.3333 | 23.9444 | 17.29 | 0.0112
3 | 1894 | 237 | 7546.1526 | 5878.1205 | 1668.0321 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114
4 | 1890 | 236 | 7528.2735 | 5873.4309 | 1654.8426 | 0.0094 | 3.5411 | 17.7778 | 23.8333 | 17.37 | 0.0114
5 | 1694 | 215 | 6753.024 | 5671.7781 | 1081.2459 | 0.009 | 3.5375 | 17.2222 | 23.7778 | 16.94 | 0.0103
6 | 2133 | 259 | 8185.1106 | 6438.5277 | 1746.5829 | 0.0092 | 3.4219 | 19.4444 | 24.1111 | 17.3 | 0.0113
7 | 3223 | 353 | 11232.7644 | 8347.7811 | 2884.9833 | 0.0098 | 3.1412 | 25 | 24.9444 | 18.23 | 0.0133
8 | 3145 | 335 | 10271.6895 | 9069.1002 | 1202.5893 | 0.0094 | 2.9516 | 27.2222 | 25.2778 | 17.78 | 0.0109
9 | 4526 | 467 | 14844.0495 | 11875.2396 | 2968.8099 | 0.0099 | 2.973 | 28.8889 | 25.5556 | 18.28 | 0.0117
10 | 4655 | 478 | 15392.7327 | 12041.1342 | 3351.5985 | 0.0102 | 2.9988 | 28.8889 | 25.5556 | 18.6 | 0.0125
11 | 5456 | 536 | 17605.0515 | 12817.5561 | 4787.4954 | 0.0107 | 2.9381 | 31.1111 | 25.8889 | 19.33 | 0.0148
12 | 5015 | 498 | 16187.6199 | 12610.9206 | 3576.6993 | 0.0108 | 2.9363 | 30.5556 | 25.8333 | 19.23 | 0.0134
13 | 6036 | 600 | 19620.9933 | 17135.2122 | 2485.7811 | 0.0102 | 2.9568 | 31.1111 | 25.9444 | 18.64 | 0.0115
14 | 6429 | 635 | 20819.1861 | 17639.0511 | 3180.135 | 0.01 | 2.9472 | 31.6667 | 26.0556 | 18.6 | 0.0121
15 | 7683 | 754 | 25392.7185 | 22196.7561 | 3195.9624 | 0.0098 | 3.0097 | 32.2222 | 26.1111 | 18.46 | 0.0119
16 | 8222 | 803 | 27721.1049 | 22533.2349 | 5187.87 | 0.0098 | 3.0716 | 32.2222 | 26.1667 | 18.76 | 0.0144
17 | 5696 | 556 | 18244.5957 | 13600.1331 | 4644.4626 | 0.0107 | 2.9182 | 31.6667 | 26.0556 | 19.35 | 0.0146
18 | 5531 | 541 | 17977.8747 | 12831.6249 | 5146.2498 | 0.0112 | 2.9608 | 31.1111 | 25.9444 | 19.68 | 0.0157
19 | 4689 | 479 | 15914.4507 | 11871.1362 | 4043.3145 | 0.0111 | 3.0794 | 28.3333 | 25.5 | 19.4 | 0.0143
20 | 4855 | 503 | 17120.2641 | 11534.0712 | 5586.1929 | 0.0113 | 3.1953 | 27.2222 | 25.3333 | 19.76 | 0.0164
21 | 3918 | 406 | 13445.0832 | 9302.7009 | 4142.3823 | 0.0113 | 3.1094 | 27.2222 | 25.3333 | 19.76 | 0.0164
22 | 3823 | 399 | 13285.0506 | 8973.8427 | 4311.2079 | 0.0114 | 3.1466 | 26.6667 | 25.2222 | 19.8 | 0.0167
23 | 3748 | 394 | 13192.1379 | 8787.4311 | 4404.7068 | 0.0115 | 3.185 | 26.1111 | 25.1111 | 19.84 | 0.0169
24 | 3880 | 407 | 13754.3037 | 8799.7413 | 4954.5624 | 0.0117 | 3.2084 | 26.1111 | 25.1111 | 20.06 | 0.0178
EnergyPlus | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 2153.3475 | Note 1 | 7602.8745 | 5807.8573 | 1795.0172 | 0.0092568 | 3.5307 | 17.9875 | 23.945 | 0 | 0.011202
2 | 2166.9933 | Note 1 | 7628.0999 | 5850.1562 | 1777.9436 | 0.0092201 | 3.5201 | 18.1125 | 23.9636 | 0 | 0.011296
3 | 2147.8736 | Note 1 | 7579.4624 | 5806.3857 | 1773.0767 | 0.0092267 | 3.5288 | 17.9875 | 23.9451 | 0 | 0.011199
4 | 2109.7575 | Note 1 | 7463.8071 | 5740.6566 | 1723.1504 | 0.0091699 | 3.5378 | 17.8 | 23.9169 | 0 | 0.011061
5 | 2031.5836 | Note 1 | 7218.877 | 5611.5024 | 1607.3746 | 0.009048 | 3.5533 | 17.425 | 23.8612 | 0 | 0.010484
6 | 2181.6446 | Note 1 | 7563.2201 | 6012.3325 | 1550.8876 | 0.0089018 | 3.4668 | 18.575 | 24.0335 | 0 | 0.010648
7 | 2926.8472 | Note 1 | 9393.041 | 7528.0125 | 1865.0285 | 0.0091706 | 3.2093 | 22.9 | 24.6841 | 0 | 0.012288
8 | 3571.6614 | Note 1 | 10820.4962 | 8751.3077 | 2069.1885 | 0.0094818 | 3.0295 | 26.375 | 25.208 | 0 | 0.011849
9 | 4771.5975 | Note 1 | 14280.6923 | 11758.2673 | 2522.4251 | 0.0096209 | 2.9929 | 28.2625 | 25.4906 | 0 | 0.01158
10 | 5029.2702 | Note 1 | 15005.1999 | 11985.6398 | 3019.5601 | 0.0099775 | 2.9836 | 28.9 | 25.5865 | 0 | 0.012406
11 | 5485.3257 | Note 1 | 16127.9094 | 12473.8609 | 3654.0485 | 0.010392 | 2.9402 | 30.275 | 25.7953 | 0 | 0.013949
12 | 5708.5515 | Note 1 | 16742.4591 | 12655.4944 | 4086.9647 | 0.010701 | 2.9329 | 30.7875 | 25.8718 | 0 | 0.013761
13 | 7233.0374 | Note 1 | 21873.9592 | 17378.5032 | 4495.456 | 0.010129 | 3.0242 | 30.9125 | 25.8849 | 0 | 0.011999
14 | 7085.957 | Note 1 | 20933.4385 | 17574.6097 | 3358.8288 | 0.009694 | 2.9542 | 31.475 | 25.9689 | 0 | 0.011528
15 | 8689.9561 | Note 1 | 26432.9109 | 22454.4561 | 3978.4548 | 0.009521 | 3.0418 | 32.0125 | 26.0513 | 0 | 0.012086
16 | 8842.8175 | Note 1 | 26943.3568 | 22527.6692 | 4415.6877 | 0.0096238 | 3.0469 | 32.2 | 26.0827 | 0 | 0.013492
17 | 5791.0239 | Note 1 | 16525.7603 | 13046.9672 | 3478.7931 | 0.010361 | 2.8537 | 31.8875 | 26.0396 | 0 | 0.014504
18 | 5952.6309 | Note 1 | 17405.5618 | 12851.4495 | 4554.1122 | 0.010924 | 2.924 | 31.325 | 25.9556 | 0 | 0.015288
19 | 5617.7336 | Note 1 | 17082.2323 | 12151.7364 | 4930.496 | 0.011075 | 3.0408 | 29.35 | 25.6558 | 0 | 0.01493
20 | 5315.9924 | Note 1 | 16742.9941 | 11537.4992 | 5205.4948 | 0.011126 | 3.1496 | 27.6125 | 25.3934 | 0 | 0.01597
21 | 4369.5515 | Note 1 | 13611.4239 | 9049.8699 | 4561.554 | 0.011355 | 3.1151 | 27.2 | 25.333 | 0 | 0.01681
22 | 4323.8097 | Note 1 | 13561.3024 | 8939.7425 | 4621.5598 | 0.011403 | 3.1364 | 26.8875 | 25.2865 | 0 | 0.016771
23 | 4215.998 | Note 1 | 13364.985 | 8740.9679 | 4624.0171 | 0.01142 | 3.1701 | 26.325 | 25.2013 | 0 | 0.016784
24 | 4194.2432 | Note 1 | 13370.4665 | 8661.2371 | 4709.2294 | 0.011476 | 3.1878 | 26.1 | 25.1674 | 0 | 0.017077
e300results.xls s:a66..n125; 07/19/04
J u n e 2 8 H o u r l y O u t p u t (Ctd.) - C a s e E 3 0 0
CODYRUN | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 1886 | 237 | 7472 | 5788 | 1684 | 0.009276 | 3.5195 | 17.8 | 23.92 | 17.155 | 0.0111
2 | 1964 | 244 | 7707 | 5961 | 1747 | 0.009302 | 3.4905 | 18.3 | 24 | 17.238 | 0.011462
3 | 1881 | 236 | 7445 | 5788 | 1657 | 0.009239 | 3.5168 | 17.8 | 23.92 | 17.12 | 0.0111
4 | 1878 | 236 | 7432 | 5788 | 1644 | 0.009201 | 3.5156 | 17.8 | 23.92 | 17.102 | 0.0111
5 | 1756 | 224 | 7000 | 5580 | 1420 | 0.008969 | 3.5354 | 17.2 | 23.83 | 16.787 | 0.01018
6 | 2075 | 253 | 7915 | 6341 | 1574 | 0.009012 | 3.3999 | 19.4 | 24.16 | 17.032 | 0.011001
7 | 3035 | 334 | 10450 | 8277 | 2173 | 0.00949 | 3.1018 | 25 | 25 | 17.911 | 0.01314
8 | 3303 | 352 | 10813 | 9038 | 1775 | 0.009314 | 2.9584 | 27.2 | 25.33 | 17.646 | 0.011075
9 | 4483 | 463 | 14631 | 11971 | 2660 | 0.009708 | 2.9581 | 28.9 | 25.59 | 18.118 | 0.011995
10 | 4594 | 472 | 15099 | 11971 | 3128 | 0.010041 | 2.9805 | 28.9 | 25.59 | 18.442 | 0.01276
11 | 5238 | 516 | 16722 | 12731 | 3991 | 0.010588 | 2.9062 | 31.1 | 25.91 | 19.142 | 0.014809
12 | 5066 | 504 | 16258 | 12559 | 3699 | 0.01058 | 2.9189 | 30.6 | 25.84 | 18.935 | 0.013253
13 | 6442 | 642 | 21090 | 17422 | 3669 | 0.009975 | 2.9771 | 31.1 | 25.91 | 18.326 | 0.011329
14 | 6523 | 645 | 21067 | 17629 | 3438 | 0.009778 | 2.939 | 31.7 | 26 | 18.269 | 0.011729
15 | 8000 | 785 | 26636 | 22491 | 4145 | 0.009579 | 3.032 | 32.2 | 26.08 | 18.239 | 0.012379
16 | 8169 | 799 | 27416 | 22491 | 4925 | 0.009733 | 3.0571 | 32.2 | 26.08 | 18.557 | 0.014232
17 | 5306 | 519 | 16702 | 12939 | 3763 | 0.01044 | 2.8673 | 31.7 | 26 | 19.063 | 0.01473
18 | 5381 | 528 | 17312 | 12729 | 4582 | 0.010912 | 2.9298 | 31.1 | 25.91 | 19.458 | 0.015684
19 | 4791 | 492 | 16232 | 11761 | 4470 | 0.010914 | 3.0725 | 28.3 | 25.5 | 19.199 | 0.014539
20 | 4809 | 498 | 16867 | 11381 | 5486 | 0.011269 | 3.1783 | 27.2 | 25.33 | 19.65 | 0.016878
21 | 3939 | 408 | 13484 | 9036 | 4447 | 0.011348 | 3.1019 | 27.2 | 25.33 | 19.706 | 0.016878
22 | 3852 | 402 | 13322 | 8864 | 4459 | 0.011383 | 3.1316 | 26.7 | 25.25 | 19.697 | 0.016832
23 | 3752 | 395 | 13139 | 8656 | 4482 | 0.011416 | 3.1683 | 26.1 | 25.16 | 19.694 | 0.016889
24 | 3794 | 399 | 13323 | 8656 | 4666 | 0.011507 | 3.1774 | 26.1 | 25.16 | 19.805 | 0.017329
HOT3000 | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 1942.81 | 240.938 | 7667.56 | 5870.06 | 1797.5 | 0.0092502 | 3.5112 | 17.8 | 23.9367 | 17.3042 | 0.011072
2 | 1950.53 | 241.104 | 7674.46 | 5871.7 | 1802.77 | 0.0092582 | 3.5017 | 18.3 | 23.9367 | 17.31 | 0.011432
3 | 1902.33 | 236.85 | 7527.94 | 5782.88 | 1745.07 | 0.0092068 | 3.5191 | 17.8 | 23.8958 | 17.2367 | 0.011072
4 | 1845.43 | 231.118 | 7317.22 | 5683.06 | 1634.17 | 0.0091047 | 3.5238 | 17.8 | 23.8375 | 17.0785 | 0.011072
5 | 1914.46 | 238.687 | 7514.35 | 5955.01 | 1559.34 | 0.0089519 | 3.4899 | 17.2 | 23.9757 | 17.0075 | 0.010155
6 | 2506.57 | 292.588 | 9222.93 | 7311.79 | 1911.15 | 0.0091583 | 3.2949 | 19.4 | 24.5756 | 17.5412 | 0.01097
7 | 3170.95 | 342.969 | 10769.5 | 8646.87 | 2122.59 | 0.0094778 | 3.0648 | 25 | 25.1643 | 17.9926 | 0.013099
8 | 3433.96 | 360.598 | 11186.4 | 9298.63 | 1887.81 | 0.0093737 | 2.948 | 27.2 | 25.4533 | 17.9591 | 0.011039
9 | 4489.15 | 460.788 | 14744.4 | 11923.2 | 2821.19 | 0.0097161 | 2.9787 | 28.9 | 25.5785 | 18.3251 | 0.011957
10 | 4853.28 | 489.455 | 15882.1 | 12287.1 | 3595.03 | 0.010237 | 2.9726 | 28.9 | 25.7393 | 18.8543 | 0.012719
11 | 5164.22 | 508.218 | 16614.5 | 12561.8 | 4052.76 | 0.010622 | 2.929 | 31.1 | 25.8631 | 19.1876 | 0.014761
12 | 5004.96 | 496.504 | 16029.6 | 12561.3 | 3468.23 | 0.010433 | 2.9137 | 30.6 | 25.8628 | 18.8671 | 0.013211
13 | 6454.59 | 639.274 | 21179.7 | 17430.7 | 3749.01 | 0.0099715 | 2.9856 | 31.1 | 25.9424 | 18.518 | 0.011293
14 | 6503.4 | 639.953 | 21055.4 | 17608.6 | 3446.79 | 0.0097436 | 2.9476 | 31.7 | 26.022 | 18.4421 | 0.011692
15 | 8040.55 | 784.905 | 27069.8 | 22350.4 | 4719.45 | 0.0097834 | 3.0672 | 32.2 | 26.1296 | 18.6471 | 0.01234
16 | 8133.59 | 793.61 | 27623.3 | 22292 | 5331.25 | 0.0098255 | 3.0943 | 32.2 | 26.0323 | 18.7965 | 0.014188
17 | 5211.79 | 509.581 | 16551 | 12739.1 | 3811.95 | 0.010257 | 2.8928 | 31.7 | 25.943 | 19.1104 | 0.014684
18 | 5122.29 | 506.956 | 16829.6 | 12180.9 | 4648.77 | 0.010859 | 2.9897 | 31.1 | 25.6955 | 19.3936 | 0.015634
19 | 4831.72 | 492.97 | 16635.3 | 11540.7 | 5094.59 | 0.011024 | 3.1242 | 28.3 | 25.4093 | 19.5323 | 0.014493
20 | 4874.85 | 501.239 | 17131.1 | 11359.2 | 5771.92 | 0.011357 | 3.1865 | 27.2 | 25.3281 | 19.7431 | 0.016824
21 | 3935.62 | 405.543 | 13524.8 | 8931.39 | 4593.42 | 0.011378 | 3.1155 | 27.2 | 25.291 | 19.7437 | 0.016824
22 | 3844.33 | 398.939 | 13355.8 | 8747.22 | 4608.6 | 0.011398 | 3.1475 | 26.7 | 25.2092 | 19.7887 | 0.016777
23 | 3807.46 | 397.275 | 13343.3 | 8646.75 | 4696.56 | 0.01145 | 3.1734 | 26.1 | 25.1645 | 19.8355 | 0.016835
24 | 3664.17 | 385.64 | 12972.7 | 8359.6 | 4613.06 | 0.011462 | 3.2033 | 26.1 | 25.0374 | 19.7678 | 0.017273
e300results.xls s:a130..n189; 08/11/03
Your Software
CODY-evap | Energy Consumption |  | Evaporator Coil Load |  |  | Zone Hum.
| Compressor | Cond Fan | Total | Sensible | Latent | Ratio | COP2 | ODB | EDB | EWB | OHR
Hour | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (kg/kg) |  | (°C) | (°C) | (°C) | (kg/kg)
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## T
e300results.XLS, Jul, 2004 | [5 empty] | SEE SHEET 'A' FOR INSTRUCTIONS
Delta Annual Space Cooling Electricity Consumptions
Total (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 4339.6026 | 4629 | 4629 | 4410.4348 | 4543.158 | 4538 | 4339.6026 | 4629 | 6.41% |  | 0
E320-E300 | 4425.8798 | 3995 | 4037 | 4351.305 | 4424.404 | 4387 | 3995 | 4425.8798 | 10.09% |  | 0
E330-E300 | 5329.5231 | 4958 | 4683 | 5445.065 | 5558.726 | 5260 | 4683 | 5558.726 | 16.82% |  | 0
E330-E320 | 903.6433 | 963 | 646 | 1093.76 | 1134.322 | 873 | 646 | 1134.322 | 52.19% |  | 0
E340-E300 | 4985.5179 | 4608 | 4510 | 5047.6908 | 5088.85 | 4877 | 4510 | 5088.85 | 11.93% |  | 0
E330-E340 | 344.0053 | 350 | 173 | 397.3742 | 469.876 | 383 | 173 | 469.876 | 84.13% |  | 0
E350-E300 | -3396.7978 | -4203 | -4207 | -3647.5233 | -3389.819 | -3328 | -4207 | -3328 | -23.79% |  | 0
E360-E300 | 19665.0145 | 19314 | 19261 | 19920.5204 | 19866.847 | 19998 | 19261 | 19998 | 3.747% |  | 0
E400-E300 | -3588.6237 | -3904 | -3879 | -3758.0865 |  | -3657 | -3904 | -3588.6237 | -8.394% |  | 0
E410-E300 | -3555.3454 | -3082 | -3056 | -3013.2237 |  | -3567 | -3567 | -3013.2237 | -17.01% |  | 0
E420-E300 | -2246.7696 | -2220 | -1845 | -2045.1846 |  | -1862 | -2246.7696 | -1845 | -19.66% |  | 0
E430-E300 | -3095.7459 | -2818 | -2944 | -2938.2118 |  | -3252 | -3252 | -2818 | -14.42% |  | 0
E440-E300 | -1942.4562 | -1718 | -1782 | -1738.9033 |  | -1822 | -1942.4562 | -1718 | -12.47% |  | 0
E500-E300 | -13295.8902 | -11933 | -11933 | -11947.9102 | -12653.458 | -11932 | -13295.8902 | -11932 | -11.1% |  | 0
E510-E500 | 17217.9243 | 18099 | 18100 | 17760.3056 | 17414.1 | 17794 | 17217.9243 | 18100 | 4.975% |  | 0
E525-E520 | -4665.708 | -4981 | -4969 | -5031.5465 | -4889.357 | -4458 | -5031.5465 | -4458 | -11.87% |  | 0
E530-E500 | -5056.616 | -5277 | -5285 | -5081.8579 | -4880.485 | -5263 | -5285 | -4880.485 | -7.869% |  | 0
E545-E540 | -3743.2989 | -4076 | -4083 | -3514.133 | -3745.491 | -3825 | -4083 | -3514.133 | -14.85% |  | 0
Compressor (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 3986.0911 | 4244 | 4244 |  | 4166.82 | 4177 | 3986.0911 | 4244 | 6.194% |  | 0
E320-E300 | 4079.6031 | 3681 | 3721 |  | 4076.025 | 4036 | 3681 | 4079.6031 | 10.17% |  | 0
E330-E300 | 4946.1978 | 4603 | 4352 |  | 5157.732 | 4899 | 4352 | 5157.732 | 16.82% |  | 0
E330-E320 | 866.5947 | 922 | 631 |  | 1081.707 | 863 | 631 | 1081.707 | 51.64% |  | 0
E340-E300 | 4609.403 | 4260 | 4172 |  | 4702.789 | 4524 | 4172 | 4702.789 | 11.92% | 0 | 0
E330-E340 | 336.7947 | 343 | 180 |  | 454.943 | 375 | 180 | 454.943 | 81.36% |  | 0
E350-E300 | -3036.6939 | -3767 | -3772 |  | -3031.946 | -2985 | -3772 | -2985 | -23.72% |  | 0
E360-E300 | 17752.3056 | 17430 | 17382 |  | 17927.161 | 18065 | 17382 | 18065 | 3.856% |  | 0
E400-E300 | -3174.5856 | -3463 | -3442 |  |  | -3247 | -3463 | -3174.5856 | -8.657% |  | 0
E410-E300 | -3149.0399 | -2746 | -2723 |  |  | -3191 | -3191 | -2723 | -15.85% |  | 0
E420-E300 | -1994.9489 | -1973 | -1639 |  |  | -1662 | -1994.9489 | -1639 | -19.59% |  | 0
E430-E300 | -2754.9132 | -2510 | -2622 |  |  | -2910 | -2910 | -2510 | -14.82% |  | 0
E440-E300 | -1724.4011 | -1527 | -1584 |  |  | -1627 | -1724.4011 | -1527 | -12.22% |  | 0
E500-E300 | -4499.2388 | -3096 | -3095 |  | -3912.149 | -3354 | -4499.2388 | -3095 | -39.1% |  | 0
E510-E500 | 13805.7311 | 14303 | 14304 |  | 13913.445 | 14230 | 13805.7311 | 14304 | 3.531% |  | 0
E525-E520 | -2963.4018 | -3241 | -3233 |  | -3148.17 | -2742 | -3241 | -2742 | -16.28% |  | 0
E530-E500 | -4197.3004 | -4346 | -4354 |  | -4001.924 | -4350 | -4354 | -4001.924 | -8.284% |  | 0
E545-E540 | -2398.8748 | -2713 | -2720 |  | -2413.197 | -2449 | -2720 | -2398.8748 | -12.65% |  | 0
e300results.xls t:a06..m49; 07/19/04
Delta Annual Space Cooling Electricity Consumptions (ctd.)
Supply Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E320-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E330-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E330-E320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E340-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E360-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E400-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E410-E300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #DIV/0! |  | 0
E420-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E430-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E440-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E500-E300 | -8316.0984 | -8511 | -8511 | -8231.549 | -8326.688 | -8241 | -8511 | -8231.549 | -3.344% |  | 0
E510-E500 | 1951.1712 | 2262 | 2262 | 2035.088 | 2001.783 | 2038 | 1951.1712 | 2262 | 14.86% |  | 0
E525-E520 | -973.4182 | -988 | -986 | -948.4547 | -995.563 | -979 | -995.563 | -948.4547 | -4.815% |  | 0
E530-E500 | -491.3766 | -536 | -536 | -508.8296 | -502.376 | -522 | -536 | -491.3766 | -8.646% |  | 0
E545-E540 | -768.7729 | -757 | -757 | -628.6074 | -761.749 | -787 | -787 | -628.6074 | -21.31% |  | 0
Condenser Fan (kWh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 353.5115 | 385 | 385 |  | 376.338 | 368 | 353.5115 | 385 | 8.429% |  | 0
E320-E300 | 346.2767 | 314 | 316 |  | 348.379 | 358 | 314 | 358 | 13.07% |  | 0
E330-E300 | 383.3254 | 355 | 331 |  | 400.994 | 370 | 331 | 400.994 | 19.02% |  | 0
E330-E320 | 37.0487 | 41 | 15 |  | 52.615 | 12 | 12 | 52.615 | 128.8% |  | 0
E340-E300 | 376.1148 | 348 | 338 |  | 386.061 | 361 | 338 | 386.061 | 13.28% |  | 0
E330-E340 | 7.2105 | 7 | -7 |  | 14.933 | 9 | -7 | 14.933 | 352.1% |  | 0
E350-E300 | -360.1038 | -436 | -435 |  | -357.873 | -353 | -436 | -353 | -21.37% |  | 0
E360-E300 | 1912.7089 | 1884 | 1879 |  | 1939.686 | 1949 | 1879 | 1949 | 3.659% |  | 0
E400-E300 | -414.0381 | -441 | -437 |  |  | -421 | -441 | -414.0381 | -6.296% |  | 0
E410-E300 | -406.3054 | -336 | -333 |  |  | -387 | -406.3054 | -333 | -20.05% |  | 0
E420-E300 | -251.8207 | -247 | -206 |  |  | -208 | -251.8207 | -206 | -20.08% |  | 0
E430-E300 | -340.8327 | -308 | -322 |  |  | -353 | -353 | -308 | -13.6% |  | 0
E440-E300 | -218.0552 | -191 | -198 |  |  | -203 | -218.0552 | -191 | -13.36% |  | 0
E500-E300 | -480.5531 | -326 | -327 |  | -414.621 | -347 | -480.5531 | -326 | -40.78% |  | 0
E510-E500 | 1461.0219 | 1534 | 1534 |  | 1498.872 | 1526 | 1461.0219 | 1534 | 4.83% |  | 0
E525-E520 | -728.888 | -752 | -750 |  | -745.624 | -733 | -752 | -728.888 | -3.115% |  | 0
E530-E500 | -367.939 | -395 | -395 |  | -376.185 | -391 | -395 | -367.939 | -7.028% |  | 0
E545-E540 | -575.6512 | -606 | -606 |  | -570.545 | -589 | -606 | -570.545 | -6.015% |  | 0
e300results.xls t:a51..m94; 07/19/04
Delta Cooling Coil Loads
Sensible Coil Load (kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | -405.371 | 504.132 | 507.9423 | -100.4356 | -24.393 | -108 | -405.371 | 507.9423 | 1466% |  | 0
E320-E300 | 6197.4569 | 6900.1602 | 6942.0735 | 6585.5914 | 6799.339 | 7543 | 6197.4569 | 7543 | 19.71% |  | 0
E330-E300 | 6421.6281 | 7514.2047 | 7522.9977 | 7908.0123 | 7439.994 | 6631 | 6421.6281 | 7908.0123 | 20.53% |  | 0
E330-E320 | 224.1712 | 614.0445 | 580.9242 | 1322.421 | 640.655 | -912 | -912 | 1322.421 | 542.7% |  | 0
E340-E300 | 6370.8576 | 7256.5698 | 7305.8106 | 7225.3169 | 7171.095 | 6215 | 6215 | 7305.8106 | 15.75% |  | 0
E330-E340 | 50.7704 | 257.6349 | 217.1871 | 682.6954 | 268.899 | 416 | 50.7704 | 682.6954 | 200.3% |  | 0
E350-E300 | -6290.9181 | -8112.4218 | -8128.2492 | -6830.4744 | -6620.663 | -6423 | -8128.2492 | -6290.9181 | -26% |  | 0
E360-E300 | 78315.0867 | 79122.9312 | 79134.9483 | 79545.0534 | 78996.242 | 79506 | 78315.0867 | 79545.0534 | 1.555% |  | 0
E400-E300 | -14709.3889 | -14377.7274 | -14367.762 | -14566.8442 |  | -14010 | -14709.3889 | -14010 | -4.855% |  | 0
E410-E300 | -10985.1029 | -8138.2146 | -8144.9559 |  |  | -9606 | -10985.1029 | -8138.2146 | -30.88% |  | 0
E420-E300 | -6271.9238 | -6130.7727 | -5192.5596 | -5721.4244 |  | -5207 | -6271.9238 | -5192.5596 | -18.92% |  | 0
E430-E300 | -8798.4022 | -8065.5258 | -8350.7121 | -8254.3534 |  | -9048 | -9048 | -8065.5258 | -11.55% |  | 0
E440-E300 | -5785.676 | -5204.2836 | -5312.7306 | -5165.0306 |  | -5406 | -5785.676 | -5165.0306 | -11.55% |  | 0
E500-E300 | -11617.9484 | -8147.0076 | -8158.7316 | -7808.6231 | -10335.24 | -7661 | -11617.9484 | -7661 | -44.19% |  | 0
E510-E500 | 43046.1977 | 45710.1174 | 45709.8243 | 44950.3557 | 43050.834 | 45083 | 43046.1977 | 45710.1174 | 5.974% |  | 0
E525-E520 | -130.6037 | -883.9896 | -882.231 | -1187.4385 | -201.619 | -949 | -1187.4385 | -130.6037 | -149.7% |  | 0
E530-E500 | 2.048 | -1076.2632 | -1075.9701 | -369.1301 | 0 | -528 | -1076.2632 | 2.048 | -212.3% |  | 0
E545-E540 | -130.4955 | -808.6629 | -808.6629 | -837.5233 | -201.642 | -792 | -837.5233 | -130.4955 | -118.5% |  | 0
Latent Coil Load(kWh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 19320.6351 | 19607.2176 | 19612.2003 | 19118.099 | 19575.693 | 19111 | 19111 | 19612.2003 | 2.585% |  | 0
E320-E300 | 13167.3536 | 12172.7361 | 12259.2006 | 12519.2494 | 12597.449 | 11157 | 11157 | 13167.3536 | 16.33% |  | 0
E330-E300 | 18164.3759 | 15932.3298 | 16178.5338 | 17572.9191 | 18528.23 | 17119 | 15932.3298 | 18528.23 | 15.05% |  | 0
E330-E320 | 4997.0223 | 3759.5937 | 3919.3332 | 5053.6697 | 5930.781 | 5962 | 3759.5937 | 5962 | 44.61% |  | 0
E340-E300 | 15930.2538 | 14487.6399 | 14625.3969 | 15578.2133 | 15760.481 | 15279 | 14487.6399 | 15930.2538 | 9.443% |  | 0
E330-E340 | 2234.1221 | 1444.6899 | 1553.1369 | 1994.7059 | 2767.749 | 1840 | 1444.6899 | 2767.749 | 67.08% |  | 0
E350-E300 | -4747.9518 | -5434.6602 | -5529.0384 | -4904.9759 | -4263.749 | -4446 | -5529.0384 | -4263.749 | -25.89% |  | 0
E360-E300 | 4232.1084 | 3400.8393 | 3426.9252 | 4332.6356 | 4459.339 | 4403 | 3400.8393 | 4459.339 | 26.18% |  | 0
E400-E300 | 3075.3436 | 2011.8384 | 2100.9408 | 2727.3459 |  | 2650 | 2011.8384 | 3075.3436 | 42.32% |  | 0
E410-E300 | -768.9108 | -2365.6101 | -2303.4729 |  |  | -2477 | -2477 | -768.9108 | -86.32% |  | 0
E420-E300 | -1545.6363 | -1541.706 | -1217.2443 | -1360.4828 |  | -1212 | -1545.6363 | -1212 | -24.26% |  | 0
E430-E300 | -1872.1533 | -1577.1711 | -1721.9625 | -1787.8897 |  | -2010 | -2010 | -1577.1711 | -24.13% |  | 0
E440-E300 | -929.828 | -699.0435 | -798.1113 | -802.8657 |  | -823 | -929.828 | -699.0435 | -28.47% |  | 0
E500-E300 | -5451.8128 | -3140.5665 | -3140.8596 | -4932.0181 | -4304.002 | -4983 | -5451.8128 | -3140.5665 | -53.43% |  | 0
E510-E500 | 17484.6814 | 17615.0169 | 17615.0169 | 17488.8475 | 17488.438 | 17340 | 17340 | 17615.0169 | 1.571% |  | 0
E525-E520 | 2.0047 | -288.1173 | -288.1173 | 2.4788 | -8.624 | -42 | -288.1173 | 2.4788 | -280.1% |  | 0
E530-E500 | -18313.3062 | -18285.3366 | -18285.6297 | -18231.6742 | -18229.955 | -18084 | -18313.3062 | -18084 | -1.257% |  | 0
E545-E540 | -0.97976 | -81.4818 | -81.4818 | -8.8672 | -3.086 | -2 | -81.4818 | -0.97976 | -271.5% |  | 0
e300results.xls t:a99..m142; 07/19/04
Delta Various Annual Means (COP2, IDB)
COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.16552 | 0.1798 | 0.18013 | 0.16518 | 0.17086 | 0.15 | 0.15 | 0.18013 | 17.87% |  | 0
E320-E300 | 0.17083 | 0.22029 | 0.21969 | 0.1753 | 0.17958 | 0.16 | 0.16 | 0.22029 | 32.13% |  | 0
E330-E300 | 0.24166 | 0.25649 | 0.29907 | 0.26442 | 0.2709 | 0.23 | 0.23 | 0.29907 | 26.52% |  | 0
E330-E320 | 0.070831 | 0.036201 | 0.079382 | 0.089118 | 0.091321 | 0.07 | 0.036201 | 0.091321 | 75.7% |  | 0
E340-E300 | 0.20521 | 0.23966 | 0.25826 | 0.22045 | 0.22316 | 0.19 | 0.19 | 0.25826 | 30.64% |  | 0
E330-E340 | 0.036452 | 0.016833 | 0.040815 | 0.043961 | 0.047744 | 0.04 | 0.016833 | 0.047744 | 82.14% |  | 0
E350-E300 | -0.00011501 | 0.003096 | -0.0019178 | 0.0043635 | 0.0025325 | 0 | -0.0019178 | 0.0043635 | 473.5% |  | 0
E360-E300 | 0.41996 | 0.46293 | 0.46845 | 0.43775 | 0.44031 | 0.43 | 0.41996 | 0.46845 | 10.94% |  | 0
E400-E300 | 0.0012106 | 0.013724 | 0.014548 | 0.016855 |  | 0.03 | 0.0012106 | 0.03 | 188.6% |  | 0
E410-E300 | -0.0095511 | -0.025269 | -0.026661 |  |  | -0.02 | -0.026661 | -0.0095511 | -84% |  | 0
E420-E300 | -0.023 | -0.022394 | -0.019831 | -0.020419 |  | -0.02 | -0.023 | -0.019831 | -15% |  | 0
E430-E300 | -0.02827 | -0.024649 | -0.025889 | -0.024351 |  | -0.02 | -0.02827 | -0.02 | -33.58% |  | 0
E440-E300 | -0.017725 | -0.015393 | -0.015474 | -0.01474 |  | -0.01 | -0.017725 | -0.01 | -52.67% |  | 0
E500-E300 | -0.045013 | -0.010183 | -0.010822 | -0.033871 | -0.034365 | -0.03 | -0.045013 | -0.010183 | -127.2% |  | 0
E510-E500 | 0.40948 | 0.41598 | 0.41577 | 0.40814 | 0.39713 | 0.41 | 0.39713 | 0.41598 | 4.606% |  | 0
E525-E520 | 0.58247 | 0.57414 | 0.57204 | 0.57773 | 0.60629 | 0.49 | 0.49 | 0.60629 | 20.51% |  | 0
E530-E500 | -0.24223 | -0.25849 | -0.25718 | -0.24762 | -0.27645 | -0.22 | -0.27645 | -0.22 | -22.55% |  | 0
E545-E540 | 0.5601 | 0.55853 | 0.56036 | 0.46974 | 0.54604 | 0.51 | 0.46974 | 0.56036 | 16.97% |  | 0
IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.1313 | 0.055556 | 0 | 0.0023647 | 0.0080616 | 0.02 | 0 | 0.1313 | 362.6% |  | 0
E320-E300 | 0.27622 | 0.33333 | 0.33333 | 0.14305 | 0.24571 | 0.54 | 0.14305 | 0.54 | 127.3% |  | 0
E330-E300 | 0.25545 | 0.22222 | 0.22222 | 0.20615 | 0.21382 | 0.19 | 0.19 | 0.25545 | 29.98% |  | 0
E330-E320 | -0.02077 | -0.11111 | -0.11111 | 0.063101 | -0.031885 | -0.35 | -0.35 | 0.063101 | -441.2% |  | 0
E340-E300 | 0.25135 | 0.22222 | 0.22222 | 0.22139 | 0.22722 | 0.22 | 0.22 | 0.25135 | 13.79% |  | 0
E330-E340 | 0.0041016 | 0 | 0 | -0.015241 | -0.013394 | -0.03 | -0.03 | 0.0041016 | -375.2% |  | 0
E350-E300 | 2.0352 | 2.1111 | 2.1111 | 2.1477 | 2.187 | 2.16 | 2.0352 | 2.187 | 7.141% |  | 0
E360-E300 | 1.7407 | 1.5556 | 1.5 | 1.342 | 1.3992 | 1.38 | 1.342 | 1.7407 | 26.82% |  | 0
E400-E300 | 0.50202 | 0 | 0 | 0.0013587 |  | 0 | 0 | 0.50202 | 498.7% |  | 0
E410-E300 | 0.49787 | 0 | 0 |  |  | 0 | 0 | 0.49787 | 400% |  | 0
E420-E300 | 0.3019 | 0 | 0 | -6.2527e-05 |  | 0 | -6.2527e-05 | 0.3019 | 500.2% |  | 0
E430-E300 | 0.36731 | 0 | 0 | -6.9725e-05 |  | 0 | -6.9725e-05 | 0.36731 | 500.2% |  | 0
E440-E300 | 0.2875 | 0 | 0 | -3.3826e-05 |  | 0 | -3.3826e-05 | 0.2875 | 500.1% |  | 0
E500-E300 | -3.3901 | -3.3889 | -3.5 | -3.6854 | -2.9838 | -1.13 | -3.6854 | -1.13 | -84.81% |  | 0
E510-E500 | 1.2445 | 0.11111 | 0.11111 | -0.022969 | 0 | 0 | -0.022969 | 1.2445 | 526.7% |  | 0
E525-E520 | 13.3272 | 13.6111 | 13.5556 | 13.5028 | 13.6289 | 15.8 | 13.3272 | 15.8 | 17.78% |  | 0
E530-E500 | -0.20888 | -0.055556 | 0 | 0.1914 | 0 | 0 | -0.20888 | 0.1914 | -3288% |  | 0
E545-E540 | 13.3159 | 13.5556 | 13.5556 | 13.5202 | 13.576 | 15.71 | 13.3159 | 15.71 | 17.26% |  | 0
e300results.xls t:a145..m188; 07/19/04
Delta Various Annual Means (Zone Humidity)
Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.0020018 | 0.0021 | 0.0021 | 0.0019881 | 0.0019998 | 0.0019 | 0.0019 | 0.0021 | 9.926% |  | 0
E320-E300 | 0.00091896 | 0.0009 | 0.0009 | 0.0008715 | 0.00087438 | 0.0007 | 0.0007 | 0.00091896 | 25.44% |  | 0
E330-E300 | 0.00067186 | 0.0007 | 0.0007 | 0.00071519 | 0.00063678 | 0.0007 | 0.00063678 | 0.00071519 | 11.41% |  | 0
E330-E320 | -0.00024709 | -0.0002 | -0.0002 | -0.00015631 | -0.00023759 | 0 | -0.00024709 | 0 | -142.4% |  | 0
E340-E300 | 0.00072232 | 0.0007 | 0.0007 | 0.00073675 | 0.00069351 | 0.0007 | 0.00069351 | 0.00073675 | 6.1% |  | 0
E330-E340 | -5.0461e-05 | 0 | 0 | -2.1555e-05 | -5.6729e-05 | 0 | -5.6729e-05 | 0 | -264.4% |  | 0
E350-E300 | 0.00063685 | 0.0008 | 0.0008 | 0.00063099 | 0.00058373 | 0.00057 | 0.00057 | 0.0008 | 34.31% |  | 0
E360-E300 | -0.0005696 | -0.0005 | -0.0005 | -0.00055909 | -0.00062237 | -0.00062 | -0.00062237 | -0.0005 | -21.78% |  | 0
E400-E300 | 0.00073206 | 0.0008 | 0.0008 | 0.00087651 |  | 0.0008 | 0.00073206 | 0.00087651 | 18.02% |  | 0
E410-E300 | 0.00067139 | 0.0003 | 0.0003 |  |  | 0.0003 | 0.0003 | 0.00067139 | 94.54% |  | 0
E420-E300 | 0.00019481 | 0.0002 | 0.0002 | 0.00018218 |  | 0.0001 | 0.0001 | 0.0002 | 57.01% |  | 0
E430-E300 | 0.00024119 | 0.0002 | 0.0002 | 0.00022163 |  | 0.0002 | 0.0002 | 0.00024119 | 19.38% |  | 0
E440-E300 | 8.8738e-05 | 0.0001 | 0.0001 | 6.5316e-05 |  | 0 | 0 | 0.0001 | 141.2% |  | 0
E500-E300 | 0.00070622 |  |  | -1.9753e-05 | 0.0010435 | 0.0015 | -1.9753e-05 | 0.0015 | 188.2% |  | 0
E510-E500 | 0.00037457 |  |  | 8.3769e-06 | -8.8998e-07 | 0 | -8.8998e-07 | 0.00037457 | 393.1% |  | 0
E525-E520 | 0.0070203 |  |  | 0.0073646 | 0.0069569 | 0.00747 | 0.0069569 | 0.00747 | 7.123% |  | 0
E530-E500 | -0.0035488 |  |  | -0.0026609 | -0.0044208 | -0.00403 | -0.0044208 | -0.0026609 | -48.02% |  | 0
E545-E540 | 0.0017664 |  |  | 0.0024077 | 0.0028945 | 0.00259 | 0.0017664 | 0.0028945 | 46.72% |  | 0
Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 9.7158 | 10.25 | 10.25 | 10.0163 | 10.0148 | 9.87 | 9.7158 | 10.25 | 5.331% |  | 0
E320-E300 | 3.3904 | 2.95 | 2.97 | 3.5083 | 3.2773 | 2.01 | 2.01 | 3.5083 | 49.65% |  | 0
E330-E300 | 2.2296 | 2.32 | 2.37 | 2.6617 | 2.2587 | 2.77 | 2.2296 | 2.77 | 22.19% |  | 0
E330-E320 | -1.1608 | -0.63 | -0.6 | -0.84659 | -1.0186 | 0.76 | -1.1608 | 0.76 | -329.7% |  | 0
E340-E300 | 2.4702 | 2.43 | 2.45 | 2.7026 | 2.4705 | 2.85 | 2.43 | 2.85 | 16.39% |  | 0
E330-E340 | -0.24056 | -0.11 | -0.08 | -0.040899 | -0.21187 | -0.08 | -0.24056 | -0.040899 | -156.9% |  | 0
E350-E300 | -3.1309 | -2.81 | -2.73 | -3.3505 | -3.5099 | -3.37 | -3.5099 | -2.73 | -24.76% |  | 0
E360-E300 | -7.5814 | -6.77 | -6.79 | -6.581 | -6.9551 | -6.72 | -7.5814 | -6.581 | -14.5% |  | 0
E400-E300 | 2.156 | 3.95 | 3.97 | 4.3298 |  | 4.08 | 2.156 | 4.3298 | 58.8% |  | 0
E410-E300 | 1.8822 | 1.39 | 1.35 |  |  | 1.82 | 1.35 | 1.8822 | 33.05% |  | 0
E420-E300 | 0.16451 | 0.88 | 0.69 | 0.90472 |  | 0.83 | 0.16451 | 0.90472 | 106.7% |  | 0
E430-E300 | 0.20708 | 0.91 | 1.02 | 1.0997 |  | 1.24 | 0.20708 | 1.24 | 115.4% |  | 0
E440-E300 | -0.28509 | 0.2 | 0.29 | 0.32416 |  | 0.3 | -0.28509 | 0.32416 | 367.4% |  | 0
E500-E300 | 17.9113 |  |  | 9.9915 | 18.1158 | 15.8 | 9.9915 | 18.1158 | 52.57% |  | 0
E510-E500 | -2.3476 |  |  | 0.11782 | -0.010621 | 0.11 | -2.3476 | 0.11782 | -462.9% |  | 0
E525-E520 | -8.4071 |  |  | -7.2115 | -10.0881 | -14.8 | -14.8 | -7.2115 | -74.94% |  | 0
E530-E500 | -19.7962 |  |  | -10.4047 | -24.4903 | -24.13 | -24.4903 | -10.4047 | -71.48% |  | 0
E545-E540 | -11.8961 |  |  | -7.5469 | -3.1763 | -14.62 | -14.62 | -3.1763 | -122.9% |  | 0
e300results.xls t:a191..m234; 07/19/04
Delta Hourly Integrated Maximum Total Consumptions
Total Consumption (Wh,e) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 968.3645 | 1019 | 993 | 576.3704 | 721 | 614 | 576.3704 | 1019 | 54.29% |  | 0
E320-E300 | 1402.1615 | 1352 | 1379 | 993.1303 | 1172 | 1327 | 993.1303 | 1402.1615 | 32.18% |  | 0
E330-E300 | 1720.664 | 1648 | 1805 | 1360.526 | 1535 | 1787 | 1360.526 | 1805 | 27.06% |  | 0
E330-E320 | 318.5024 | 296 | 426 | 367.3957 | 363 | 460 | 296 | 460 | 44.11% |  | 0
E340-E300 | 1554.8648 | 1594 | 1588 | 1179.2169 | 1345 | 1553 | 1179.2169 | 1594 | 28.24% |  | 0
E330-E340 | 165.7992 | 54 | 217 | 181.3091 | 190 | 234 | 54 | 234 | 103.6% |  | 0
E350-E300 | 0.85194 | 90 | 0 | -0.0072418 | 0 | -2 | -2 | 90 | 621.3% |  | 0
E360-E300 | 1143.4651 | 1172 | 1124 | 780.7195 | 931 | 1214 | 780.7195 | 1214 | 40.84% |  | 0
E400-E300 | 1.8307 | 0 | 75 | -0.01154 |  | -29 | -29 | 75 | 1087% |  | 0
E410-E300 | 1.8307 | 0 | 0 |  |  | 1 | 0 | 1.8307 | 258.7% |  | 0
E420-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E430-E300 | 0 | 0 | 0 | 1.0004e-10 |  | 0 | 0 | 1.0004e-10 | 500% |  | 0
E440-E300 | 0 | 0 | 0 | 1.0004e-10 |  | -87 | -87 | 1.0004e-10 | -500% |  | 0
E500-E300 | -1459.5539 | -1133 | -1177 | -1557.1915 | -1755 | -1274 | -1755 | -1133 | -44.66% |  | 0
E510-E500 | 1038.4136 | 1159 | 1162 | 1012.234 | 1009 | 1070 | 1009 | 1162 | 14.23% |  | 0
E525-E520 | -1668.6417 | -1451 | -1483 | -1673.579 | -1625 | -1099 | -1673.579 | -1099 | -38.3% |  | 0
E530-E500 | -2138.1546 | -2372 | -2370 | -2145.4765 | -2185 | -2185 | -2372 | -2138.1546 | -10.47% |  | 0
E545-E540 | -1494.1291 | -1593 | -1593 | -1308.4538 | -1495 | -1514 | -1593 | -1308.4538 | -18.97% |  | 0
e300results.xls t:a242..m264; 07/19/04
Delta Hourly Integrated Maximum Coil Loads
Sensible + Latent Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 5153.95 | 5349 | 5578 | 4315.0471 | 4759 | 4919 | 4315.0471 | 5578 | 25.2% |  | 0
E320-E300 | 8143.55 | 22412 | 22368 | 7039.5416 | 7402 | 7848 | 7039.5416 | 22412 | 122.6% |  | 0
E330-E300 | 11317.95 | 12227 | 33117 | 10540.4711 | 11476 | 10343 | 10343 | 33117 | 153.5% |  | 0
E330-E320 | 3174.4 | -10185 | 10749 | 3500.9295 | 4074 | 2495 | -10185 | 10749 | 909.6% |  | 0
E340-E300 | 9477.65 | 19418 | 28094 | 8550.9999 | 8864 | 9060 | 8550.9999 | 28094 | 140.5% |  | 0
E330-E340 | 1840.3 | -7191 | 5023 | 1989.4712 | 2612 | 1283 | -7191 | 5023 | 1319% |  | 0
E350-E300 | -82.32 | 0 | -1 | -0.025077 | 0 | 5 | -82.32 | 5 | -668.7% |  | 0
E360-E300 | 6683.11 | 9212 | 9564 | 5634.0125 | 5820 | 6379 | 5634.0125 | 9564 | 54.47% |  | 0
E400-E300 | 9004.55 | 9142 | 18383 | 8054.7322 |  | 8702 | 8054.7322 | 18383 | 96.91% |  | 0
E410-E300 | -82.32 | 0 | 0 |  |  | 1 | -82.32 | 1 | -409.8% |  | 0
E420-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E430-E300 | 0 | 0 | 0 | 2.7649e-10 |  | 0 | 0 | 2.7649e-10 | 500% |  | 0
E440-E300 | 0 | 0 | 0 | 2.7649e-10 |  | -295 | -295 | 2.7649e-10 | -500% |  | 0
E500-E300 | -4688.54 | -3694 | -3749 | -5401.0537 | -5935 | -4517 | -5935 | -3694 | -48.05% |  | 0
E510-E500 | 3107.54 | 3481 | 3482 | 3538.1292 | 3381 | 3542 | 3107.54 | 3542 | 12.7% |  | 0
E525-E520 | 410.17 | -412 | -412 | -166.7296 | 8 | -881 | -881 | 410.17 | -533% |  | 0
E530-E500 | -7651.41 | -8131 | -8131 | -8000.2799 | -7791 | -7929 | -8131 | -7651.41 | -6.041% |  | 0
E545-E540 | 500.2 | -291 | -292 | -273.7041 | -30 | -302 | -302 | 500.2 | -699.1% |  | 0
Sensible Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | -183.1 | -123 | -86 | -318.1104 | -379 | -259 | -379 | -86 | -130.4% |  | 0
E320-E300 | 8038.2 | 7916 | 7867 | 8065.5499 | 7677 | 8059 | 7677 | 8065.5499 | 4.895% |  | 0
E330-E300 | 9948.7 | 10207 | 11285 | 11229.0176 | 10540 | 10513 | 9948.7 | 11285 | 12.58% |  | 0
E330-E320 | 1910.5 | 2291 | 3418 | 3163.4677 | 2863 | 2454 | 1910.5 | 3418 | 56.18% |  | 0
E340-E300 | 9551.5 | 8883 | 8881 | 9273.9256 | 9483 | 9272 | 8881 | 9551.5 | 7.269% |  | 0
E330-E340 | 397.2 | 1324 | 2404 | 1955.092 | 1057 | 1241 | 397.2 | 2404 | 143.7% |  | 0
E350-E300 | 0.1 | 0 | 0 | -0.039522 | 0 | -32 | -32 | 0.1 | -603% |  | 0
E360-E300 | 8783.3 | 8908 | 8860 | 8946.1221 | 8524 | 9271 | 8524 | 9271 | 8.41% |  | 0
E400-E300 | 0.1 | 0 | 0 | -0.05333 |  | -31 | -31 | 0.1 | -502.4% |  | 0
E410-E300 | -11.7 | 0 | 0 |  |  | -15 | -15 | 0 | -224.7% |  | 0
E420-E300 | 0 | 0 | 0 | 2.9104e-11 |  | -15 | -15 | 2.9104e-11 | -500% |  | 0
E430-E300 | 0 | 0 | 0 | 5.0204e-10 |  | -15 | -15 | 5.0204e-10 | -500% |  | 0
E440-E300 | 0 | 0 | 0 | 3.0559e-10 |  | -33 | -33 | 3.0559e-10 | -500% |  | 0
E500-E300 | -3728.2 | -3194 | -3197 | -3667.2651 | -4681 | -3090 | -4681 | -3090 | -44.28% |  | 0
E510-E500 | 2180 | 2504 | 2505 | 2432.0566 | 2345 | 2451 | 2180 | 2505 | 13.53% |  | 0
E525-E520 | 286.8 | -309 | -304 | -413.5213 | -210 | -717 | -717 | 286.8 | -361.4% |  | 0
E530-E500 | 284.9 | -433 | -433 | -139.7703 | 0 | -192 | -433 | 284.9 | -471.9% |  | 0
E545-E540 | 500.2 | -291 | -292 | -273.7041 | -35 | -302 | -302 | 500.2 | -694% |  | 0
Latent Coil Load (Wh,th) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 6271.3 | 5835 | 5876 | 6049.2222 | 5737 | 5685 | 5685 | 6271.3 | 9.922% |  | 0
E320-E300 | 13511.6 | 22193 | 22109 | 12161.09 | 11322 | 11537 | 11322 | 22193 | 70.26% |  | 0
E330-E300 | 18189.5 | 17637 | 31415 | 17001.6155 | 17809 | 17096 | 17001.6155 | 31415 | 72.58% |  | 0
E330-E320 | 4677.9 | -4556 | 9306 | 4840.5255 | 6487 | 5559 | -4556 | 9306 | 316.1% |  | 0
E340-E300 | 15212.6 | 21147 | 26617 | 13840.6802 | 13850 | 13402 | 13402 | 26617 | 76.19% |  | 0
E330-E340 | 2976.9 | -3510 | 4798 | 3160.9352 | 3959 | 3694 | -3510 | 4798 | 330.6% |  | 0
E350-E300 | 115.56 | -1 | -1 | 0.55759 | 380 | 1211 | -1 | 1211 | 426.5% |  | 0
E360-E300 | -360.54 | 722 | 942 | -1687.8651 | -1516 | -1458 | -1687.8651 | 942 | -469.8% |  | 0
E400-E300 | 17439.6 | 16274 | 23002 | 16172.5916 |  | 16253 | 16172.5916 | 23002 | 38.31% |  | 0
E410-E300 | 1503.2 | 0 | -3 |  |  | -15 | -15 | 1503.2 | 408.9% |  | 0
E420-E300 | 115.34 | 0 | 0 | -1.3824e-10 |  | 2 | -1.3824e-10 | 115.34 | 491.5% |  | 0
E430-E300 | 0 | 1801 | 1707 | 780.2398 |  | 2 | 0 | 1801 | 209.9% |  | 0
E440-E300 | 0 | 0 | -3 | -8.3674e-11 |  | -253 | -253 | 0 | -494.1% |  | 0
E500-E300 | -1670.24 | -1571 | -1661 | -2686.1278 | -2570 | -2630 | -2686.1278 | -1571 | -52.32% |  | 0
E510-E500 | 927.1 | 990 | 990 | 1132.0803 | 1045 | 1112 | 927.1 | 1132.0803 | 19.85% |  | 0
E525-E520 | 123.37 | -122 | -122 | 221.1694 | 212 | -144 | -144 | 221.1694 | 1300% |  | 0
E530-E500 | -7965.46 | -7733 | -7733 | -7798.7789 | -7626 | -7726.1 | -7965.46 | -7626 | -4.372% |  | 0
E545-E540 | -627.186 | 0 | 0 | -1636.359 | -841 | -1181 | -1636.359 | 0 | -229.1% |  | 0
e300results.xls t:a266..m330; 07/19/04
Delta Hourly Integrated Maximum and Minimum COP2 and Zone Conditions (IDB, Humidity Ratio, Relative Humidity)
Delta Hourly Integrated Maximum and Minimum COP2
Maximum COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | -0.025037 | 0.272 | 0.271 | 0.27226 | 0.25703 | 0.24 | -0.025037 | 0.27226 | 138.6% |  | 0
E320-E300 | 0 | 1.274 | 1.11 | 0.041596 | 0.072694 | 0.5 | 0 | 1.274 | 254.9% |  | 0
E330-E300 | 0 | 0.24 | 1.738 | 0.17299 | 0.25134 | 0.17 | 0 | 1.738 | 405.4% |  | 0
E330-E320 | 0 | -1.034 | 0.628 | 0.13139 | 0.17864 | -0.33 | -1.034 | 0.628 | -2341% |  | 0
E340-E300 | 0 | 0.752 | 1.482 | 0.091522 | 0.14655 | 0.07 | 0 | 1.482 | 349.8% |  | 0
E330-E340 | 0 | -0.512 | 0.256 | 0.081466 | 0.10479 | 0.1 | -0.512 | 0.256 | 15232% |  | 0
E350-E300 | 0 | 0.02 | 0.006 | 0.42216 | 0.061488 | 0 | 0 | 0.42216 | 497% |  | 0
E360-E300 | 0.23263 | 0.559 | 0.57 | 0.50758 | 0.5614 | 0.56 | 0.23263 | 0.57 | 67.69% |  | 0
E400-E300 | -0.091398 | 0.219 | 0.919 | 0.17297 |  | 0.17 | -0.091398 | 0.919 | 363.6% |  | 0
E410-E300 | -0.28043 | 0.034 | -0.002 |  |  | -0.04 | -0.28043 | 0.034 | -436.1% |  | 0
E420-E300 | -0.38705 | -0.062 | -0.098 | -0.078559 |  | 0.06 | -0.38705 | 0.06 | -395.2% |  | 0
E430-E300 | -0.38705 | -0.064 | -0.098 | -0.11877 |  | 0.05 | -0.38705 | 0.05 | -353.7% |  | 0
E440-E300 | -0.28486 | -0.095 | -0.098 | -0.11877 |  | -0.07 | -0.28486 | -0.07 | -161.2% |  | 0
E500-E300 | 0.1068 | 3.498 | 1.444 | 0.31113 | 0.31401 | 0.26 | 0.1068 | 3.498 | 342.9% |  | 0
E510-E500 | 0.4174 | 0 | 0 | 0.47259 | 0.50496 | 0.39 | 0 | 0.50496 | 169.7% |  | 0
E525-E520 | 0.90402 | 1.429 | 1.379 | 0.83955 | 0.83633 | 0.56 | 0.56 | 1.429 | 87.66% |  | 0
E530-E500 | -0.26907 | -3.386 | -1.451 | -0.31413 | -0.34458 | -0.26 | -3.386 | -0.26 | -311.3% |  | 0
E545-E540 | 0.79448 | 0.819 | 0.973 | 0.69873 | 0.48982 | 0.48 | 0.48 | 0.973 | 69.52% |  | 0
Minimum COP2 | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.072169 | 0.052 | 0.05 | 0.092733 | 0.087015 | 0.06 | 0.05 | 0.092733 | 61.94% |  | 0
E320-E300 | 0.032137 | 0.003 | 0.004 | 0.048689 | 0.028893 | 0.02 | 0.003 | 0.048689 | 200.5% |  | 0
E330-E300 | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0 | 0.054161 | 211% |  | 0
E330-E320 | 0 | -0.003 | -0.004 | 0.0054718 | 0.0088028 | 0.01 | -0.004 | 0.01 | 486.3% |  | 0
E340-E300 | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0 | 0.054161 | 211% |  | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E350-E300 | -0.0026372 | 0 | 0 | -8.3391e-08 | 0.00027963 | 0 | -0.0026372 | 0.00027963 | -742.3% |  | 0
E360-E300 | 0.032137 | 0.001 | 0 | 0.054163 | 0.037696 | 0.03 | 0 | 0.054163 | 209.7% |  | 0
E400-E300 | -0.011155 | -0.064 | -0.066 | -4.2365e-07 |  | 0 | -0.066 | 0 | -233.8% |  | 0
E410-E300 | -0.0072339 | 0 | 0 |  |  | 0 | -0.0072339 | 0 | -400% |  | 0
E420-E300 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! |  | 0
E430-E300 | -0.021929 | -0.064 | -0.066 | 4.885e-15 |  | 0 | -0.066 | 4.885e-15 | -217.2% |  | 0
E440-E300 | -0.010585 | -0.064 | -0.066 | 0 |  | 0 | -0.066 | 0 | -234.7% |  | 0
E500-E300 | -0.10787 | -0.105 | -0.149 | -0.079652 | -0.11916 | -0.1 | -0.149 | -0.079652 | -62.98% |  | 0
E510-E500 | 0.20276 | 0.124 | 0 | 0.20451 | 0.21527 | 0.19 | 0 | 0.21527 | 137.9% |  | 0
E525-E520 | 0.46939 | 0.476 | 0.42 | 0.47145 | 0.56074 | 0.43 | 0.42 | 0.56074 | 29.86% |  | 0
E530-E500 | -0.18393 | -0.198 | -0.154 | -0.20025 | -0.19318 | -0.19 | -0.20025 | -0.154 | -24.79% |  | 0
E545-E540 | 0.4795 | 0.459 | 0.46 | 0.37917 | 0.54916 | 0.44 | 0.37917 | 0.54916 | 36.86% |  | 0
e300results.xls t:a341..m384; 07/19/04
Delta Hourly Integrated Maximum and Minimum IDB
Maximum IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.8779 | 1.78 | 1.61 | 1.5534 | 1.57 | 1 | 0.8779 | 1.78 | 64.5% |  | 0
E320-E300 | 6.1605 | 6.5 | 6.39 | 6.8407 | 7.27 | 5.46 | 5.46 | 7.27 | 28.12% |  | 0
E330-E300 | 6.0322 | 6.61 | 6.89 | 6.493 | 6.85 | 5.11 | 5.11 | 6.89 | 28.12% |  | 0
E330-E320 | -0.1283 | 0.11 | 0.5 | -0.34771 | -0.42 | -0.35 | -0.42 | 0.5 | -867.9% |  | 0
E340-E300 | 6.1067 | 6.5 | 6.45 | 6.7419 | 7.1 | 5.39 | 5.39 | 7.1 | 26.8% |  | 0
E330-E340 | -0.0745 | 0.11 | 0.44 | -0.24889 | -0.25 | -0.28 | -0.28 | 0.44 | -1424% |  | 0
E350-E300 | 8.3842 | 9.83 | 9.83 | 9.9988 | 9.95 | 8.81 | 8.3842 | 9.9988 | 17.05% |  | 0
E360-E300 | 7.5586 | 7.67 | 7.45 | 7.8165 | 7.95 | 6.94 | 6.94 | 7.95 | 13.35% |  | 0
E400-E300 | 0.9149 | 2.45 | 3.72 | 1.8999 |  | -0.15 | -0.15 | 3.72 | 219% |  | 0
E410-E300 | 0.6257 | 0 | 0 |  |  | 0 | 0 | 0.6257 | 400% |  | 0
E420-E300 | 0 | 0 | 0 | -1.56e-11 |  | 0.04 | -1.56e-11 | 0.04 | 500% |  | 0
E430-E300 | 0.9993 | 0 | 0 | 0.00048996 |  | 0.26 | 0 | 0.9993 | 396.6% |  | 0
E440-E300 | 0.8453 | 0 | 0 | 0.00048996 |  | 0.07 | 0 | 0.8453 | 461.5% |  | 0
E500-E300 | -0.3945 | 0 | 0 | -0.001584 | -0.03 | -1.19 | -1.19 | 0 | -441.8% |  | 0
E510-E500 | 0.2949 | 0 | 0 | 8.488e-07 | 0 | 0 | 0 | 0.2949 | 600% |  | 0
E525-E520 | 19.9568 | 18.95 | 19.12 | 19.7296 | 19.02 | 16.38 | 16.38 | 19.9568 | 18.97% |  | 0
E530-E500 | 0.3106 | -0.05 | -0.05 | 0.0010308 | 0 | 0 | -0.05 | 0.3106 | 1022% |  | 0
E545-E540 | 19.525 | 19.89 | 19.89 | 19.9975 | 19.95 | 20 | 19.525 | 20 | 2.39% |  | 0
Minimum IDB (°C) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0 | 0 | 0 | -7.6877e-05 | 0 | 0 | -7.6877e-05 | 0 | -600% |  | 0
E320-E300 | 0 | 1.94 | 1.95 | -0.97006 | 0 | 0 | -0.97006 | 1.95 | 600% |  | 0
E330-E300 | 0 | 0 | 0 | -0.0015637 | 0 | 0 | -0.0015637 | 0 | -600% |  | 0
E330-E320 | 0 | -1.94 | -1.95 | 0.96849 | 0 | 0 | -1.95 | 0.96849 | -599.4% |  | 0
E340-E300 | 0 | 0 | 0 | -0.0015637 | 0 | 0 | -0.0015637 | 0 | -600% |  | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E360-E300 | 0 | 0 | 0 | 0.00017992 | 0 | 0 | 0 | 0.00017992 | 600% |  | 0
E400-E300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -500% |  | 0
E410-E300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #DIV/0! |  | 0
E420-E300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -500% |  | 0
E430-E300 | 0 | 0 | 0 | -3.0198e-14 |  | 0 | -3.0198e-14 | 0 | -500% |  | 0
E440-E300 | 0 | 0 | 0 | -3.0198e-14 |  | 0.01 | -3.0198e-14 | 0.01 | 500% |  | 0
E500-E300 | 0.49703 | -0.72 | -0.89 | 0.11004 | 0.54 | 17.05 | -0.89 | 17.05 | 648.9% |  | 0
E510-E500 | 0 | 0 | 0 | 9.3018e-09 | 0 | 0 | 0 | 9.3018e-09 | 600% |  | 0
E525-E520 | 0.13889 | 0.06 | 0.05 | 0.17939 | 0.03 | 19.44 | 0.03 | 19.44 | 585.3% |  | 0
E530-E500 | -0.00551 | 0 | 0 | 0.14539 | 0 | 0 | -0.00551 | 0.14539 | 647.3% |  | 0
E545-E540 | 0.22078 | 0.06 | 0.05 | 0.18093 | 0.03 | 18.06 | 0.03 | 18.06 | 581.6% |  | 0
e300results.xls t:a386..m429; 07/19/04
Delta Hourly Integrated Maximum and Minimum Zone Humidity Ratio
Maximum Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.0024658 | 0.005 | 0.0052 | 0.0019812 | 0.001975 | 0.0023 | 0.001975 | 0.0052 | 102.3% |  | 0
E320-E300 | 0.0047326 | 0.0039 | 0.0039 | 0.0041823 | 0.00409 | 0.0043 | 0.0039 | 0.0047326 | 19.9% |  | 0
E330-E300 | 0.0043671 | 0.004 | 0.004 | 0.004303 | 0.003588 | 0.0043 | 0.003588 | 0.0043671 | 19.03% |  | 0
E330-E320 | -0.0003655 | 0.0001 | 0.0001 | 0.00012066 | -0.000502 | 0 | -0.000502 | 0.00012066 | -683.2% |  | 0
E340-E300 | 0.0045871 | 0.0039 | 0.0037 | 0.0041869 | 0.003815 | 0.0043 | 0.0037 | 0.0045871 | 21.73% |  | 0
E330-E340 | -0.00022 | 0.0001 | 0.0003 | 0.00011606 | -0.000227 | 0 | -0.000227 | 0.0003 | 4579% |  | 0
E350-E300 | 0.0034739 | 0.0061 | 0.0062 | 0.0034245 | 0.003022 | 0.0032 | 0.003022 | 0.0062 | 75.01% |  | 0
E360-E300 | 0.0001491 | 0 | 0 | -3.5233e-08 | 0 | 0 | -3.5233e-08 | 0.0001491 | 600.3% |  | 0
E400-E300 | 0.0036593 | 0.0032 | 0.0033 | 0.0033728 |  | 0.0039 | 0.0032 | 0.0039 | 20.08% |  | 0
E410-E300 | 0.0035512 | 0.0031 | 0.0032 |  |  | 0.0039 | 0.0031 | 0.0039 | 23.27% |  | 0
E420-E300 | 0.0010125 | 0.0009 | 0.0004 | 0.0010861 |  | 0.0013 | 0.0004 | 0.0013 | 95.77% |  | 0
E430-E300 | 0.0029463 | 0.0018 | 0.0019 | 0.0026257 |  | 0.0024 | 0.0018 | 0.0029463 | 49.1% |  | 0
E440-E300 | 2.85e-05 | 0 | 0 | 1.6639e-12 |  | 0 | 0 | 2.85e-05 | 500% |  | 0
E500-E300 | -0.0015646 | -0.0019 | -0.0019 | -0.0021408 | -0.001744 | -0.0019 | -0.0021408 | -0.0015646 | -31.01% |  | 0
E510-E500 | 0.0001517 | 0 | 0.0001 | 1.0006e-05 | 3e-06 | 0 | 0 | 0.0001517 | 343.9% |  | 0
E525-E520 | 0.010392 | 0.0103 | 0.0102 | 0.010744 | 0.01006 | 0.0067 | 0.0067 | 0.010744 | 41.56% |  | 0
E530-E500 | -0.0047305 | -0.0038 | -0.0037 | -0.0045893 | -0.006222 | -0.00473 | -0.006222 | -0.0037 | -54.49% |  | 0
E545-E540 | 0.0009051 | 0.0072 | 0.0059 | 4.3897e-15 | 0.003433 | 0.00129 | 4.3897e-15 | 0.0072 | 230.7% |  | 0
Minimum Humidity Ratio (kg/kg) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 1e-08 | 0 | 0 | 1.4269e-05 | 5.1e-05 | -1e-05 | -1e-05 | 5.1e-05 | 662.1% |  | 0
E320-E300 | 0 | 0 | 0 | 5.8778e-06 | 0 | 0 | 0 | 5.8778e-06 | 600% |  | 0
E330-E300 | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | -1.7099e-08 | 0 | -600% |  | 0
E330-E320 | 0 | 0 | 0 | -5.8949e-06 | 0 | 0 | -5.8949e-06 | 0 | -600% |  | 0
E340-E300 | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | -1.7099e-08 | 0 | -600% |  | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E360-E300 | 0 | 0 | 0 | -2.2215e-11 | 0 | 0 | -2.2215e-11 | 0 | -600% |  | 0
E400-E300 | 0 | 0 | 0 | 3.0931e-12 |  | 0 | 0 | 3.0931e-12 | 500% |  | 0
E410-E300 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | #DIV/0! |  | 0
E420-E300 | 0 | 0 | 0 | -7.6947e-13 |  | 0 | -7.6947e-13 | 0 | -500% |  | 0
E430-E300 | 0 | 0 | 0 | 3.0931e-12 |  | 0 | 0 | 3.0931e-12 | 500% |  | 0
E440-E300 | 0 | 0 | 0 | -9.3204e-13 |  | 0 | -9.3204e-13 | 0 | -500% |  | 0
E500-E300 | 0.0049507 |  |  | 0.0050316 | 0.00494 | 0.00833 | 0.00494 | 0.00833 | 58.32% |  | 0
E510-E500 | 0 |  |  | 0 | 0 | 0.0002 | 0 | 0.0002 | 400% |  | 0
E525-E520 | 0.00073266 |  |  | 0.00053199 | 0.000384 | 0.00883 | 0.000384 | 0.00883 | 322.4% |  | 0
E530-E500 | -0.00061959 |  |  | -0.00051756 | -0.001454 | -0.00367 | -0.00367 | -0.00051756 | -201.4% |  | 0
E545-E540 | 0.0020983 |  |  | 0.0029798 | 0.003432 | 0.0028 | 0.0020983 | 0.003432 | 47.17% |  | 0
e300results.xls t:a431..m474; 07/19/04
Delta Hourly Integrated Maximum and Minimum Zone Relative Humidity
Maximum Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 8.9137 | 30.83 | 31.85 | 10.1493 | 9 | 10.75 | 8.9137 | 31.85 | 135.6% |  | 0
E320-E300 | 13.0466 | 14.06 | 14.82 | 14.9388 | 15 | 14.44 | 13.0466 | 15 | 13.58% |  | 0
E330-E300 | 7.8699 | 9.11 | 9.09 | 8.8625 | 8 | 11.26 | 7.8699 | 11.26 | 37.53% |  | 0
E330-E320 | -5.1767 | -4.95 | -5.73 | -6.0763 | -7 | -3.18 | -7 | -3.18 | -71.37% |  | 0
E340-E300 | 11.1401 | 12.02 | 12.41 | 12.7691 | 12 | 12.81 | 11.1401 | 12.81 | 13.7% |  | 0
E330-E340 | -3.2702 | -2.91 | -3.32 | -3.9066 | -4 | -1.55 | -4 | -1.55 | -77.54% |  | 0
E350-E300 | 0 | 11.77 | 12.27 | 0 | 2 | 5.21 | 0 | 12.27 | 235.6% |  | 0
E360-E300 | 0 | 0 | 0 | -0.00017286 | 0 | 0 | -0.00017286 | 0 | -600% |  | 0
E400-E300 | 14.9642 | 16.22 | 16.72 | 16.856 |  | 18.87 | 14.9642 | 18.87 | 23.35% |  | 0
E410-E300 | 14.4355 | 15.44 | 15.94 |  |  | 18.74 | 14.4355 | 18.74 | 26.67% |  | 0
E420-E300 | 2.0519 | 5.16 | 2.68 | 5.5009 |  | 6.41 | 2.0519 | 6.41 | 99.94% |  | 0
E430-E300 | 11.9195 | 9.08 | 9.58 | 12.9398 |  | 11.5 | 9.08 | 12.9398 | 35.08% |  | 0
E440-E300 | -0.065 | 0 | 0 | 8.1634e-09 |  | 0.07 | -0.065 | 0.07 | 13500% |  | 0
E500-E300 | 31.2108 |  |  | 32.2238 | 32 | -7.36 | -7.36 | 32.2238 | 179.8% |  | 0
E510-E500 | 0 |  |  | 0 | 0 | -2.57 | -2.57 | 0 | -400% |  | 0
E525-E520 | 9.7701 |  |  | 6.3958 | 5 | -20.65 | -20.65 | 9.7701 | 23585% |  | 0
E530-E500 | -8.9555 |  |  | -8.302 | -21 | -24.07 | -24.07 | -8.302 | -101.2% |  | 0
E545-E540 | 29.6022 |  |  | 41.2182 | 50 | -15.82 | -15.82 | 50 | 250.7% |  | 0
Minimum Relative Humidity (%) | [6 empty] | Statistics, All Results
| TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 |  |  | (Max-Min)
| TUD | NREL | NREL | GARD | UR | NRCan | Min | Max | /Mean |  | Your Software
E310-E300 | 0.0586 | 0 | 0 | 1.0832 | 1 | 0.99 | 0 | 1.0832 | 207.5% |  | 0
E320-E300 | 0 | 0 | 0 | 0.40959 | 0 | -2.02 | -2.02 | 0.40959 | -905.2% |  | 0
E330-E300 | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0 | 0.00011523 | 600% |  | 0
E330-E320 | 0 | 0 | 0 | -0.40947 | 0 | 2.02 | -0.40947 | 2.02 | 905.1% |  | 0
E340-E300 | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0 | 0.00011523 | 600% |  | 0
E330-E340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E350-E300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! |  | 0
E360-E300 | 0 | 0 | 0 | -5.6978e-05 | 0 | 0 | -5.6978e-05 | 0 | -600% |  | 0
E400-E300 | -0.1222 | 0 | 0 | -0.46234 |  | -0.37 | -0.46234 | 0 | -242.2% |  | 0
E410-E300 | -0.1221 | 0 | 0 |  |  | -0.36 | -0.36 | 0 | -298.7% |  | 0
E420-E300 | -0.1213 | 0 | 0 | -0.46224 |  | -0.35 | -0.46224 | 0 | -247.6% |  | 0
E430-E300 | -0.1234 | 0 | 0 | -0.46235 |  | -0.36 | -0.46235 | 0 | -244.4% |  | 0
E440-E300 | -0.1243 | 0 | 0 | -0.46235 |  | -0.4 | -0.46235 | 0 | -234.3% |  | 0
E500-E300 | 40.0742 |  |  | 39.0378 | 39 | 37.89 | 37.89 | 40.0742 | 5.6% |  | 0
E510-E500 | -1.3175 |  |  | 0.10666 | 0 | 0.32 | -1.3175 | 0.32 | -735.3% |  | 0
E525-E520 | -15.7395 |  |  | -15.0875 | -17 | -17.5 | -17.5 | -15.0875 | -14.77% |  | 0
E530-E500 | -23.812 |  |  | -20.8644 | -26 | -19.15 | -26 | -19.15 | -30.5% |  | 0
E545-E540 | -19.3505 |  |  | -16.6007 | -12 | -19.6 | -19.6 | -12 | -45% |  | 0
e300results.xls t:a476..m519; 07/19/04

## Qdata
0 | e300results.XLS, July, 2004 | 0 | 0 | 0 | 0 | 0 | SEE SHEET 'A' FOR INSTRUCTIONS | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Space Cooling Electricity Consumption | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Energy Consumption, Total (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your |  |  |  | For QtotINIT plot (results before BESTESTing); results imported from various files as appropriate for first runs of software and specific cases.
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software | (max-min)/mean |  |  |  | TRNSYS TUD | DOE21E-J NREL | DOE21E-E NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN UR | HOT3000 NRCan | (max-min)/mean
0 | E300 Base, 15% OA | 35633.7773 | 34750 | 34755 | 35023.7298 | 34976.411 | 35070 | 0 |  |  |  | E300 Base, 15% OA | 35633.7773 | 34608 | 37908 | 35149 | 31988 | 35029 | 0.16889
0 | E310, High Latent | 39973.3798 | 39379 | 39384 | 39434.1646 | 39519.569 | 39608 | 0 |  |  |  | E310, High Latent | 39973.3798 | 39268 | 43821 | 39999 | 35628 | 39626 | 0.20627
0 | E320, High Infiltration | 40059.657 | 38745 | 38792 | 39375.0348 | 39400.815 | 39457 | 0 |  |  |  | E320, High Infiltration | 38897 | 38692 | 41626 | 39274 | 43434 | 38575 | 0.12122
0 | E330, 100% OA | 40963.3004 | 39708 | 39438 | 40468.7948 | 40535.137 | 40330 | 0 |  |  |  | E330, 100% OA | 40963.3004 | 39445 | 43103 | 40373 | 44484 | 38770 | 0.13872
0 | E340, 50% OA, 50% Infl | 40619.2951 | 39358 | 39265 | 40071.4206 | 40065.261 | 39947 | 0 |  |  |  | E340, 50% OA, 50% Infl | 39665 | 39181 | 42648 | 39997 | 44077 | 39373 | 0.11993
0 | E350, Tstat Set Up | 32236.9795 | 30547 | 30548 | 31376.2065 | 31586.592 | 31742 | 0 |  |  |  | E350, Tstat Set Up | 32236.9795 | 30394 | 33326 | 31447 | 31862 | 31627 | 0.092156
0 | E360, Undersized System | 55298.7917 | 54064 | 54016 | 54944.2502 | 54843.258 | 55068 | 0 |  |  |  | E360, Undersized System | 55298.7917 | 53819 | 55028 | 55351 | 54306 | 54924 | 0.027962
0 | E400, Ec. Temp. Ctrl. | 32045.1536 | 30846 | 30876 | 31265.6433 | 0 | 31413 | 0 |  |  |  | E400, Ec. Temp. Ctrl. | 32045.1536 | 30784 | 37594 | 34331 |  | 31413 | 0.20491
0 | E410, Ec. Comp. Lockout | 32078.4319 | 31668 | 31699 | 32010.5061 | 0 | 31503 | 0 |  |  |  | E410, Ec. Comp. Lockout | 32078.4319 | 31632 | 33629 | 34331 |  | 31503 | 0.086656
0 | E420, Ec. ODB Limit | 33387.0076 | 32530 | 32910 | 32978.5453 | 0 | 33208 | 0 |  |  |  | E420, Ec. ODB Limit | 33387.0076 | 32787 | 35245 | 34331 |  | 33208 | 0.07274
0 | E430, Ec. Enthalpy Ctrl. | 32538.0313 | 31932 | 31811 | 32085.518 | 0 | 31818 | 0 |  |  |  | E430, Ec. Enthalpy Ctrl. | 32538.0313 | 31754 | 35630 | 34035 |  | 31818 | 0.11691
0 | E440, Ec. Enthalpy Limit | 33691.321 | 33032 | 32973 | 33284.8265 | 0 | 33248 | 0 |  |  |  | E440, Ec. Enthalpy Limit | 32041.3688 | 32892 | 35905 | 34035 |  | 33248 | 0.11491
0 | E500, Base w/ 0%OA | 22337.887 | 22817 | 22822 | 23075.8197 | 22322.953 | 23138 | 0 |  |  |  | E500, Base w/ 0%OA | 22337.887 | 22802 | 22808 | 23055 | 22438 | 23138 | 0.035149
0 | E500 May-Sep | 17390.8511 | 17872 | 17870 | 18030.7145 | 17434.537 | 18051 | 0 |  |  |  | E500 May-Sep | 17390.8511 | 17854 | 17854 | 18006 | 17459 | 18051 | 0.037151
0 | E510 May-Sep, High PLR | 34608.7754 | 35971 | 35970 | 35791.0201 | 34848.637 | 35845 | 0 |  |  |  | E510 May-Sep, High PLR | 34608.7754 | 35955 | 35954 | 35720 | 34908 | 35845 | 0.037923
0 | E520, EDB = 15°C | 24986.582 | 25389 | 25390 | 25812.8973 | 25131.07 | 25781 | 0 |  |  |  | E520, EDB = 15°C | 24986.582 | 26043 | 27201 | 24051 | 25161 | 25781 | 0.12335
0 | E522, EDB = 20°C | 23544.1607 | 24293 | 24307 | 24385.5401 | 23619.744 | 24360 | 0 |  |  |  | E522, EDB = 20°C | 23544.1607 | 24424 | 24462 | 24027 | 23741 | 24360 | 0.038096
0 | E525, EDB = 35°C | 20320.874 | 20408 | 20421 | 20781.3508 | 20241.713 | 21323 | 0 |  |  |  | E525, EDB = 35°C | 20320.874 | 20077 | 20074 | 20718 | 20303 | 21323 | 0.061018
0 | E530, Dry Coil | 17281.271 | 17540 | 17537 | 17993.9617 | 17442.468 | 17875 | 0 |  |  |  | E530, Dry Coil | 17281.271 | 17558 | 17548 | 17738 | 17447 | 17875 | 0.033783
0 | E540, Dry, EDB = 15°C | 19430.3785 | 19878 | 19874 | 20122.7341 | 19536.572 | 20164 | 0 |  |  |  | E540, Dry, EDB = 15°C | 19430.3785 | 20145 | 21685 | 17789 | 19566 | 20164 | 0.1968
0 | E545, Dry, EDB = 35°C | 15687.0796 | 15802 | 15791 | 16608.6011 | 15791.081 | 16339 | 0 |  |  |  | E545, Dry, EDB = 35°C | 15687.0796 | 15741 | 15740 | 16643 | 15781 | 16339 | 0.059788
| Energy Consumption, Compressor (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
| 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
| E300 Base, 15% OA | 22353.5343 | 21569 | 21573 | 0 | 21770.001 | 21876 | 0
| E310, High Latent | 26339.6254 | 25813 | 25817 | 0 | 25936.821 | 26053 | 0
| E320, High Infiltration | 26433.1374 | 25250 | 25294 | 0 | 25846.026 | 25912 | 0
| E330, 100% OA | 27299.7321 | 26172 | 25925 | 0 | 26927.733 | 26775 | 0
| E340, 50% OA, 50% Infl | 26962.9373 | 25829 | 25745 | 0 | 26472.79 | 26400 | 0
| E350, Tstat Set Up | 19316.8404 | 17802 | 17801 | 0 | 18738.055 | 18891 | 0
| E360, Undersized System | 40105.8399 | 38999 | 38955 | 0 | 39697.162 | 39941 | 0
| E400, Ec. Temp. Ctrl. | 19178.9487 | 18106 | 18131 | 0 | 0 | 18629 | 0
| E410, Ec. Comp. Lockout | 19204.4944 | 18823 | 18850 | 0 | 0 | 18685 | 0
| E420, Ec. ODB Limit | 20358.5854 | 19596 | 19934 | 0 | 0 | 20214 | 0
| E430, Ec. Enthalpy Ctrl. | 19598.6211 | 19059 | 18951 | 0 | 0 | 18966 | 0
| E440, Ec. Enthalpy Limit | 20629.1333 | 20042 | 19989 | 0 | 0 | 20249 | 0
| E500, Base w/ 0%OA | 17854.2956 | 18473 | 18478 | 0 | 17857.852 | 18522 | 0
| E500 May-Sep | 13942.1479 | 14508 | 14506 | 0 | 13988.512 | 14491 | 0
| E510 May-Sep, High PLR | 27747.879 | 28811 | 28810 | 0 | 27901.957 | 28721 | 0
| E520, EDB = 15°C | 19521.2767 | 20121 | 20126 | 0 | 19654.972 | 20185 | 0
| E522, EDB = 20°C | 18620.3108 | 19407 | 19418 | 0 | 18689.799 | 19281 | 0
| E525, EDB = 35°C | 16557.8748 | 16880 | 16893 | 0 | 16506.802 | 17443 | 0
| E530, Dry Coil | 13656.9951 | 14127 | 14124 | 0 | 13855.928 | 14172 | 0
| E540, Dry, EDB = 15°C | 15020.7433 | 15680 | 15677 | 0 | 15163.82 | 15664 | 0
| E545, Dry, EDB = 35°C | 12621.8685 | 12967 | 12957 | 0 | 12750.623 | 13215 | 0
| Energy Consumption, Supply Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
| 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
| E300 Base, 15% OA | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E310, High Latent | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E320, High Infiltration | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E330, 100% OA | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E340, 50% OA, 50% Infl | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E350, Tstat Set Up | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E360, Undersized System | 10879.92 | 10880 | 10880 | 10862.0919 | 10879.92 | 10880 | 0
| E400, Ec. Temp. Ctrl. | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0
| E410, Ec. Comp. Lockout | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0
| E420, Ec. ODB Limit | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0
| E430, Ec. Enthalpy Ctrl. | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0
| E440, Ec. Enthalpy Limit | 10879.92 | 10880 | 10880 | 10862.0919 | 0 | 10880 | 0
| E500, Base w/ 0%OA | 2563.8216 | 2369 | 2369 | 2630.543 | 2553.232 | 2639 | 0
| E500 May-Sep | 1972.0485 | 1837 | 1837 | 2030.7654 | 1970.497 | 2035 | 0
| E510 May-Sep, High PLR | 3923.2198 | 4099 | 4099 | 4065.8535 | 3972.28 | 4073 | 0
| E520, EDB = 15°C | 3125.1884 | 2874 | 2871 | 3140.7019 | 3131.271 | 3200 | 0
| E522, EDB = 20°C | 2815.5716 | 2704 | 2707 | 2878.8649 | 2819.112 | 2904 | 0
| E525, EDB = 35°C | 2151.7702 | 1886 | 1885 | 2192.2472 | 2135.708 | 2221 | 0
| E530, Dry Coil | 2072.4451 | 1833 | 1833 | 2121.7134 | 2050.856 | 2117 | 0
0 | E540, Dry, EDB = 15°C | 2521.5317 | 2258 | 2258 | 2493.7908 | 2500.416 | 2573 | 0
0 | E545, Dry, EDB = 35°C | 1752.7588 | 1501 | 1501 | 1865.1834 | 1738.667 | 1786 | 0
0 | Energy Consumption, Condenser Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 2400.3229 | 2301 | 2302 | 0 | 2326.49 | 2323 | 0
0 | E310, High Latent | 2753.8345 | 2686 | 2687 | 0 | 2702.828 | 2691 | 0
0 | E320, High Infiltration | 2746.5996 | 2615 | 2618 | 0 | 2674.869 | 2681 | 0
0 | E330, 100% OA | 2783.6483 | 2656 | 2633 | 0 | 2727.484 | 2693 | 0
0 | E340, 50% OA, 50% Infl | 2776.4378 | 2649 | 2640 | 0 | 2712.551 | 2684 | 0
0 | E350, Tstat Set Up | 2040.2191 | 1865 | 1867 | 0 | 1968.617 | 1970 | 0
0 | E360, Undersized System | 4313.0318 | 4185 | 4181 | 0 | 4266.176 | 4272 | 0
0 | E400, Ec. Temp. Ctrl. | 1986.2848 | 1860 | 1865 | 0 | 0 | 1902 | 0
0 | E410, Ec. Comp. Lockout | 1994.0175 | 1965 | 1969 | 0 | 0 | 1936 | 0
0 | E420, Ec. ODB Limit | 2148.5022 | 2054 | 2096 | 0 | 0 | 2115 | 0
0 | E430, Ec. Enthalpy Ctrl. | 2059.4903 | 1993 | 1980 | 0 | 0 | 1970 | 0
0 | E440, Ec. Enthalpy Limit | 2182.2678 | 2110 | 2104 | 0 | 0 | 2120 | 0
0 | E500, Base w/ 0%OA | 1919.7698 | 1975 | 1975 | 0 | 1911.869 | 1976 | 0
0 | E500 May-Sep | 1476.6547 | 1527 | 1527 | 0 | 1475.528 | 1524 | 0
0 | E510 May-Sep, High PLR | 2937.6766 | 3061 | 3061 | 0 | 2974.4 | 3050 | 0
0 | E520, EDB = 15°C | 2340.1169 | 2394 | 2393 | 0 | 2344.827 | 2396 | 0
0 | E522, EDB = 20°C | 2108.2783 | 2182 | 2182 | 0 | 2110.833 | 2174 | 0
0 | E525, EDB = 35°C | 1611.2289 | 1642 | 1643 | 0 | 1599.203 | 1663 | 0
0 | E530, Dry Coil | 1551.8309 | 1580 | 1580 | 0 | 1535.684 | 1585 | 0
| E540, Dry, EDB = 15°C | 1888.1035 | 1940 | 1939 | 0 | 1872.336 | 1926 | 0
| E545, Dry, EDB = 35°C | 1312.4522 | 1334 | 1333 | 0 | 1301.791 | 1337 | 0
0
0 | Weather Data Checks, E300 Only | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | Annual Mean Output | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ODB | 19.9145 | 19.8889 | 19.8889 | 19.9141 | 19.9145 | 19.91 | 0
0 | OHR | 0.011643 | 0.0116 | 0.0116 | 0.011608 | 0.011649 | 0.0116 | 0
0 | Annual Hourly Integrated Maxima | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | ODB | 34.7 | 35 | 35 | 34.775 | 35 | 35 | 0
0 | OHR | 0.021878 | 0.0225 | 0.0225 | 0.021868 | 0.022406 | 0.0223 | 0
0
0
0
0
0
0
0 | Space Cooling Coil Loads | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Total Sensible + Latent (kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 80426.8675 | 77283.4356 | 77291.9355 | 78329.9975 | 77744.589 | 78257 | 0
0 | E310, High Latent | 99342.1316 | 97394.7852 | 97412.0781 | 97347.6609 | 97295.866 | 97261 | 0
0 | E320, High Infiltration | 99791.678 | 96356.3319 | 96493.2096 | 97434.8383 | 97141.307 | 96957 | 0
0 | E330, 100% OA | 105012.8715 | 100729.9701 | 100993.467 | 103810.929 | 103712.915 | 102008 | 0
0 | E340, 50% OA, 50% Infl | 102727.9789 | 99027.6453 | 99223.143 | 101133.5278 | 100676.21 | 99753 | 0
0 | E350, Tstat Set Up | 69387.9976 | 63736.3536 | 63634.6479 | 66594.5472 | 66860.163 | 67389 | 0
0 | E360, Undersized System | 162974.0626 | 159807.2061 | 159853.809 | 162207.6865 | 161200.179 | 162168 | 0
0 | E400, Ec. Temp. Ctrl. | 68792.8221 | 64917.5466 | 65025.1143 | 66490.4992 | 0 | 66898 | 0
0 | E410, Ec. Comp. Lockout | 68672.8538 | 66779.6109 | 66843.5067 | 68071.4219 | 0 | 66175 | 0
0 | E420, Ec. ODB Limit | 72609.3074 | 69610.9569 | 70882.1316 | 71248.0904 | 0 | 71803 | 0
0 | E430, Ec. Enthalpy Ctrl. | 69756.312 | 67640.7387 | 67219.2609 | 68287.7544 | 0 | 67200 | 0
0 | E440, Ec. Enthalpy Limit | 73711.3635 | 71380.1085 | 71181.0936 | 72362.1012 | 0 | 72029 | 0
0 | E500, Base w/ 0%OA | 63357.1063 | 65995.8615 | 65992.3443 | 65589.3563 | 63105.366 | 65614 | 0
0 | E500 May-Sep | 48443.4308 | 50692.8174 | 50690.4726 | 50355.6741 | 48439.57 | 50357 | 0
0 | E510 May-Sep, High PLR | 108974.3099 | 114017.9517 | 114015.3138 | 112794.8773 | 108979.013 | 112781 | 0
0 | E520, EDB = 15°C | 63421.5444 | 66571.2168 | 66565.3548 | 66213.2769 | 63212.102 | 66146 | 0
0 | E522, EDB = 20°C | 63389.2228 | 66373.0812 | 66371.9088 | 65893.8706 | 63157.03 | 65900 | 0
0 | E525, EDB = 35°C | 63292.9454 | 65399.1099 | 65395.0065 | 65028.3172 | 63001.558 | 65155 | 0
0 | E530, Dry Coil | 45045.848 | 46634.2617 | 46630.7445 | 46988.5521 | 44875.414 | 47002 | 0
0 | E540, Dry, EDB = 15°C | 45112.827 | 47129.8938 | 47126.0835 | 47482.0855 | 44979.842 | 47462 | 0
0 | E545, Dry, EDB = 35°C | 44981.3517 | 46239.7491 | 46235.9388 | 46635.6951 | 44775.11 | 46668 | 0
0 | Sensible Coil Load (kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 56661.7484 | 55796.8608 | 55804.7745 | 55166.0635 | 55209.465 | 55191 | 0
0 | E310, High Latent | 56256.3775 | 56300.9928 | 56312.7168 | 55065.6279 | 55185.072 | 55083 | 0
0 | E320, High Infiltration | 62859.2053 | 62697.021 | 62746.848 | 61751.6548 | 62008.804 | 62734 | 0
0 | E330, 100% OA | 63083.3765 | 63311.0655 | 63327.7722 | 63074.0758 | 62649.459 | 61822 | 0
0 | E340, 50% OA, 50% Infl | 63032.6061 | 63053.4306 | 63110.5851 | 62391.3804 | 62380.56 | 61406 | 0
0 | E350, Tstat Set Up | 50370.8304 | 47684.439 | 47676.5253 | 48335.5891 | 48588.802 | 48768 | 0
0 | E360, Undersized System | 134976.8351 | 134919.792 | 134939.7228 | 134711.1169 | 134205.707 | 134697 | 0
0 | E400, Ec. Temp. Ctrl. | 41952.3595 | 41419.1334 | 41437.0125 | 40599.2192 | 0 | 41181 | 0
0 | E410, Ec. Comp. Lockout | 45676.6456 | 47658.6462 | 47659.8186 | 47103.2086 | 0 | 45585 | 0
0 | E420, Ec. ODB Limit | 50389.8247 | 49666.0881 | 50612.2149 | 49444.6391 | 0 | 49984 | 0
0 | E430, Ec. Enthalpy Ctrl. | 47863.3462 | 47731.335 | 47454.0624 | 46911.71 | 0 | 46143 | 0
0 | E440, Ec. Enthalpy Limit | 50876.0725 | 50592.5772 | 50492.0439 | 50001.0328 | 0 | 49785 | 0
0 | E500, Base w/ 0%OA | 45043.8 | 47649.8532 | 47646.0429 | 47357.4403 | 44874.225 | 47530 | 0
0 | E500 May-Sep | 34443.2344 | 36595.5867 | 36593.2419 | 36365.0866 | 34448.151 | 36480 | 0
0 | E510 May-Sep, High PLR | 77489.4321 | 82305.7041 | 82303.0662 | 81315.4422 | 77498.985 | 81563 | 0
0 | E520, EDB = 15°C | 45109.6141 | 48101.5203 | 48095.6583 | 47983.7484 | 44976.724 | 48059 | 0
0 | E522, EDB = 20°C | 45076.0312 | 47962.2978 | 47961.4185 | 47663.109 | 44924.113 | 47795 | 0
0 | E525, EDB = 35°C | 44979.0103 | 47217.5307 | 47213.4273 | 46796.3098 | 44775.105 | 47110 | 0
0 | E530, Dry Coil | 45045.848 | 46573.59 | 46570.0728 | 46988.3103 | 44874.225 | 47002 | 0
0 | E540, Dry, EDB = 15°C | 45111.8473 | 47022.9123 | 47019.102 | 47473.2183 | 44976.747 | 47460 | 0
0 | E545, Dry, EDB = 35°C | 44981.3517 | 46214.2494 | 46210.4391 | 46635.6951 | 44775.105 | 46668 | 0
0 | Latent Coil Load(kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 23765.119 | 21486.5748 | 21487.161 | 23163.9341 | 22535.143 | 23067 | 0
0 | E310, High Latent | 43085.7541 | 41093.7924 | 41099.3613 | 42282.0331 | 42110.836 | 42178 | 0
0 | E320, High Infiltration | 36932.4726 | 33659.3109 | 33746.3616 | 35683.1835 | 35132.592 | 34224 | 0
0 | E330, 100% OA | 41929.495 | 37418.9046 | 37665.6948 | 40736.8532 | 41063.373 | 40186 | 0
0 | E340, 50% OA, 50% Infl | 39695.3729 | 35974.2147 | 36112.5579 | 38742.1474 | 38295.624 | 38346 | 0
0 | E350, Tstat Set Up | 19017.1672 | 16051.9146 | 15958.1226 | 18258.9581 | 18271.394 | 18621 | 0
0 | E360, Undersized System | 27997.2274 | 24887.4141 | 24914.0862 | 27496.5697 | 26994.482 | 27470 | 0
0 | E400, Ec. Temp. Ctrl. | 26840.4626 | 23498.4132 | 23588.1018 | 25891.28 | 0 | 25717 | 0
0 | E410, Ec. Comp. Lockout | 22996.2083 | 19120.9647 | 19183.6881 | 20968.2133 | 0 | 20590 | 0
0 | E420, Ec. ODB Limit | 22219.4827 | 19944.8688 | 20269.9167 | 21803.4513 | 0 | 21855 | 0
0 | E430, Ec. Enthalpy Ctrl. | 21892.9657 | 19909.4037 | 19765.1985 | 21376.0444 | 0 | 21057 | 0
0 | E440, Ec. Enthalpy Limit | 22835.291 | 20787.5313 | 20689.0497 | 22361.0683 | 0 | 22244 | 0
0 | E500, Base w/ 0%OA | 18313.3062 | 18346.0083 | 18346.3014 | 18231.916 | 18231.141 | 18084 | 0
0 | E500 May-Sep | 14000.1964 | 14097.2307 | 14097.2307 | 13990.5875 | 13991.418 | 13877 | 0
0 | E510 May-Sep, High PLR | 31484.8778 | 31712.2476 | 31712.2476 | 31479.435 | 31479.856 | 31217 | 0
0 | E520, EDB = 15°C | 18311.9303 | 18469.6965 | 18469.6965 | 18229.5285 | 18235.133 | 18087 | 0
0 | E522, EDB = 20°C | 18313.1916 | 18410.7834 | 18410.4903 | 18230.7617 | 18233.151 | 18104 | 0
0 | E525, EDB = 35°C | 18313.9351 | 18181.5792 | 18181.5792 | 18232.0073 | 18226.509 | 18045 | 0
0 | E530, Dry Coil | 5.6053e-13 | 60.6717 | 60.6717 | 0.24183 | 1.186 | 0 | 0
0 | E540, Dry, EDB = 15°C | 0.97976 | 106.9815 | 106.9815 | 8.8672 | 3.09 | 2 | 0
0 | E545, Dry, EDB = 35°C | -3.3573e-14 | 25.4997 | 25.4997 | 3.5428e-12 | 0.004 | 0 | 0
0 | 0 | 0 | 0 | e300results.xls q:a125..m198; 07/19/04 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Various Annual Means (Humidity Ratio, Zone Relative Humidity) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 3.2491 | 3.2377 | 3.2374 | 3.2419 | 3.2264 | 3.23 | 0
0 | E310, High Latent | 3.4146 | 3.4175 | 3.4175 | 3.4071 | 3.3972 | 3.38 | 0
0 | E320, High Infiltration | 3.4199 | 3.458 | 3.4571 | 3.4172 | 3.406 | 3.39 | 0
0 | E330, 100% OA | 3.4907 | 3.4942 | 3.5364 | 3.5063 | 3.4973 | 3.46 | 0
0 | E340, 50% OA, 50% Infl | 3.4543 | 3.4773 | 3.4956 | 3.4624 | 3.4495 | 3.42 | 0
0 | E350, Tstat Set Up | 3.2489 | 3.2408 | 3.2354 | 3.2463 | 3.2289 | 3.23 | 0
0 | E360, Undersized System | 3.669 | 3.7006 | 3.7058 | 3.6797 | 3.6667 | 3.66 | 0
0 | E400, Ec. Temp. Ctrl. | 3.2503 | 3.2514 | 3.2519 | 3.2588 | 0 | 3.26 | 0
0 | E410, Ec. Comp. Lockout | 3.2395 | 3.2124 | 3.2107 | 3.2187 | 0 | 3.21 | 0
0 | E420, Ec. ODB Limit | 3.2261 | 3.2153 | 3.2175 | 3.2215 | 0 | 3.21 | 0
0 | E430, Ec. Enthalpy Ctrl. | 3.2208 | 3.213 | 3.2115 | 3.2176 | 0 | 3.21 | 0
0 | E440, Ec. Enthalpy Limit | 3.2313 | 3.2223 | 3.2219 | 3.2272 | 0 | 3.22 | 0
0 | E500, Base w/ 0%OA | 3.2041 | 3.2275 | 3.2265 | 3.208 | 3.192 | 3.2 | 0
0 | E500 May-Sep | 3.1418 | 3.1614 | 3.1616 | 3.1472 | 3.1324 | 3.14 | 0
0 | E510 May-Sep, High PLR | 3.5513 | 3.5774 | 3.5774 | 3.5554 | 3.5295 | 3.55 | 0
0 | E520, EDB = 15°C | 2.9011 | 2.9567 | 2.956 | 2.9205 | 2.8733 | 2.92 | 0
0 | E522, EDB = 20°C | 3.0581 | 3.0744 | 3.0728 | 3.0639 | 3.0363 | 3.07 | 0
0 | E525, EDB = 35°C | 3.4835 | 3.5309 | 3.528 | 3.4982 | 3.4796 | 3.41 | 0
0 | E530, Dry Coil | 2.9618 | 2.969 | 2.9694 | 2.9604 | 2.9156 | 2.98 | 0
0 | E540, Dry, EDB = 15°C | 2.668 | 2.6748 | 2.6752 | 2.6934 | 2.6403 | 2.69 | 0
0 | E545, Dry, EDB = 35°C | 3.2281 | 3.2333 | 3.2355 | 3.1632 | 3.1863 | 3.2 | 0
| IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
| 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
| E300 Base, 15% OA | 23.6243 | 24.0556 | 24.0556 | 24.0891 | 24.0816 | 23.99 | 0
| E310, High Latent | 23.7556 | 24.1111 | 24.0556 | 24.0915 | 24.0897 | 24.01 | 0
| E320, High Infiltration | 23.9005 | 24.3889 | 24.3889 | 24.2322 | 24.3274 | 24.53 | 0
| E330, 100% OA | 23.8797 | 24.2778 | 24.2778 | 24.2953 | 24.2955 | 24.18 | 0
| E340, 50% OA, 50% Infl | 23.8756 | 24.2778 | 24.2778 | 24.3105 | 24.3089 | 24.21 | 0
| E350, Tstat Set Up | 25.6595 | 26.1667 | 26.1667 | 26.2368 | 26.2686 | 26.15 | 0
| E360, Undersized System | 25.3649 | 25.6111 | 25.5556 | 25.4311 | 25.4809 | 25.37 | 0
| E400, Ec. Temp. Ctrl. | 24.1263 | 24.0556 | 24.0556 | 24.0905 | 0 | 23.99 | 0
| E410, Ec. Comp. Lockout | 24.1221 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0
| E420, Ec. ODB Limit | 23.9262 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0
| E430, Ec. Enthalpy Ctrl. | 23.9916 | 24.0556 | 24.0556 | 24.089 | 0 | 23.99 | 0
| E440, Ec. Enthalpy Limit | 23.9118 | 24.0556 | 24.0556 | 24.0891 | 0 | 23.99 | 0
| E500, Base w/ 0%OA | 20.2342 | 20.6667 | 20.5556 | 20.4037 | 21.0978 | 22.86 | 0
| E500 May-Sep | 24.5723 | 25 | 25 | 24.9827 | 25 | 25 | 0
| E510 May-Sep, High PLR | 25.8168 | 25.1111 | 25.1111 | 24.9597 | 25 | 25 | 0
| E520, EDB = 15°C | 13.5171 | 13.7778 | 13.7222 | 13.6259 | 14.1421 | 14.89 | 0
| E522, EDB = 20°C | 16.9456 | 17.2778 | 17.2222 | 17.0327 | 17.729 | 18.7 | 0
| E525, EDB = 35°C | 26.8443 | 27.3889 | 27.2778 | 27.1287 | 27.7709 | 30.69 | 0
| E530, Dry Coil | 20.0253 | 20.6111 | 20.5556 | 20.5951 | 21.0978 | 22.86 | 0
| E540, Dry, EDB = 15°C | 13.2893 | 13.7778 | 13.7222 | 13.8017 | 14.1406 | 14.98 | 0
| E545, Dry, EDB = 35°C | 26.6052 | 27.3333 | 27.2778 | 27.3219 | 27.7166 | 30.69 | 0
| Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
| 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
| E300 Base, 15% OA | 0.0090691 | 0.0092 | 0.0092 | 0.0091654 | 0.0091748 | 0.0092 | 0
| E310, High Latent | 0.011071 | 0.0113 | 0.0113 | 0.011154 | 0.011175 | 0.0111 | 0
| E320, High Infiltration | 0.009988 | 0.0101 | 0.0101 | 0.010037 | 0.010049 | 0.0099 | 0
| E330, 100% OA | 0.0097409 | 0.0099 | 0.0099 | 0.0098806 | 0.0098116 | 0.0099 | 0
| E340, 50% OA, 50% Infl | 0.0097914 | 0.0099 | 0.0099 | 0.0099021 | 0.0098683 | 0.0099 | 0
| E350, Tstat Set Up | 0.0097059 | 0.01 | 0.01 | 0.0097964 | 0.0097585 | 0.00977 | 0
| E360, Undersized System | 0.0084995 | 0.0087 | 0.0087 | 0.0086063 | 0.0085524 | 0.00858 | 0
| E400, Ec. Temp. Ctrl. | 0.0098011 | 0.01 | 0.01 | 0.010042 | 0 | 0.01 | 0
| E410, Ec. Comp. Lockout | 0.0097405 | 0.0095 | 0.0095 | 0.0094823 | 0 | 0.0095 | 0
| E420, Ec. ODB Limit | 0.0092639 | 0.0094 | 0.0094 | 0.0093476 | 0 | 0.0093 | 0
| E430, Ec. Enthalpy Ctrl. | 0.0093103 | 0.0094 | 0.0094 | 0.009387 | 0 | 0.0094 | 0
| E440, Ec. Enthalpy Limit | 0.0091578 | 0.0093 | 0.0093 | 0.0092307 | 0 | 0.0092 | 0
| E500, Base w/ 0%OA | 0.0097753 | 0 | 0 | 0.0091456 | 0.010218 | 0.0107 | 0
| E500 May-Sep | 0.011021 | 0.0114 | 0.0114 | 0.010999 | 0.011329 | 0.0109 | 0
| E510 May-Sep, High PLR | 0.011395 | 0.0114 | 0.0114 | 0.011008 | 0.011328 | 0.0109 | 0
| E520, EDB = 15°C | 0.0066924 | 0 | 0 | 0.0060157 | 0.0070234 | 0.00763 | 0
| E522, EDB = 20°C | 0.0081904 | 0 | 0 | 0.0074805 | 0.0085797 | 0.00901 | 0
| E525, EDB = 35°C | 0.013713 | 0 | 0 | 0.01338 | 0.01398 | 0.0151 | 0
| E530, Dry Coil | 0.0062265 | 0 | 0 | 0.0064848 | 0.0057975 | 0.00667 | 0
| E540, Dry, EDB = 15°C | 0.0044601 | 0 | 0 | 0.0043402 | 0.0038546 | 0.00463 | 0
| E545, Dry, EDB = 35°C | 0.0062265 | 0 | 0 | 0.0067479 | 0.006749 | 0.00722 | 0
| Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 48.6149 | 48.26 | 48.28 | 47.9447 | 47.8261 | 47.93 | 0
0 | E310, High Latent | 58.3307 | 58.51 | 58.53 | 57.961 | 57.841 | 57.8 | 0
0 | E320, High Infiltration | 52.0053 | 51.21 | 51.25 | 51.4531 | 51.1034 | 49.94 | 0
0 | E330, 100% OA | 50.8445 | 50.58 | 50.65 | 50.6065 | 50.0848 | 50.7 | 0
0 | E340, 50% OA, 50% Infl | 51.085 | 50.69 | 50.73 | 50.6474 | 50.2967 | 50.78 | 0
0 | E350, Tstat Set Up | 45.484 | 45.45 | 45.55 | 44.5942 | 44.3162 | 44.56 | 0
0 | E360, Undersized System | 41.0335 | 41.49 | 41.49 | 41.3637 | 40.871 | 41.21 | 0
0 | E400, Ec. Temp. Ctrl. | 50.7709 | 52.21 | 52.25 | 52.2746 | 0 | 52.01 | 0
0 | E410, Ec. Comp. Lockout | 50.4971 | 49.65 | 49.63 | 49.5161 | 0 | 49.75 | 0
0 | E420, Ec. ODB Limit | 48.7794 | 49.14 | 48.97 | 48.8495 | 0 | 48.76 | 0
0 | E430, Ec. Enthalpy Ctrl. | 48.8219 | 49.17 | 49.3 | 49.0444 | 0 | 49.17 | 0
0 | E440, Ec. Enthalpy Limit | 48.3298 | 48.46 | 48.57 | 48.2689 | 0 | 48.23 | 0
0 | E500, Base w/ 0%OA | 66.5261 | 0 | 0 | 57.9362 | 65.9419 | 63.73 | 0
0 | E500 May-Sep | 57.0476 | 57.47 | 57.47 | 55.6602 | 57.0722 | 55.13 | 0
0 | E510 May-Sep, High PLR | 54.7001 | 57.36 | 57.36 | 55.778 | 57.0615 | 55.24 | 0
0 | E520, EDB = 15°C | 69.8745 | 0 | 0 | 60.9282 | 70.2268 | 72.17 | 0
0 | E522, EDB = 20°C | 68.6774 | 0 | 0 | 59.7074 | 68.2314 | 68.11 | 0
0 | E525, EDB = 35°C | 61.4674 | 0 | 0 | 53.7167 | 60.1387 | 57.37 | 0
0 | E530, Dry Coil | 46.7299 | 0 | 0 | 47.5315 | 41.4516 | 39.6 | 0
0 | E540, Dry, EDB = 15°C | 48.521 | 0 | 0 | 46.1769 | 40.0509 | 43.82 | 0
0 | E545, Dry, EDB = 35°C | 36.6249 | 0 | 0 | 38.63 | 36.8747 | 29.2 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0 | f(ODB) Sensitivity E500 and E530, April 30 and June 25 |  |  |  |  | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TUD | NREL | NREL | GARD | UR | NRCan | Your
0 | Daily Consumptions | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E500 Apr30, Low ODB | 3892.9389 | 3975.4583 | 3975.1667 | 4019.3858 | 3901.0417 | 4073 | 0
0 | E500 Jun25, High ODB | 5044.9219 | 5204.3333 | 5204.0833 | 5244.3836 | 5066.5 | 5230 | 0
0 | E500 ODB Sensitivity | 1151.9831 | 1228.875 | 1228.9167 | 1224.9978 | 1165.4583 | 1157 | 0
0 | E530 Apr30, Low ODB | 3022.7732 | 3062 | 3061.7917 | 3131.8977 | 3091.5417 | 3144 | 0
0 | E530 Jun25, high ODB | 3894.1233 | 3978.2083 | 3978.0833 | 4090.8917 | 3934.625 | 4043 | 0
0 | E530 ODB Sensitivity | 871.3501 | 916.2083 | 916.2917 | 958.994 | 843.0833 | 899 | 0 |  | Note: Apr30, Jnue 25 compressor data not plotted
0 | E500 Apr30, Low ODB | 376.0762 | 389.125 | 389.0833 | 0 | 377.25 | 391 | 0 |  | Energy Consumption, Compressor (Wh,e) | [6 empty] | Your Software
0 | E500 Jun25, High ODB | 411.4946 | 426.3333 | 426.3333 | 0 | 411.3333 | 424 | 0 |  | E500Apr30 | 3014.619 | 3119.8333 | 3119.6667 | 0 | 3020.0417 | 3159 | 0
0 | E500 ODB Sensitivity | 35.4184 | 37.2083 | 37.25 | 0 | 34.0833 | 33 | 0 |  | E500Jun25 | 4083.8829 | 4263.5417 | 4263.4167 | 0 | 4105.9583 | 4239 | 0
0 | E530 Apr30, Low ODB | 304.5625 | 311.1667 | 311.125 | 0 | 305.3333 | 314 | 0 |  | Del E500 | 1069.2639 | 1143.7083 | 1143.75 | 0 | 1085.9167 | 1080 | 0
0 | E530 Jun25, high ODB | 332.2771 | 339.625 | 339.625 | 0 | 329.25 | 340 | 0 |  | E530Apr30 | 2311.4724 | 2390.0417 | 2389.9167 | 0 | 2378.4583 | 2411 | 0
0 | E530 ODB Sensitivity | 27.7146 | 28.4583 | 28.5 | 0 | 23.9167 | 26 | 0 |  | E530Jun25 | 3118.0954 | 3243 | 3242.9583 | 0 | 3165.5833 | 3248 | 0
0 | E500 Apr30, Low ODB | 502.2437 | 466.5 | 466.4167 | 517.8884 | 503.75 | 522 | 0 |  | Del E530 | 806.623 | 852.9583 | 853.0417 | 0 | 787.125 | 837 | 0
0 | E500 Jun25, High ODB | 549.5444 | 514.4583 | 514.3333 | 566.5961 | 549.2083 | 566 | 0
0 | E500 ODB Sensitivity | 47.3007 | 47.9583 | 47.9167 | 48.7076 | 45.4583 | 44 | 0
0 | E530 Apr30, Low ODB | 406.7383 | 360.7917 | 360.75 | 415.8771 | 407.75 | 419 | 0
0 | E530 Jun25, high ODB | 443.7507 | 395.5833 | 395.5 | 458.1925 | 439.7917 | 454 | 0
0 | E530 ODB Sensitivity | 37.0125 | 34.7917 | 34.75 | 42.3155 | 32.0417 | 35 | 0
0 | Sensible + Latent Coil Load (Wh,th) | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E500 Apr30, Low ODB | 13185.6871 | 13732.6998 | 13732.9074 | 13653.7633 | 13169.5417 | 13673 | 0
0 | E500 Jun25, High ODB | 13188.0504 | 13837.5319 | 13837.3853 | 13734.0071 | 13198.0833 | 13727 | 0
0 | E500 ODB Sensitivity | 2.3633 | 104.8321 | 104.4779 | 80.2437 | 28.5417 | 54 | 0
0 | E530 Apr30, Low ODB | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 0
0 | E530 Jun25, high ODB | 9376.2963 | 9760.7918 | 9760.6941 | 9843.2403 | 9387.625 | 9834 | 0
0 | E530 ODB Sensitivity | 23.1329 | 39.6418 | 39.2998 | 64.4987 | 22.1667 | 36 | 0
0 | E500 Apr30, Low ODB | 9374.7971 | 9924.8179 | 9925.0255 | 9849.8339 | 9365.4583 | 9902 | 0
0 | E500 Jun25, High ODB | 9377.6867 | 9981.2396 | 9981.0931 | 9923.758 | 9387.625 | 9946 | 0
0 | E500 ODB Sensitivity | 2.8896 | 56.4217 | 56.0676 | 73.9242 | 22.1667 | 44 | 0
0 | E530 Apr30, Low ODB | 9353.1633 | 9721.15 | 9721.3943 | 9778.7416 | 9365.4583 | 9798 | 0
0 | E530 Jun25, high ODB | 9376.2963 | 9760.7674 | 9760.6697 | 9843.2403 | 9387.625 | 9834 | 0
0 | E530 ODB Sensitivity | 23.1329 | 39.6174 | 39.2754 | 64.4987 | 22.1667 | 36 | 0
0 | E500 Apr30, Low ODB | 3810.89 | 3807.8819 | 3807.8819 | 3803.9295 | 3804.375 | 3770 | 0
0 | E500 Jun25, High ODB | 3810.3637 | 3856.2923 | 3856.2923 | 3810.249 | 3810.4167 | 3780 | 0
0 | E500 ODB Sensitivity | -0.52625 | 48.4104 | 48.4104 | 6.3196 | 6.0417 | 10 | 0
0 | E530 Apr30, Low ODB | -5.4771e-13 | 0 | 0 | 3.0182e-13 | 0 | 0 | 0
0 | E530 Jun25, high ODB | 7.2905e-13 | 0.024425 | 0.024425 | 3.5571e-13 | 0 | 0 | 0
0 | E530 ODB Sensitivity | 1.2768e-12 | 0.024425 | 0.024425 | 5.3896e-14 | 0 | 0 | 0
0
0
0
0
0
0
0
0
0
0
0
0
0 | f(ODB) Sensitivity E500 and E530, April 30 and June 25 |  |  |  |  | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | Your
0 | 0 | TUD | NREL | NREL | GARD | UR | NRCan | Software
0 | Humidity Ratio (kg/kg) | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E500 Apr30, Low ODB | 0.010675 | 0.011 | 0.011 | 0.010646 | 0.010938 | 0.016 | 0
0 | E500 Jun25, High ODB | 0.011168 | 0.0115 | 0.0115 | 0.011144 | 0.011479 | 0.011 | 0
0 | E500 ODB Sensitivity | 0.00049288 | 0.0005 | 0.0005 | 0.0004979 | 0.00054117 | -0.005 | 0
0 | E530 Apr30, Low ODB | 0.006208 | 0.0071 | 0.0071 | 0.006466 | 0.005485 | 0.00674 | 0
0 | E530 Jun25, high ODB | 0.006208 | 0.0078 | 0.0078 | 0.006466 | 0.005478 | 0.00674 | 0
0 | E530 ODB Sensitivity | 0 | 0.0007 | 0.0007 | 8.0838e-16 | -7e-06 | 0 | 0
0 | COP2 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E500 Apr30, Low ODB | 3.8448 | 3.9136 | 3.9139 | 3.8588 | 3.8372 | 3.85 | 0
0 | E500 Jun25, High ODB | 2.9313 | 2.9505 | 2.9506 | 2.9346 | 2.9213 | 2.94 | 0
0 | E500 ODB Sensitivity | -0.9135 | -0.9631 | -0.96334 | -0.92417 | -0.91589 | -0.91 | 0
0 | E530 Apr30, Low ODB | 3.5431 | 3.5988 | 3.5991 | 3.4048 | 3.4604 | 3.59 | 0
0 | E530 Jun25, high ODB | 2.7197 | 2.7245 | 2.7245 | 2.7405 | 2.69 | 2.74 | 0
0 | E530 ODB Sensitivity | -0.82341 | -0.87433 | -0.87464 | -0.66433 | -0.7704 | -0.85 | 0
0 | ODB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | E500 Apr30, Low ODB | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 0
0 | E500 Jun25, High ODB | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 0
0 | E500 ODB Sensitivity | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 0
0 | E530 Apr30, Low ODB | 16.7917 | 16.8333 | 16.8333 | 16.8146 | 16.8833 | 16.96 | 0
0 | E530 Jun25, high ODB | 29.5167 | 29.5 | 29.5 | 29.5167 | 29.5167 | 29.5 | 0
| E530 ODB Sensitivity | 12.725 | 12.6667 | 12.6667 | 12.7021 | 12.6333 | 12.54 | 0
| EDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
| E500 Apr30, Low ODB | 24.6411 | 24.9444 | 24.9444 | 24.982 | 25 | 25 | 0
| E500 Jun25, High ODB | 24.5478 | 25 | 25 | 24.9831 | 25 | 25 | 0
| E500 ODB Sensitivity | -0.093296 | 0.055556 | 0.055556 | 0.001091 | 0 | 0 | 0
| E530 Apr30, Low ODB | 24.365 | 24.9444 | 24.6667 | 25.0003 | 25 | 25 | 0
| E530 Jun25, high ODB | 24.3537 | 24.9444 | 24.9444 | 25.0003 | 25 | 25 | 0
| E530 ODB Sensitivity | -0.011358 | 0 | 0.27778 | 3.6047e-05 | 0 | 0 | 0

## Rdata
0
0
0
0
0
0
0 | Hourly Integrated Maxima (Total Cooling System Energy Consumption and Total Coil Load) | 0
0 | Energy Consumption, Compressor + Both Fans (Wh,e) | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 11626.0371 | 11564 | 11602 | 11995.7089 | 11932 | 11548 | 0
0 | E310, High Latent | 12594.4016 | 12583 | 12595 | 12572.0793 | 12653 | 12162 | 0
0 | E320, High Infiltration | 13028.1986 | 12916 | 12981 | 12988.8392 | 13104 | 12875 | 0
0 | E330, 100% OA | 13346.701 | 13212 | 13407 | 13356.2349 | 13467 | 13335 | 0
0 | E340, 50% OA, 50% Infl | 13180.9018 | 13158 | 13190 | 13174.9258 | 13277 | 13101 | 0
0 | E350, Tstat Set Up | 11626.889 | 11654 | 11602 | 11995.7017 | 11932 | 11546 | 0
0 | E360, Undersized System | 12769.5022 | 12736 | 12726 | 12776.4285 | 12863 | 12762 | 0
0 | E400, Ec. Temp. Ctrl. | 11627.8677 | 11564 | 11677 | 11995.6974 | 0 | 11519 | 0
0 | E410, Ec. Comp. Lockout | 11627.8677 | 11564 | 11602 | 11995.7089 | 0 | 11549 | 0
0 | E420, Ec. ODB Limit | 11626.0371 | 11564 | 11602 | 11995.7089 | 0 | 11548 | 0
0 | E430, Ec. Enthalpy Ctrl. | 11626.0371 | 11564 | 11602 | 11995.7089 | 0 | 11548 | 0
0 | E440, Ec. Enthalpy Limit | 11626.0371 | 11564 | 11602 | 11995.7089 | 0 | 11461 | 0
0 | E500, Base w/ 0%OA | 10166.4831 | 10431 | 10425 | 10438.5175 | 10177 | 10274 | 0
0 | E510 High PLR | 11204.8968 | 11590 | 11587 | 11450.7514 | 11186 | 11344 | 0
0 | E520, EDB = 15°C | 11035.3898 | 10989 | 11014 | 11261.8296 | 11044 | 10684 | 0
0 | E522, EDB = 20°C | 10430.7791 | 10972 | 10966 | 10902.675 | 10639 | 10747 | 0
0 | E525, EDB = 35°C | 9366.7481 | 9538 | 9531 | 9588.2506 | 9419 | 9585 | 0
0 | E530, Dry Coil | 8028.3285 | 8059 | 8055 | 8293.041 | 7992 | 8089 | 0
0 | E540, Dry, EDB = 15°C | 8698.9562 | 8943 | 8939 | 9076.4428 | 8846 | 8985 | 0
0 | E545, Dry, EDB = 35°C | 7204.827 | 7350 | 7346 | 7767.989 | 7351 | 7471 | 0
0 | Sensible Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 23277.4 | 23203 | 23205 | 23463.1755 | 23457 | 22908 | 0
0 | E310, High Latent | 23094.3 | 23080 | 23119 | 23145.0651 | 23078 | 22649 | 0
0 | E320, High Infiltration | 31315.6 | 31119 | 31072 | 31528.7254 | 31134 | 30967 | 0
0 | E330, 100% OA | 33226.1 | 33410 | 34490 | 34692.1931 | 33997 | 33421 | 0
0 | E340, 50% OA, 50% Infl | 32828.9 | 32086 | 32086 | 32737.1011 | 32940 | 32180 | 0
0 | E350, Tstat Set Up | 23277.5 | 23203 | 23205 | 23463.136 | 23457 | 22876 | 0
0 | E360, Undersized System | 32060.7 | 32111 | 32065 | 32409.2976 | 31981 | 32179 | 0
0 | E400, Ec. Temp. Ctrl. | 23277.5 | 23203 | 23205 | 23463.1222 | 0 | 22877 | 0
0 | E410, Ec. Comp. Lockout | 23265.7 | 23203 | 23205 | 0 | 0 | 22893 | 0
0 | E420, Ec. ODB Limit | 23277.4 | 23203 | 23205 | 23463.1755 | 0 | 22893 | 0
0 | E430, Ec. Enthalpy Ctrl. | 23277.4 | 23203 | 23205 | 23463.1755 | 0 | 22893 | 0
0 | E440, Ec. Enthalpy Limit | 23277.4 | 23203 | 23205 | 23463.1755 | 0 | 22875 | 0
0 | E500, Base w/ 0%OA | 19549.2 | 20009 | 20008 | 19795.9105 | 18776 | 19818 | 0
0 | E510 High PLR | 21729.2 | 22513 | 22513 | 22227.967 | 21121 | 22269 | 0
0 | E520, EDB = 15°C | 19415.9 | 20159 | 20154 | 20012.5751 | 18969 | 20378 | 0
0 | E522, EDB = 20°C | 19488.8 | 20137 | 20135 | 19901.8714 | 18785 | 19920 | 0
0 | E525, EDB = 35°C | 19702.7 | 19850 | 19850 | 19599.0538 | 18759 | 19661 | 0
0 | E530, Dry Coil | 19834.1 | 19576 | 19575 | 19656.1402 | 18776 | 19626 | 0
0 | E540, Dry, EDB = 15°C | 19575 | 19766 | 19766 | 19812.465 | 18794 | 19799 | 0
0 | E545, Dry, EDB = 35°C | 20075.2 | 19475 | 19474 | 19538.7609 | 18759 | 19497 | 0
0 | Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 9635.7 | 9304 | 9394 | 10595.085 | 10375 | 10392 | 0
0 | E310, High Latent | 15907 | 15139 | 15270 | 16644.3073 | 16112 | 16077 | 0
0 | E320, High Infiltration | 23147.3 | 31497 | 31503 | 22756.175 | 21697 | 21929 | 0
0 | E330, 100% OA | 27825.2 | 26941 | 40809 | 27596.7005 | 28184 | 27488 | 0
0 | E340, 50% OA, 50% Infl | 24848.3 | 30451 | 36011 | 24435.7652 | 24225 | 23794 | 0
0 | E350, Tstat Set Up | 9751.26 | 9303 | 9393 | 10595.6426 | 10755 | 11603 | 0
0 | E360, Undersized System | 9275.16 | 10026 | 10336 | 8907.2199 | 8859 | 8934 | 0
0 | E400, Ec. Temp. Ctrl. | 27075.3 | 25578 | 32396 | 26767.6767 | 0 | 26645 | 0
0 | E410, Ec. Comp. Lockout | 11138.9 | 9304 | 9391 | 0 | 0 | 10377 | 0
0 | E420, Ec. ODB Limit | 9751.04 | 9304 | 9394 | 10595.085 | 0 | 10394 | 0
0 | E430, Ec. Enthalpy Ctrl. | 9635.7 | 11105 | 11101 | 11375.3248 | 0 | 10394 | 0
0 | E440, Ec. Enthalpy Limit | 9635.7 | 9304 | 9391 | 10595.085 | 0 | 10139 | 0
0 | E500, Base w/ 0%OA | 7965.46 | 7733 | 7733 | 7908.9572 | 7805 | 7762 | 0
0 | E510 High PLR | 8892.56 | 8723 | 8723 | 9041.0375 | 8850 | 8874 | 0
0 | E520, EDB = 15°C | 7913.7 | 7785 | 7785 | 7785.2261 | 7726 | 7964 | 0
0 | E522, EDB = 20°C | 7906.7 | 7760 | 7760 | 7850.1656 | 7743 | 7745 | 0
0 | E525, EDB = 35°C | 8037.07 | 7663 | 7663 | 8006.3955 | 7938 | 7820 | 0
0 | E530, Dry Coil | 1.6431e-11 | 0 | 0 | 110.1783 | 179 | 35.9 | 0
0 | E540, Dry, EDB = 15°C | 627.186 | 0 | 0 | 1636.359 | 845 | 1181 | 0
0 | E545, Dry, EDB = 35°C | 1.8119e-11 | 0 | 0 | 8.2784e-12 | 4 | 0 | 0
0 | Senstible + Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 32174.05 | 31401 | 31455 | 33057.4738 | 32502 | 32072 | 0
0 | E310, High Latent | 37328 | 36750 | 37033 | 37372.5209 | 37261 | 36991 | 0
0 | E320, High Infiltration | 40317.6 | 53813 | 53823 | 40097.0154 | 39904 | 39920 | 0
0 | E330, 100% OA | 43492 | 43628 | 64572 | 43597.9449 | 43978 | 42415 | 0
0 | E340, 50% OA, 50% Infl | 41651.7 | 50819 | 59549 | 41608.4737 | 41366 | 41132 | 0
0 | E350, Tstat Set Up | 32091.73 | 31401 | 31454 | 33057.4487 | 32502 | 32077 | 0
0 | E360, Undersized System | 38857.16 | 40613 | 41019 | 38691.4863 | 38322 | 38451 | 0
0 | E400, Ec. Temp. Ctrl. | 41178.6 | 40543 | 49838 | 41112.206 | 0 | 40774 | 0
0 | E410, Ec. Comp. Lockout | 32091.73 | 31401 | 31455 | 0 | 0 | 32073 | 0
0 | E420, Ec. ODB Limit | 32174.05 | 31401 | 31455 | 33057.4738 | 0 | 32072 | 0
0 | E430, Ec. Enthalpy Ctrl. | 32174.05 | 31401 | 31455 | 33057.4738 | 0 | 32072 | 0
0 | E440, Ec. Enthalpy Limit | 32174.05 | 31401 | 31455 | 33057.4738 | 0 | 31777 | 0
0 | E500, Base w/ 0%OA | 27485.51 | 27707 | 27706 | 27656.4201 | 26567 | 27555 | 0
0 | E510 High PLR | 30593.05 | 31188 | 31188 | 31194.5493 | 29948 | 31097 | 0
0 | E520, EDB = 15°C | 27329.6 | 27878 | 27878 | 27731.0711 | 26675 | 28343 | 0
0 | E522, EDB = 20°C | 27383.59 | 27868 | 27866 | 27698.162 | 26514 | 27636 | 0
0 | E525, EDB = 35°C | 27739.77 | 27466 | 27466 | 27564.3415 | 26683 | 27462 | 0
0 | E530, Dry Coil | 19834.1 | 19576 | 19575 | 19656.1402 | 18776 | 19626 | 0
0 | E540, Dry, EDB = 15°C | 19575 | 19766 | 19766 | 19812.465 | 18794 | 19799 | 0
0 | E545, Dry, EDB = 35°C | 20075.2 | 19475 | 19474 | 19538.7609 | 18764 | 19497 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
#REF! | #REF! | [6 empty] | #REF!
#REF! | #REF! | [6 empty] | #REF!
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
0 | 0 | [6 empty] | 0
0 | Hourly Integrated Maxima and Minima (COP2) | [6 empty] | 0
0 | Maximum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 4.1683 | 3.869 | 3.857 | 3.9232 | 3.8706 | 3.88 | 0
0 | E310, High Latent | 4.1433 | 4.141 | 4.128 | 4.1954 | 4.1276 | 4.12 | 0
0 | E320, High Infiltration | 4.1683 | 5.143 | 4.967 | 3.9648 | 3.9433 | 4.38 | 0
0 | E330, 100% OA | 4.1683 | 4.109 | 5.595 | 4.0962 | 4.1219 | 4.05 | 0
0 | E340, 50% OA, 50% Infl | 4.1683 | 4.621 | 5.339 | 4.0147 | 4.0172 | 3.95 | 0
0 | E350, Tstat Set Up | 4.1683 | 3.889 | 3.863 | 4.3453 | 3.9321 | 3.88 | 0
0 | E360, Undersized System | 4.401 | 4.428 | 4.427 | 4.4308 | 4.432 | 4.44 | 0
0 | E400, Ec. Temp. Ctrl. | 4.0769 | 4.088 | 4.776 | 4.0961 | 0 | 4.05 | 0
0 | E410, Ec. Comp. Lockout | 3.8879 | 3.903 | 3.855 | 0 | 0 | 3.84 | 0
0 | E420, Ec. ODB Limit | 3.7813 | 3.807 | 3.759 | 3.8446 | 0 | 3.94 | 0
0 | E430, Ec. Enthalpy Ctrl. | 3.7813 | 3.805 | 3.759 | 3.8044 | 0 | 3.93 | 0
0 | E440, Ec. Enthalpy Limit | 3.8835 | 3.774 | 3.759 | 3.8044 | 0 | 3.81 | 0
0 | E500, Base w/ 0%OA | 4.2751 | 7.367 | 5.301 | 4.2343 | 4.1846 | 4.14 | 0
0 | E510 High PLR | 4.6925 | 7.367 | 5.301 | 4.7069 | 4.6896 | 4.53 | 0
0 | E520, EDB = 15°C | 3.8137 | 4.896 | 4.652 | 3.838 | 3.8017 | 3.84 | 0
0 | E522, EDB = 20°C | 3.9855 | 6.233 | 5.678 | 4.0074 | 3.9858 | 4 | 0
0 | E525, EDB = 35°C | 4.7178 | 6.325 | 6.031 | 4.6776 | 4.6381 | 4.4 | 0
0 | E530, Dry Coil | 4.0061 | 3.981 | 3.85 | 3.9202 | 3.84 | 3.88 | 0
0 | E540, Dry, EDB = 15°C | 3.456 | 3.456 | 3.455 | 3.5169 | 3.6667 | 3.69 | 0
0 | E545, Dry, EDB = 35°C | 4.2505 | 4.275 | 4.428 | 4.2157 | 4.1565 | 4.17 | 0
0 | Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 2.7931 | 2.798 | 2.801 | 2.7744 | 2.7856 | 2.81 | 0
0 | E310, High Latent | 2.8652 | 2.85 | 2.851 | 2.8671 | 2.8726 | 2.87 | 0
0 | E320, High Infiltration | 2.8252 | 2.801 | 2.805 | 2.8231 | 2.8145 | 2.83 | 0
0 | E330, 100% OA | 2.8252 | 2.798 | 2.801 | 2.8286 | 2.8233 | 2.84 | 0
0 | E340, 50% OA, 50% Infl | 2.8252 | 2.798 | 2.801 | 2.8286 | 2.8233 | 2.84 | 0
0 | E350, Tstat Set Up | 2.7904 | 2.798 | 2.801 | 2.7744 | 2.7859 | 2.81 | 0
0 | E360, Undersized System | 2.8252 | 2.799 | 2.801 | 2.8286 | 2.8233 | 2.84 | 0
0 | E400, Ec. Temp. Ctrl. | 2.7819 | 2.734 | 2.735 | 2.7744 | 0 | 2.81 | 0
0 | E410, Ec. Comp. Lockout | 2.7858 | 2.798 | 2.801 | 0 | 0 | 2.81 | 0
0 | E420, Ec. ODB Limit | 2.7931 | 2.798 | 2.801 | 2.7744 | 0 | 2.81 | 0
0 | E430, Ec. Enthalpy Ctrl. | 2.7711 | 2.734 | 2.735 | 2.7744 | 0 | 2.81 | 0
0 | E440, Ec. Enthalpy Limit | 2.7825 | 2.734 | 2.735 | 2.7744 | 0 | 2.81 | 0
0 | E500, Base w/ 0%OA | 2.6852 | 2.693 | 2.652 | 2.6947 | 2.6665 | 2.71 | 0
0 | E510 High PLR | 2.888 | 2.817 | 2.652 | 2.8993 | 2.8817 | 2.9 | 0
0 | E520, EDB = 15°C | 2.4417 | 2.463 | 2.394 | 2.4618 | 2.3333 | 2.47 | 0
0 | E522, EDB = 20°C | 2.5689 | 2.572 | 2.562 | 2.5777 | 2.4286 | 2.59 | 0
0 | E525, EDB = 35°C | 2.9111 | 2.939 | 2.814 | 2.9333 | 2.8941 | 2.9 | 0
0 | E530, Dry Coil | 2.5013 | 2.495 | 2.498 | 2.4945 | 2.4733 | 2.52 | 0
0 | E540, Dry, EDB = 15°C | 2.253 | 2.261 | 2.262 | 2.2794 | 2.1429 | 2.28 | 0
0 | E545, Dry, EDB = 35°C | 2.7325 | 2.72 | 2.722 | 2.6585 | 2.692 | 2.72 | 0
0 | Maximum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 26.1999 | 25.11 | 25.11 | 25.0033 | 25.05 | 26.19 | 0
0 | E310, High Latent | 27.0778 | 26.89 | 26.72 | 26.5567 | 26.62 | 27.19 | 0
0 | E320, High Infiltration | 32.3604 | 31.61 | 31.5 | 31.844 | 32.32 | 31.65 | 0
0 | E330, 100% OA | 32.2321 | 31.72 | 32 | 31.4963 | 31.9 | 31.3 | 0
0 | E340, 50% OA, 50% Infl | 32.3066 | 31.61 | 31.56 | 31.7451 | 32.15 | 31.58 | 0
0 | E350, Tstat Set Up | 34.5841 | 34.94 | 34.94 | 35.0021 | 35 | 35 | 0
0 | E360, Undersized System | 33.7585 | 32.78 | 32.56 | 32.8198 | 33 | 33.13 | 0
0 | E400, Ec. Temp. Ctrl. | 27.1148 | 27.56 | 28.83 | 26.9032 | 0 | 26.04 | 0
0 | E410, Ec. Comp. Lockout | 26.8256 | 25.11 | 25.11 | 0 | 0 | 26.19 | 0
0 | E420, Ec. ODB Limit | 26.1999 | 25.11 | 25.11 | 25.0033 | 0 | 26.23 | 0
0 | E430, Ec. Enthalpy Ctrl. | 27.1992 | 25.11 | 25.11 | 25.0038 | 0 | 26.45 | 0
0 | E440, Ec. Enthalpy Limit | 27.0452 | 25.11 | 25.11 | 25.0038 | 0 | 26.26 | 0
0 | E500, Base w/ 0%OA | 25.8054 | 25.11 | 25.11 | 25.0017 | 25.02 | 25 | 0
0 | E510 High PLR | 26.1003 | 25.11 | 25.11 | 25.0017 | 25.02 | 25 | 0
0 | E520, EDB = 15°C | 16.1232 | 16.11 | 15.94 | 15.2669 | 15.98 | 18.62 | 0
0 | E522, EDB = 20°C | 21.0091 | 20.11 | 20.11 | 20.0027 | 20.05 | 20.93 | 0
0 | E525, EDB = 35°C | 36.08 | 35.06 | 35.06 | 34.9964 | 35 | 35 | 0
0 | E530, Dry Coil | 26.116 | 25.06 | 25.06 | 25.0027 | 25.02 | 25 | 0
0 | E540, Dry, EDB = 15°C | 16.1465 | 15.11 | 15.11 | 15.0028 | 15.05 | 15 | 0
0 | E545, Dry, EDB = 35°C | 35.6715 | 35 | 35 | 35.0003 | 35 | 35 | 0
0 | Minimum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 7.93 | 8.89 | 8.83 | 8.7263 | 8 | 6.99 | 0
0 | E310, High Latent | 7.93 | 8.89 | 8.83 | 8.7262 | 8 | 6.99 | 0
0 | E320, High Infiltration | 7.93 | 10.83 | 10.78 | 7.7562 | 8 | 6.99 | 0
0 | E330, 100% OA | 7.93 | 8.89 | 8.83 | 8.7247 | 8 | 6.99 | 0
0 | E340, 50% OA, 50% Infl | 7.93 | 8.89 | 8.83 | 8.7247 | 8 | 6.99 | 0
0 | E350, Tstat Set Up | 7.93 | 8.89 | 8.83 | 8.7263 | 8 | 6.99 | 0
0 | E360, Undersized System | 7.93 | 8.89 | 8.83 | 8.7265 | 8 | 6.99 | 0
0 | E400, Ec. Temp. Ctrl. | 7.93 | 8.89 | 8.83 | 8.7263 | 0 | 6.99 | 0
0 | E410, Ec. Comp. Lockout | 7.93 | 8.89 | 8.83 | 0 | 0 | 6.99 | 0
0 | E420, Ec. ODB Limit | 7.93 | 8.89 | 8.83 | 8.7263 | 0 | 6.99 | 0
0 | E430, Ec. Enthalpy Ctrl. | 7.93 | 8.89 | 8.83 | 8.7263 | 0 | 6.99 | 0
0 | E440, Ec. Enthalpy Limit | 7.93 | 8.89 | 8.83 | 8.7263 | 0 | 7 | 0
0 | E500, Base w/ 0%OA | 8.427 | 8.17 | 7.94 | 8.8363 | 8.54 | 24.04 | 0
0 | E510 High PLR | 8.427 | 8.17 | 7.94 | 8.8363 | 8.54 | 24.04 | 0
0 | E520, EDB = 15°C | 8.3053 | 8.11 | 7.89 | 8.733 | 8.51 | 13.57 | 0
0 | E522, EDB = 20°C | 8.4141 | 8.17 | 7.94 | 8.7911 | 8.54 | 15.98 | 0
0 | E525, EDB = 35°C | 8.4442 | 8.17 | 7.94 | 8.9123 | 8.54 | 33.01 | 0
0 | E530, Dry Coil | 8.4215 | 8.17 | 7.94 | 8.9817 | 8.54 | 24.04 | 0
0 | E540, Dry, EDB = 15°C | 8.2278 | 8.11 | 7.89 | 8.8775 | 8.51 | 14.95 | 0
0 | E545, Dry, EDB = 35°C | 8.4486 | 8.17 | 7.94 | 9.0584 | 8.54 | 33.01 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Hourly Integrated Maxima and Minima (Zone Humidity Ratio) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | Maximum Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 0.013284 | 0.0138 | 0.0137 | 0.01352 | 0.013457 | 0.0134 | 0
0 | E310, High Latent | 0.01575 | 0.0188 | 0.0189 | 0.015502 | 0.015432 | 0.0157 | 0
0 | E320, High Infiltration | 0.018017 | 0.0177 | 0.0176 | 0.017703 | 0.017547 | 0.0177 | 0
0 | E330, 100% OA | 0.017651 | 0.0178 | 0.0177 | 0.017823 | 0.017045 | 0.0177 | 0
0 | E340, 50% OA, 50% Infl | 0.017871 | 0.0177 | 0.0174 | 0.017707 | 0.017272 | 0.0177 | 0
0 | E350, Tstat Set Up | 0.016758 | 0.0199 | 0.0199 | 0.016945 | 0.016479 | 0.0166 | 0
0 | E360, Undersized System | 0.013433 | 0.0138 | 0.0137 | 0.01352 | 0.013457 | 0.0134 | 0
0 | E400, Ec. Temp. Ctrl. | 0.016944 | 0.017 | 0.017 | 0.016893 | 0 | 0.0173 | 0
0 | E410, Ec. Comp. Lockout | 0.016835 | 0.0169 | 0.0169 | 0 | 0 | 0.0173 | 0
0 | E420, Ec. ODB Limit | 0.014297 | 0.0147 | 0.0141 | 0.014607 | 0 | 0.0147 | 0
0 | E430, Ec. Enthalpy Ctrl. | 0.016231 | 0.0156 | 0.0156 | 0.016146 | 0 | 0.0158 | 0
0 | E440, Ec. Enthalpy Limit | 0.013313 | 0.0138 | 0.0137 | 0.01352 | 0 | 0.0134 | 0
0 | E500, Base w/ 0%OA | 0.01172 | 0.0119 | 0.0118 | 0.01138 | 0.011713 | 0.0115 | 0
0 | E510 High PLR | 0.011871 | 0.0119 | 0.0119 | 0.01139 | 0.011716 | 0.0115 | 0
0 | E520, EDB = 15°C | 0.0075403 | 0.0077 | 0.0078 | 0.007104 | 0.007566 | 0.0106 | 0
0 | E522, EDB = 20°C | 0.0094264 | 0.0095 | 0.0138 | 0.0089745 | 0.009398 | 0.0107 | 0
0 | E525, EDB = 35°C | 0.017932 | 0.018 | 0.018 | 0.017848 | 0.017626 | 0.0173 | 0
0 | E530, Dry Coil | 0.0069892 | 0.0081 | 0.0081 | 0.0067904 | 0.005491 | 0.00677 | 0
0 | E540, Dry, EDB = 15°C | 0.006084 | 0.005 | 0.0063 | 0.0067904 | 0.003256 | 0.00634 | 0
0 | E545, Dry, EDB = 35°C | 0.0069892 | 0.0122 | 0.0122 | 0.0067904 | 0.006689 | 0.00763 | 0
0 | Minimum Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0.001968 | 0.00197 | 0
0 | E310, High Latent | 0.0018769 | 0.0017 | 0.0017 | 0.0019435 | 0.002019 | 0.00196 | 0
0 | E320, High Infiltration | 0.0018769 | 0.0017 | 0.0017 | 0.0019351 | 0.001968 | 0.00197 | 0
0 | E330, 100% OA | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0.001968 | 0.00197 | 0
0 | E340, 50% OA, 50% Infl | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0.001968 | 0.00197 | 0
0 | E350, Tstat Set Up | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0.001968 | 0.00197 | 0
0 | E360, Undersized System | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0.001968 | 0.00197 | 0
0 | E400, Ec. Temp. Ctrl. | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0 | 0.00197 | 0
0 | E410, Ec. Comp. Lockout | 0.0018769 | 0.0017 | 0.0017 | 0 | 0 | 0.00197 | 0
0 | E420, Ec. ODB Limit | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0 | 0.00197 | 0
0 | E430, Ec. Enthalpy Ctrl. | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0 | 0.00197 | 0
0 | E440, Ec. Enthalpy Limit | 0.0018769 | 0.0017 | 0.0017 | 0.0019292 | 0 | 0.00197 | 0
0 | E500, Base w/ 0%OA | 0.0068276 | 0 | 0 | 0.0069608 | 0.006908 | 0.0103 | 0
0 | E510 High PLR | 0.0068276 | 0 | 0 | 0.0069608 | 0.006908 | 0.0105 | 0
0 | E520, EDB = 15°C | 0.006103 | 0 | 0 | 0.006466 | 0.006525 | 0.00657 | 0
0 | E522, EDB = 20°C | 0.0068215 | 0 | 0 | 0.0069388 | 0.006908 | 0.00783 | 0
0 | E525, EDB = 35°C | 0.0068356 | 0 | 0 | 0.006998 | 0.006909 | 0.0154 | 0
0 | E530, Dry Coil | 0.006208 | 0 | 0 | 0.0064432 | 0.005454 | 0.00663 | 0
0 | E540, Dry, EDB = 15°C | 0.0041096 | 0 | 0 | 0.0038106 | 0.003253 | 0.0042 | 0
0 | E545, Dry, EDB = 35°C | 0.006208 | 0 | 0 | 0.0067904 | 0.006685 | 0.007 | 0
0 | Maximum Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 68.7892 | 69.35 | 68.85 | 67.7762 | 68 | 67.44 | 0
0 | E310, High Latent | 77.7029 | 100.18 | 100.7 | 77.9255 | 77 | 78.19 | 0
0 | E320, High Infiltration | 81.8358 | 83.41 | 83.67 | 82.7149 | 83 | 81.88 | 0
0 | E330, 100% OA | 76.6591 | 78.46 | 77.94 | 76.6386 | 76 | 78.7 | 0
0 | E340, 50% OA, 50% Infl | 79.9293 | 81.37 | 81.26 | 80.5452 | 80 | 80.25 | 0
0 | E350, Tstat Set Up | 68.7892 | 81.12 | 81.12 | 67.7762 | 70 | 72.65 | 0
0 | E360, Undersized System | 68.7892 | 69.35 | 68.85 | 67.776 | 68 | 67.44 | 0
0 | E400, Ec. Temp. Ctrl. | 83.7534 | 85.57 | 85.57 | 84.6321 | 0 | 86.31 | 0
0 | E410, Ec. Comp. Lockout | 83.2247 | 84.79 | 84.79 | 0 | 0 | 86.18 | 0
0 | E420, Ec. ODB Limit | 70.8411 | 74.51 | 71.53 | 73.2771 | 0 | 73.85 | 0
0 | E430, Ec. Enthalpy Ctrl. | 80.7087 | 78.43 | 78.43 | 80.716 | 0 | 78.94 | 0
0 | E440, Ec. Enthalpy Limit | 68.7242 | 69.35 | 68.85 | 67.7762 | 0 | 67.51 | 0
0 | E500, Base w/ 0%OA | 100 | 0 | 0 | 100 | 100 | 60.08 | 0
0 | E510 High PLR | 100 | 0 | 0 | 100 | 100 | 57.51 | 0
0 | E520, EDB = 15°C | 90.2299 | 0 | 0 | 93.6042 | 95 | 71.77 | 0
0 | E522, EDB = 20°C | 100 | 0 | 0 | 100 | 100 | 71.32 | 0
0 | E525, EDB = 35°C | 100 | 0 | 0 | 100 | 100 | 51.12 | 0
0 | E530, Dry Coil | 91.0445 | 0 | 0 | 91.698 | 79 | 36.01 | 0
0 | E540, Dry, EDB = 15°C | 61.275 | 0 | 0 | 54.8557 | 47 | 39.96 | 0
0 | E545, Dry, EDB = 35°C | 90.8772 | 0 | 0 | 96.074 | 97 | 24.14 | 0
0 | Minimum Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | 0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
0 | E300 Base, 15% OA | 13.3312 | 11.97 | 11.97 | 14.3878 | 15 | 14.94 | 0
0 | E310, High Latent | 13.3898 | 11.97 | 11.97 | 15.471 | 16 | 15.93 | 0
0 | E320, High Infiltration | 13.3312 | 11.97 | 11.97 | 14.7974 | 15 | 12.92 | 0
0 | E330, 100% OA | 13.3312 | 11.97 | 11.97 | 14.3879 | 15 | 14.94 | 0
0 | E340, 50% OA, 50% Infl | 13.3312 | 11.97 | 11.97 | 14.3879 | 15 | 14.94 | 0
0 | E350, Tstat Set Up | 13.3312 | 11.97 | 11.97 | 14.3878 | 15 | 14.94 | 0
0 | E360, Undersized System | 13.3312 | 11.97 | 11.97 | 14.3878 | 15 | 14.94 | 0
0 | E400, Ec. Temp. Ctrl. | 13.209 | 11.97 | 11.97 | 13.9255 | 0 | 14.57 | 0
0 | E410, Ec. Comp. Lockout | 13.2091 | 11.97 | 11.97 | 0 | 0 | 14.58 | 0
0 | E420, Ec. ODB Limit | 13.2099 | 11.97 | 11.97 | 13.9256 | 0 | 14.59 | 0
0 | E430, Ec. Enthalpy Ctrl. | 13.2078 | 11.97 | 11.97 | 13.9255 | 0 | 14.58 | 0
0 | E440, Ec. Enthalpy Limit | 13.2069 | 11.97 | 11.97 | 13.9255 | 0 | 14.54 | 0
0 | E500, Base w/ 0%OA | 53.4054 | 0 | 0 | 53.4256 | 54 | 52.83 | 0
0 | E510 High PLR | 52.0879 | 0 | 0 | 53.5323 | 54 | 53.15 | 0
0 | E520, EDB = 15°C | 61.2679 | 0 | 0 | 61.1938 | 61 | 61.9 | 0
0 | E522, EDB = 20°C | 58.5054 | 0 | 0 | 57.8308 | 60 | 57.97 | 0
0 | E525, EDB = 35°C | 45.5284 | 0 | 0 | 46.1063 | 44 | 44.4 | 0
0 | E530, Dry Coil | 29.5934 | 0 | 0 | 32.5613 | 28 | 33.68 | 0
0 | E540, Dry, EDB = 15°C | 36.4749 | 0 | 0 | 35.8475 | 31 | 39.74 | 0
0 | E545, Dry, EDB = 35°C | 17.1244 | 0 | 0 | 19.2467 | 19 | 20.14 | 0

## Sdata
Energy Consumption
Compressor + OD fan | [7 empty] | Condenser (OD) fan | [6 empty] | Compressor
Hour | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software | Hour | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 2312.3023 | 2134 | 2131 | 2153.3475 | 2123 | 2183.748 | 0 | 256.5326 | 237 | 237 | Note 1 | 237 | 240.938 | 0 | 1 | 2055.7697 | 1897 | 1894 |  | 1886 | 1942.81 | 0
2 | 2310.1977 | 2181 | 2182 | 2166.9933 | 2208 | 2191.634 | 0 | 256.5271 | 240 | 241 | Note 1 | 244 | 241.104 | 0 | 2 | 2053.6706 | 1941 | 1941 |  | 1964 | 1950.53 | 0
3 | 2311.0279 | 2134 | 2131 | 2147.8736 | 2117 | 2139.18 | 0 | 256.5356 | 237 | 237 | Note 1 | 236 | 236.85 | 0 | 3 | 2054.4923 | 1897 | 1894 |  | 1881 | 1902.33 | 0
4 | 2059.6681 | 2128 | 2126 | 2109.7575 | 2114 | 2076.548 | 0 | 229.5857 | 237 | 236 | Note 1 | 236 | 231.118 | 0 | 4 | 1830.0824 | 1891 | 1890 |  | 1878 | 1845.43 | 0
5 | 2285.7366 | 1912 | 1909 | 2031.5836 | 1980 | 2153.147 | 0 | 256.394 | 215 | 215 | Note 1 | 224 | 238.687 | 0 | 5 | 2029.3426 | 1697 | 1694 |  | 1756 | 1914.46 | 0
6 | 2068.9914 | 2385 | 2392 | 2181.6446 | 2328 | 2799.158 | 0 | 229.5597 | 259 | 259 | Note 1 | 253 | 292.588 | 0 | 6 | 1839.4317 | 2126 | 2133 |  | 2075 | 2506.57 | 0
7 | 2975.789 | 3550 | 3576 | 2926.8472 | 3369 | 3513.919 | 0 | 308.5446 | 352 | 353 | Note 1 | 334 | 342.969 | 0 | 7 | 2667.2444 | 3198 | 3223 |  | 3035 | 3170.95 | 0
8 | 3936.764 | 3467 | 3480 | 3571.6614 | 3655 | 3794.558 | 0 | 384.0455 | 332 | 335 | Note 1 | 352 | 360.598 | 0 | 8 | 3552.7185 | 3135 | 3145 |  | 3303 | 3433.96 | 0
9 | 4822.8773 | 4997 | 4993 | 4771.5975 | 4946 | 4949.938 | 0 | 458.1014 | 469 | 467 | Note 1 | 463 | 460.788 | 0 | 9 | 4364.7758 | 4528 | 4526 |  | 4483 | 4489.15 | 0
10 | 4899.0565 | 5130 | 5133 | 5029.2702 | 5066 | 5342.735 | 0 | 457.9932 | 479 | 478 | Note 1 | 472 | 489.455 | 0 | 10 | 4441.0633 | 4651 | 4655 |  | 4594 | 4853.28 | 0
11 | 5505.8995 | 5971 | 5992 | 5485.3257 | 5754 | 5672.438 | 0 | 506.3045 | 537 | 536 | Note 1 | 516 | 508.218 | 0 | 11 | 4999.595 | 5434 | 5456 |  | 5238 | 5164.22 | 0
12 | 5846.136 | 5517 | 5513 | 5708.5515 | 5570 | 5501.464 | 0 | 529.3648 | 498 | 498 | Note 1 | 504 | 496.504 | 0 | 12 | 5316.7711 | 5019 | 5015 |  | 5066 | 5004.96 | 0
13 | 6805.1571 | 6637 | 6636 | 7233.0374 | 7084 | 7093.864 | 0 | 616.6094 | 597 | 600 | Note 1 | 642 | 639.274 | 0 | 13 | 6188.5477 | 6040 | 6036 |  | 6442 | 6454.59 | 0
14 | 6827.0535 | 7053 | 7064 | 7085.957 | 7168 | 7143.353 | 0 | 616.1242 | 633 | 635 | Note 1 | 645 | 639.953 | 0 | 14 | 6210.9293 | 6420 | 6429 |  | 6523 | 6503.4 | 0
15 | 8703.455 | 8422 | 8437 | 8689.9561 | 8785 | 8825.455 | 0 | 781.0016 | 751 | 754 | Note 1 | 785 | 784.905 | 0 | 15 | 7922.4534 | 7671 | 7683 |  | 8000 | 8040.55 | 0
16 | 8745.8354 | 8990 | 9025 | 8842.8175 | 8968 | 8927.2 | 0 | 781.0124 | 800 | 803 | Note 1 | 799 | 793.61 | 0 | 16 | 7964.823 | 8190 | 8222 |  | 8169 | 8133.59 | 0
17 | 5950.276 | 6276 | 6252 | 5791.0239 | 5825 | 5721.371 | 0 | 529.4985 | 561 | 556 | Note 1 | 519 | 509.581 | 0 | 17 | 5420.7775 | 5715 | 5696 |  | 5306 | 5211.79 | 0
18 | 5939.3653 | 6080 | 6072 | 5952.6309 | 5909 | 5629.246 | 0 | 529.3784 | 544 | 541 | Note 1 | 528 | 506.956 | 0 | 18 | 5409.9868 | 5536 | 5531 |  | 5381 | 5122.29 | 0
19 | 5789.2634 | 5192 | 5168 | 5617.7336 | 5283 | 5324.69 | 0 | 529.2289 | 481 | 479 | Note 1 | 492 | 492.97 | 0 | 19 | 5260.0345 | 4711 | 4689 |  | 4791 | 4831.72 | 0
20 | 5386.5635 | 5363 | 5358 | 5315.9924 | 5307 | 5376.089 | 0 | 506.2207 | 504 | 503 | Note 1 | 498 | 501.239 | 0 | 20 | 4880.3429 | 4859 | 4855 |  | 4809 | 4874.85 | 0
21 | 4347.7986 | 4318 | 4324 | 4369.5515 | 4347 | 4341.163 | 0 | 409.0843 | 405 | 406 | Note 1 | 408 | 405.543 | 0 | 21 | 3938.7143 | 3913 | 3918 |  | 3939 | 3935.62 | 0
22 | 4333.4889 | 4224 | 4222 | 4323.8097 | 4254 | 4243.269 | 0 | 409.5326 | 399 | 399 | Note 1 | 402 | 398.939 | 0 | 22 | 3923.9563 | 3825 | 3823 |  | 3852 | 3844.33 | 0
23 | 4556.4267 | 4145 | 4142 | 4215.998 | 4147 | 4204.735 | 0 | 433.8551 | 395 | 394 | Note 1 | 395 | 397.275 | 0 | 23 | 4122.5716 | 3750 | 3748 |  | 3752 | 3807.46 | 0
24 | 4286.9653 | 4287 | 4287 | 4194.2432 | 4193 | 4049.81 | 0 | 409.5808 | 407 | 407 | Note 1 | 399 | 385.64 | 0 | 24 | 3877.3845 | 3880 | 3880 |  | 3794 | 3664.17 | 0
Coil Load, Total (kWh,thermal)
Sensible | [7 empty] | Latent
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 6189.34 | 5889.2583 | 5886.9135 | 5807.8573 | 5788 | 5870.06 | 0 | 1942.39 | 1663.0494 | 1658.0667 | 1795.0172 | 1684 | 1797.5 | 0
2 | 6201.56 | 6069.8079 | 6067.17 | 5850.1562 | 5961 | 5871.7 | 0 | 1914.24 | 1560.4644 | 1559.8782 | 1777.9436 | 1747 | 1802.77 | 0
3 | 6194.38 | 5881.3446 | 5878.1205 | 5806.3857 | 5788 | 5782.88 | 0 | 1933.51 | 1668.9114 | 1668.0321 | 1773.0767 | 1657 | 1745.07 | 0
4 | 5548.55 | 5878.1205 | 5873.4309 | 5740.6566 | 5788 | 5683.06 | 0 | 1675.6 | 1655.7219 | 1654.8426 | 1723.1504 | 1644 | 1634.17 | 0
5 | 6318.9 | 5675.2953 | 5671.7781 | 5611.5024 | 5580 | 5955.01 | 0 | 1785.95 | 1122.573 | 1081.2459 | 1607.3746 | 1420 | 1559.34 | 0
6 | 5686.24 | 6438.5277 | 6438.5277 | 6012.3325 | 6341 | 7311.79 | 0 | 1444.63 | 1697.6352 | 1746.5829 | 1550.8876 | 1574 | 1911.15 | 0
7 | 7596.88 | 8342.2122 | 8347.7811 | 7528.0125 | 8277 | 8646.87 | 0 | 2114.5 | 2733.7437 | 2884.9833 | 1865.0285 | 2173 | 2122.59 | 0
8 | 9558.23 | 9069.9795 | 9069.1002 | 8751.3077 | 9038 | 9298.63 | 0 | 2563.08 | 1220.7615 | 1202.5893 | 2069.1885 | 1775 | 1887.81 | 0
9 | 11757.9 | 11872.6017 | 11875.2396 | 11758.2673 | 11971 | 11923.2 | 0 | 2797.72 | 2913.1209 | 2968.8099 | 2522.4251 | 2660 | 2821.19 | 0
10 | 11506.4 | 12039.0825 | 12041.1342 | 11985.6398 | 11971 | 12287.1 | 0 | 3132.98 | 3300.8922 | 3351.5985 | 3019.5601 | 3128 | 3595.03 | 0
11 | 12342.2 | 12811.9872 | 12817.5561 | 12473.8609 | 12731 | 12561.8 | 0 | 4031.89 | 4643.2902 | 4787.4954 | 3654.0485 | 3991 | 4052.76 | 0
12 | 12810 | 12612.093 | 12610.9206 | 12655.4944 | 12559 | 12561.3 | 0 | 4438.4 | 3603.0783 | 3576.6993 | 4086.9647 | 3699 | 3468.23 | 0
13 | 16816.1 | 17139.0225 | 17135.2122 | 17378.5032 | 17422 | 17430.7 | 0 | 3682.11 | 2583.9696 | 2485.7811 | 4495.456 | 3669 | 3749.01 | 0
14 | 17283.5 | 17638.1718 | 17639.0511 | 17574.6097 | 17629 | 17608.6 | 0 | 2950.56 | 3170.1696 | 3180.135 | 3358.8288 | 3438 | 3446.79 | 0
15 | 22882.4 | 22196.463 | 22196.7561 | 22454.4561 | 22491 | 22350.4 | 0 | 3804.88 | 3190.6866 | 3195.9624 | 3978.4548 | 4145 | 4719.45 | 0
16 | 22284.7 | 22527.9591 | 22533.2349 | 22527.6692 | 22491 | 22292 | 0 | 4437.98 | 5053.044 | 5187.87 | 4415.6877 | 4925 | 5331.25 | 0
17 | 13048.3 | 13599.2538 | 13600.1331 | 13046.9672 | 12939 | 12739.1 | 0 | 4183.03 | 4605.4803 | 4644.4626 | 3478.7931 | 3763 | 3811.95 | 0
18 | 12720.6 | 12829.8663 | 12831.6249 | 12851.4495 | 12729 | 12180.9 | 0 | 4785.28 | 5103.4572 | 5146.2498 | 4554.1122 | 4582 | 4648.77 | 0
19 | 12490.8 | 11875.5327 | 11871.1362 | 12151.7364 | 11761 | 11540.7 | 0 | 5170.89 | 4136.5203 | 4043.3145 | 4930.496 | 4470 | 5094.59 | 0
20 | 11655.3 | 11532.3126 | 11534.0712 | 11537.4992 | 11381 | 11359.2 | 0 | 5334.51 | 5549.8485 | 5586.1929 | 5205.4948 | 5486 | 5771.92 | 0
21 | 8882.19 | 9302.4078 | 9302.7009 | 9049.8699 | 9036 | 8931.39 | 0 | 4657.75 | 4133.0031 | 4142.3823 | 4561.554 | 4447 | 4593.42 | 0
22 | 8880.28 | 8973.5496 | 8973.8427 | 8939.7425 | 8864 | 8747.22 | 0 | 4684.26 | 4306.8114 | 4311.2079 | 4621.5598 | 4459 | 4608.6 | 0
23 | 9449.35 | 8787.4311 | 8787.4311 | 8740.9679 | 8656 | 8646.75 | 0 | 5081.99 | 4404.4137 | 4404.7068 | 4624.0171 | 4482 | 4696.56 | 0
24 | 8806.54 | 8799.1551 | 8799.7413 | 8661.2371 | 8656 | 8359.6 | 0 | 4885.22 | 4925.2524 | 4954.5624 | 4709.2294 | 4666 | 4613.06 | 0
HumRat
0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 0.0090778 | 0.0094 | 0.0094 | 0.0092568 | 0.009276 | 0.0092502 | 0
2 | 0.0090138 | 0.0093 | 0.0093 | 0.0092201 | 0.009302 | 0.0092582 | 0
3 | 0.0090644 | 0.0094 | 0.0094 | 0.0092267 | 0.009239 | 0.0092068 | 0
4 | 0.0089864 | 0.0094 | 0.0094 | 0.0091699 | 0.009201 | 0.0091047 | 0
5 | 0.0088405 | 0.0089 | 0.009 | 0.009048 | 0.008969 | 0.0089519 | 0
6 | 0.0086578 | 0.0092 | 0.0092 | 0.0089018 | 0.009012 | 0.0091583 | 0
7 | 0.0091531 | 0.01 | 0.0098 | 0.0091706 | 0.00949 | 0.0094778 | 0
8 | 0.0095303 | 0.0094 | 0.0094 | 0.0094818 | 0.009314 | 0.0093737 | 0
9 | 0.0096727 | 0.0099 | 0.0099 | 0.0096209 | 0.009708 | 0.0097161 | 0
10 | 0.010058 | 0.0103 | 0.0102 | 0.0099775 | 0.010041 | 0.010237 | 0
11 | 0.010408 | 0.0109 | 0.0107 | 0.010392 | 0.010588 | 0.010622 | 0
12 | 0.010684 | 0.0108 | 0.0108 | 0.010701 | 0.01058 | 0.010433 | 0
13 | 0.010087 | 0.0101 | 0.0102 | 0.010129 | 0.009975 | 0.0099715 | 0
14 | 0.0097987 | 0.01 | 0.01 | 0.009694 | 0.009778 | 0.0097436 | 0
15 | 0.0095792 | 0.0098 | 0.0098 | 0.009521 | 0.009579 | 0.0097834 | 0
16 | 0.0096663 | 0.01 | 0.0098 | 0.0096238 | 0.009733 | 0.0098255 | 0
17 | 0.01077 | 0.0107 | 0.0107 | 0.010361 | 0.01044 | 0.010257 | 0
18 | 0.011184 | 0.0112 | 0.0112 | 0.010924 | 0.010912 | 0.010859 | 0
19 | 0.011131 | 0.011 | 0.0111 | 0.011075 | 0.010914 | 0.011024 | 0
20 | 0.010991 | 0.0114 | 0.0113 | 0.011126 | 0.011269 | 0.011357 | 0
21 | 0.01114 | 0.0113 | 0.0113 | 0.011355 | 0.011348 | 0.011378 | 0
22 | 0.011177 | 0.0114 | 0.0114 | 0.011403 | 0.011383 | 0.011398 | 0
23 | 0.011176 | 0.0115 | 0.0115 | 0.01142 | 0.011416 | 0.01145 | 0
24 | 0.011275 | 0.0117 | 0.0117 | 0.011476 | 0.011507 | 0.011462 | 0
COP2
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 3.5167 | 3.539 | 3.5406 | 3.5307 | 3.5195 | 3.5112 | 0
2 | 3.513 | 3.4985 | 3.4954 | 3.5201 | 3.4905 | 3.5017 | 0
3 | 3.517 | 3.5381 | 3.5411 | 3.5288 | 3.5168 | 3.5191 | 0
4 | 3.5074 | 3.5403 | 3.5411 | 3.5378 | 3.5156 | 3.5238 | 0
5 | 3.5458 | 3.5554 | 3.5375 | 3.5533 | 3.5354 | 3.4899 | 0
6 | 3.4465 | 3.4114 | 3.4219 | 3.4668 | 3.3999 | 3.2949 | 0
7 | 3.2635 | 3.12 | 3.1412 | 3.2093 | 3.1018 | 3.0648 | 0
8 | 3.079 | 2.9682 | 2.9516 | 3.0295 | 2.9584 | 2.948 | 0
9 | 3.018 | 2.9589 | 2.973 | 2.9929 | 2.9581 | 2.9787 | 0
10 | 2.9882 | 2.9902 | 2.9988 | 2.9836 | 2.9805 | 2.9726 | 0
11 | 2.9739 | 2.9233 | 2.9381 | 2.9402 | 2.9062 | 2.929 | 0
12 | 2.9504 | 2.9391 | 2.9363 | 2.9329 | 2.9189 | 2.9137 | 0
13 | 3.0122 | 2.9717 | 2.9568 | 3.0242 | 2.9771 | 2.9856 | 0
14 | 2.9638 | 2.9503 | 2.9472 | 2.9542 | 2.939 | 2.9476 | 0
15 | 3.0663 | 3.0144 | 3.0097 | 3.0418 | 3.032 | 3.0672 | 0
16 | 3.0555 | 3.068 | 3.0716 | 3.0469 | 3.0571 | 3.0943 | 0
17 | 2.8959 | 2.9007 | 2.9182 | 2.8537 | 2.8673 | 2.8928 | 0
18 | 2.9474 | 2.9496 | 2.9608 | 2.924 | 2.9298 | 2.9897 | 0
19 | 3.0508 | 3.084 | 3.0794 | 3.0408 | 3.0725 | 3.1242 | 0
20 | 3.1541 | 3.1852 | 3.1953 | 3.1496 | 3.1783 | 3.1865 | 0
21 | 3.1142 | 3.1115 | 3.1094 | 3.1151 | 3.1019 | 3.1155 | 0
22 | 3.1302 | 3.144 | 3.1466 | 3.1364 | 3.1316 | 3.1475 | 0
23 | 3.1892 | 3.1826 | 3.185 | 3.1701 | 3.1683 | 3.1734 | 0
24 | 3.1938 | 3.2014 | 3.2084 | 3.1878 | 3.1774 | 3.2033 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
ODB (°C) | 0 | 0 | 0 | 0 | 0 | 0
0 |  |  |  | 0 | 0 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | 0
2 | 18.05 | 18.3333 | 18.3333 | 18.1125 | 18.3 | 18.3 | 0
3 | 18.05 | 17.7778 | 17.7778 | 17.9875 | 17.8 | 17.8 | 0
4 | 17.8 | 17.7778 | 17.7778 | 17.8 | 17.8 | 17.8 | 0
5 | 17.5 | 17.2222 | 17.2222 | 17.425 | 17.2 | 17.2 | 0
6 | 18.3 | 19.4444 | 19.4444 | 18.575 | 19.4 | 19.4 | 0
7 | 22.2 | 25 | 25 | 22.9 | 25 | 25 | 0
8 | 26.1 | 27.2222 | 27.2222 | 26.375 | 27.2 | 27.2 | 0
9 | 28.05 | 28.8889 | 28.8889 | 28.2625 | 28.9 | 28.9 | 0
10 | 28.9 | 28.8889 | 28.8889 | 28.9 | 28.9 | 28.9 | 0
11 | 30 | 31.1111 | 31.1111 | 30.275 | 31.1 | 31.1 | 0
12 | 30.85 | 30.5556 | 30.5556 | 30.7875 | 30.6 | 30.6 | 0
13 | 30.85 | 31.1111 | 31.1111 | 30.9125 | 31.1 | 31.1 | 0
14 | 31.4 | 31.6667 | 31.6667 | 31.475 | 31.7 | 31.7 | 0
15 | 31.95 | 32.2222 | 32.2222 | 32.0125 | 32.2 | 32.2 | 0
16 | 32.2 | 32.2222 | 32.2222 | 32.2 | 32.2 | 32.2 | 0
17 | 31.95 | 31.6667 | 31.6667 | 31.8875 | 31.7 | 31.7 | 0
18 | 31.4 | 31.1111 | 31.1111 | 31.325 | 31.1 | 31.1 | 0
19 | 29.7 | 28.3333 | 28.3333 | 29.35 | 28.3 | 28.3 | 0
20 | 27.75 | 27.2222 | 27.2222 | 27.6125 | 27.2 | 27.2 | 0
21 | 27.2 | 27.2222 | 27.2222 | 27.2 | 27.2 | 27.2 | 0
22 | 26.95 | 26.6667 | 26.6667 | 26.8875 | 26.7 | 26.7 | 0
23 | 26.4 | 26.1111 | 26.1111 | 26.325 | 26.1 | 26.1 | 0
24 | 26.1 | 26.1111 | 26.1111 | 26.1 | 26.1 | 26.1 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0
EDB (°C) | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 |  | EWB
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 23.4068 | 23.8333 | 23.8333 | 23.945 | 23.92 | 23.9367 | 0 | 16.9641 | 17.34 | 17.34 | 0 | 17.155 | 17.3042 | 0
2 | 23.3748 | 23.9444 | 23.9444 | 23.9636 | 24 | 23.9367 | 0 | 16.9046 | 17.29 | 17.29 | 0 | 17.238 | 17.31 | 0
3 | 23.3833 | 23.8333 | 23.8333 | 23.9451 | 23.92 | 23.8958 | 0 | 16.9418 | 17.34 | 17.37 | 0 | 17.12 | 17.2367 | 0
4 | 23.3739 | 23.8333 | 23.8333 | 23.9169 | 23.92 | 23.8375 | 0 | 16.8619 | 17.34 | 17.37 | 0 | 17.102 | 17.0785 | 0
5 | 23.3503 | 23.7778 | 23.7778 | 23.8612 | 23.83 | 23.9757 | 0 | 16.6966 | 16.85 | 16.94 | 0 | 16.787 | 17.0075 | 0
6 | 23.4171 | 24.1111 | 24.1111 | 24.0335 | 24.16 | 24.5756 | 0 | 16.5734 | 17.3 | 17.3 | 0 | 17.032 | 17.5412 | 0
7 | 24.0395 | 24.9444 | 24.9444 | 24.6841 | 25 | 25.1643 | 0 | 17.3192 | 18.39 | 18.23 | 0 | 17.911 | 17.9926 | 0
8 | 24.5724 | 25.2778 | 25.2778 | 25.208 | 25.33 | 25.4533 | 0 | 17.7945 | 17.78 | 17.78 | 0 | 17.646 | 17.9591 | 0
9 | 25.0937 | 25.5556 | 25.5556 | 25.4906 | 25.59 | 25.5785 | 0 | 17.973 | 18.36 | 18.28 | 0 | 18.118 | 18.3251 | 0
10 | 25.2815 | 25.5556 | 25.5556 | 25.5865 | 25.59 | 25.7393 | 0 | 18.3972 | 18.68 | 18.6 | 0 | 18.442 | 18.8543 | 0
11 | 25.3592 | 25.8889 | 25.8889 | 25.7953 | 25.91 | 25.8631 | 0 | 18.8246 | 19.48 | 19.33 | 0 | 19.142 | 19.1876 | 0
12 | 25.5877 | 25.8333 | 25.8333 | 25.8718 | 25.84 | 25.8628 | 0 | 19.1202 | 19.23 | 19.23 | 0 | 18.935 | 18.8671 | 0
13 | 26.53 | 25.9444 | 25.9444 | 25.8849 | 25.91 | 25.9424 | 0 | 18.8377 | 18.56 | 18.64 | 0 | 18.326 | 18.518 | 0
14 | 26.5617 | 26.0556 | 26.0556 | 25.9689 | 26 | 26.022 | 0 | 18.5548 | 18.6 | 18.6 | 0 | 18.269 | 18.4421 | 0
15 | 26.7812 | 26.1111 | 26.1111 | 26.0513 | 26.08 | 26.1296 | 0 | 18.5486 | 18.46 | 18.46 | 0 | 18.239 | 18.6471 | 0
16 | 26.5632 | 26.1667 | 26.1667 | 26.0827 | 26.08 | 26.0323 | 0 | 18.673 | 18.84 | 18.76 | 0 | 18.557 | 18.7965 | 0
17 | 26.198 | 26.0556 | 26.0556 | 26.0396 | 26 | 25.943 | 0 | 19.4032 | 19.35 | 19.35 | 0 | 19.063 | 19.1104 | 0
18 | 26.2263 | 25.9444 | 25.9444 | 25.9556 | 25.91 | 25.6955 | 0 | 19.7724 | 19.75 | 19.68 | 0 | 19.458 | 19.3936 | 0
19 | 25.7001 | 25.5 | 25.5 | 25.6558 | 25.5 | 25.4093 | 0 | 19.5753 | 19.32 | 19.4 | 0 | 19.199 | 19.5323 | 0
20 | 25.1673 | 25.3333 | 25.3333 | 25.3934 | 25.33 | 25.3281 | 0 | 19.3718 | 19.76 | 19.76 | 0 | 19.65 | 19.7431 | 0
21 | 24.6544 | 25.3333 | 25.3333 | 25.333 | 25.33 | 25.291 | 0 | 19.438 | 19.76 | 19.76 | 0 | 19.706 | 19.7437 | 0
22 | 24.7445 | 25.2222 | 25.2222 | 25.2865 | 25.25 | 25.2092 | 0 | 19.4846 | 19.8 | 19.8 | 0 | 19.697 | 19.7887 | 0
23 | 24.6707 | 25.1111 | 25.1111 | 25.2013 | 25.16 | 25.1645 | 0 | 19.4693 | 19.84 | 19.84 | 0 | 19.694 | 19.8355 | 0
24 | 24.7257 | 25.1111 | 25.1111 | 25.1674 | 25.16 | 25.0374 | 0 | 19.5725 | 20.14 | 20.06 | 0 | 19.805 | 19.7678 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OHR (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
1 | 0.011255 | 0.0114 | 0.0114 | 0.011202 | 0.0111 | 0.011072 | 0
2 | 0.011255 | 0.0112 | 0.0112 | 0.011296 | 0.011462 | 0.011432 | 0
3 | 0.011255 | 0.0114 | 0.0114 | 0.011199 | 0.0111 | 0.011072 | 0
4 | 0.011075 | 0.0114 | 0.0114 | 0.011061 | 0.0111 | 0.011072 | 0
5 | 0.01061 | 0.0103 | 0.0103 | 0.010484 | 0.01018 | 0.010155 | 0
6 | 0.010568 | 0.0113 | 0.0113 | 0.010648 | 0.011001 | 0.01097 | 0
7 | 0.012071 | 0.0133 | 0.0133 | 0.012288 | 0.01314 | 0.013099 | 0
8 | 0.012173 | 0.0109 | 0.0109 | 0.011849 | 0.011075 | 0.011039 | 0
9 | 0.011538 | 0.0117 | 0.0117 | 0.01158 | 0.011995 | 0.011957 | 0
10 | 0.012388 | 0.0125 | 0.0125 | 0.012406 | 0.01276 | 0.012719 | 0
11 | 0.013776 | 0.0148 | 0.0148 | 0.013949 | 0.014809 | 0.014761 | 0
12 | 0.014041 | 0.0134 | 0.0134 | 0.013761 | 0.013253 | 0.013211 | 0
13 | 0.012315 | 0.0115 | 0.0115 | 0.011999 | 0.011329 | 0.011293 | 0
14 | 0.011543 | 0.0121 | 0.0121 | 0.011528 | 0.011729 | 0.011692 | 0
15 | 0.012069 | 0.0119 | 0.0119 | 0.012086 | 0.012379 | 0.01234 | 0
16 | 0.013324 | 0.0144 | 0.0144 | 0.013492 | 0.014232 | 0.014188 | 0
17 | 0.014505 | 0.0146 | 0.0146 | 0.014504 | 0.01473 | 0.014684 | 0
18 | 0.015234 | 0.0157 | 0.0157 | 0.015288 | 0.015684 | 0.015634 | 0
19 | 0.015134 | 0.0143 | 0.0143 | 0.01493 | 0.014539 | 0.014493 | 0
20 | 0.015748 | 0.0164 | 0.0164 | 0.01597 | 0.016878 | 0.016824 | 0
21 | 0.016886 | 0.0164 | 0.0164 | 0.01681 | 0.016878 | 0.016824 | 0
22 | 0.016863 | 0.0167 | 0.0167 | 0.016771 | 0.016832 | 0.016777 | 0
23 | 0.016867 | 0.0169 | 0.0169 | 0.016784 | 0.016889 | 0.016835 | 0
24 | 0.017112 | 0.0178 | 0.0178 | 0.017077 | 0.017329 | 0.017273 | 0

## Tdata
e300results.XLS, Jul, 2004 | 0 | 0 | 0 | 0 | 0 | SEE SHEET 'A' FOR INSTRUCTIONS | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Delta Annual Space Cooling Electricity Consumptions | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 4339.6026 | 4629 | 4629 | 4410.4348 | 4543.158 | 4538 | 0
E320-E300, Infiltration | 4425.8798 | 3995 | 4037 | 4351.305 | 4424.404 | 4387 | 0
E330-E300, 100% OA | 5329.5231 | 4958 | 4683 | 5445.065 | 5558.726 | 5260 | 0
E330-E320, OA-Infl | 903.6433 | 963 | 646 | 1093.76 | 1134.322 | 873 | 0
E340-E300, 50/50 OA/inf | 4985.5179 | 4608 | 4510 | 5047.6908 | 5088.85 | 4877 | 0
E330-E340, OA-50/50 | 344.0053 | 350 | 173 | 397.3742 | 469.876 | 383 | 0
E350-E300, Tstat Set Up | -3396.7978 | -4203 | -4207 | -3647.5233 | -3389.819 | -3328 | 0
(E360-E300)/4, Overload | 4916.2536 | 4828.5 | 4815.25 | 4980.1301 | 4966.7118 | 4999.5 | 0
E400-E300, Ec. T Ctrl | -3588.6237 | -3904 | -3879 | -3758.0865 | 0 | -3657 | 0
E410-E300, Ec. No Compr. | -3555.3454 | -3082 | -3056 | -3013.2237 | 0 | -3567 | 0
E420-E300, Ec. ODB Lim. | -2246.7696 | -2220 | -1845 | -2045.1846 | 0 | -1862 | 0
E430-E300, Ec. Enth Ctrl | -3095.7459 | -2818 | -2944 | -2938.2118 | 0 | -3252 | 0
E440-E300, Ec. Enth Lim | -1942.4562 | -1718 | -1782 | -1738.9033 | 0 | -1822 | 0
(E500-E300)/2, 0%OA | -6647.9451 | -5966.5 | -5966.5 | -5973.9551 | -6326.729 | -5966 | 0
(E510-E500)/4, PLR | 4304.4811 | 4524.75 | 4525 | 4440.0764 | 4353.525 | 4448.5 | 0
E525-E520, EDB | -4665.708 | -4981 | -4969 | -5031.5465 | -4889.357 | -4458 | 0
E530-E500, Dry Coil | -5056.616 | -5277 | -5285 | -5081.8579 | -4880.485 | -5263 | 0
E545-E540, EDB (Dry) | -3743.2989 | -4076 | -4083 | -3514.133 | -3745.491 | -3825 | 0
Compressor (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 3986.0911 | 4244 | 4244 | 0 | 4166.82 | 4177 | 0
E320-E300, Infiltration | 4079.6031 | 3681 | 3721 | 0 | 4076.025 | 4036 | 0
E330-E300, 100% OA | 4946.1978 | 4603 | 4352 | 0 | 5157.732 | 4899 | 0
E330-E320, OA-Infl | 866.5947 | 922 | 631 | 0 | 1081.707 | 863 | 0
E340-E300, 50/50 OA/inf | 4609.403 | 4260 | 4172 | 0 | 4702.789 | 4524 | 0
E330-E340, OA-50/50 | 336.7947 | 343 | 180 | 0 | 454.943 | 375 | 0
E350-E300, Tstat Set Up | -3036.6939 | -3767 | -3772 | 0 | -3031.946 | -2985 | 0
(E360-E300)/4, Overload | 4438.0764 | 4357.5 | 4345.5 | 0 | 4481.7903 | 4516.25 | 0
E400-E300, Ec. T Ctrl | -3174.5856 | -3463 | -3442 | 0 | 0 | -3247 | 0
E410-E300, Ec. No Compr. | -3149.0399 | -2746 | -2723 | 0 | 0 | -3191 | 0
E420-E300, Ec. ODB Lim. | -1994.9489 | -1973 | -1639 | 0 | 0 | -1662 | 0
E430-E300, Ec. Enth Ctrl | -2754.9132 | -2510 | -2622 | 0 | 0 | -2910 | 0
E440-E300, Ec. Enth Lim | -1724.4011 | -1527 | -1584 | 0 | 0 | -1627 | 0
(E500-E300)/2, 0%OA | -2249.6194 | -1548 | -1547.5 | 0 | -1956.0745 | -1677 | 0
(E510-E500)/4, PLR | 3451.4328 | 3575.75 | 3576 | 0 | 3478.3612 | 3557.5 | 0
E525-E520, EDB | -2963.4018 | -3241 | -3233 | 0 | -3148.17 | -2742 | 0
E530-E500, Dry Coil | -4197.3004 | -4346 | -4354 | 0 | -4001.924 | -4350 | 0
E545-E540, EDB (Dry) | -2398.8748 | -2713 | -2720 | 0 | -2413.197 | -2449 | 0
Supply Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0 | 0 | 0 | 0 | 0 | 0 | 0
E320-E300, Infiltration | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E300, 100% OA | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E320, OA-Infl | 0 | 0 | 0 | 0 | 0 | 0 | 0
E340-E300, 50/50 OA/inf | 0 | 0 | 0 | 0 | 0 | 0 | 0
E330-E340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300, Overload | 0 | 0 | 0 | 0 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | 0 | 0 | 0 | 0 | 0 | 0 | 0
E410-E300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | 0 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | 0 | 0 | 0 | 0
E500-E300, 0%OA | -8316.0984 | -8511 | -8511 | -8231.549 | -8326.688 | -8241 | 0
E510-E500, PLR | 1951.1712 | 2262 | 2262 | 2035.088 | 2001.783 | 2038 | 0
E525-E520, EDB | -973.4182 | -988 | -986 | -948.4547 | -995.563 | -979 | 0
E530-E500, Dry Coil | -491.3766 | -536 | -536 | -508.8296 | -502.376 | -522 | 0
E545-E540, EDB (Dry) | -768.7729 | -757 | -757 | -628.6074 | -761.749 | -787 | 0
Condenser Fan (kWh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 353.5115 | 385 | 385 | 0 | 376.338 | 368 | 0
E320-E300, Infiltration | 346.2767 | 314 | 316 | 0 | 348.379 | 358 | 0
E330-E300, 100% OA | 383.3254 | 355 | 331 | 0 | 400.994 | 370 | 0
E330-E320, OA-Infl | 37.0487 | 41 | 15 | 0 | 52.615 | 12 | 0
E340-E300, 50/50 OA/inf | 376.1148 | 348 | 338 | 0 | 386.061 | 361 | 0
E330-E340, OA-50/50 | 7.2105 | 7 | -7 | 0 | 14.933 | 9 | 0
E350-E300, Tstat Set Up | -360.1038 | -436 | -435 | 0 | -357.873 | -353 | 0
(E360-E300)/4, Overload | 478.1772 | 471 | 469.75 | 0 | 484.9215 | 487.25 | 0
E400-E300, Ec. T Ctrl | -414.0381 | -441 | -437 | 0 | 0 | -421 | 0
E410-E300, Ec. No Compr. | -406.3054 | -336 | -333 | 0 | 0 | -387 | 0
E420-E300, Ec. ODB Lim. | -251.8207 | -247 | -206 | 0 | 0 | -208 | 0
E430-E300, Ec. Enth Ctrl | -340.8327 | -308 | -322 | 0 | 0 | -353 | 0
E440-E300, Ec. Enth Lim | -218.0552 | -191 | -198 | 0 | 0 | -203 | 0
(E500-E300)/2, 0%OA | -240.2766 | -163 | -163.5 | 0 | -207.3105 | -173.5 | 0
(E510-E500)/4, PLR | 365.2555 | 383.5 | 383.5 | 0 | 374.718 | 381.5 | 0
E525-E520, EDB | -728.888 | -752 | -750 | 0 | -745.624 | -733 | 0
E530-E500, Dry Coil | -367.939 | -395 | -395 | 0 | -376.185 | -391 | 0
E545-E540, EDB (Dry) | -575.6512 | -606 | -606 | 0 | -570.545 | -589 | 0
Delta Cooling Coil Loads | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sensible Coil Load (kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | -405.371 | 504.132 | 507.9423 | -100.4356 | -24.393 | -108 | 0
E320-E300, Infiltration | 6197.4569 | 6900.1602 | 6942.0735 | 6585.5914 | 6799.339 | 7543 | 0
E330-E300, 100% OA | 6421.6281 | 7514.2047 | 7522.9977 | 7908.0123 | 7439.994 | 6631 | 0
E330-E320, OA-Infl | 224.1712 | 614.0445 | 580.9242 | 1322.421 | 640.655 | -912 | 0
E340-E300, 50/50 OA/inf | 6370.8576 | 7256.5698 | 7305.8106 | 7225.3169 | 7171.095 | 6215 | 0
E330-E340, OA-50/50 | 50.7704 | 257.6349 | 217.1871 | 682.6954 | 268.899 | 416 | 0
E350-E300, Tstat Set Up | -1572.7295 | -2028.1055 | -2032.0623 | -1707.6186 | -1655.1658 | -1605.75 | 0
(E360-E300)/4, Overload | 19578.7717 | 19780.7328 | 19783.7371 | 19886.2634 | 19749.0605 | 19876.5 | 0
E400-E300, Ec. T Ctrl | -14709.3889 | -14377.7274 | -14367.762 | -14566.8442 | 0 | -14010 | 0
E410-E300, Ec. No Compr. | -10985.1029 | -8138.2146 | -8144.9559 | 0 | 0 | -9606 | 0
E420-E300, Ec. ODB Lim. | -6271.9238 | -6130.7727 | -5192.5596 | -5721.4244 | 0 | -5207 | 0
E430-E300, Ec. Enth Ctrl | -8798.4022 | -8065.5258 | -8350.7121 | -8254.3534 | 0 | -9048 | 0
E440-E300, Ec. Enth Lim | -5785.676 | -5204.2836 | -5312.7306 | -5165.0306 | 0 | -5406 | 0
E500-E300, 0%OA | -11617.9484 | -8147.0076 | -8158.7316 | -7808.6231 | -10335.24 | -7661 | 0
(E510-E500)/4, PLR | 10761.5494 | 11427.5293 | 11427.4561 | 11237.5889 | 10762.7085 | 11270.75 | 0
E525-E520, EDB | -130.6037 | -883.9896 | -882.231 | -1187.4385 | -201.619 | -949 | 0
E530-E500, Dry Coil | 2.048 | -1076.2632 | -1075.9701 | -369.1301 | 0 | -528 | 0
E545-E540, EDB (Dry) | -130.4955 | -808.6629 | -808.6629 | -837.5233 | -201.642 | -792 | 0
Latent Coil Load(kWh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 19320.6351 | 19607.2176 | 19612.2003 | 19118.099 | 19575.693 | 19111 | 0
E320-E300, Infiltration | 13167.3536 | 12172.7361 | 12259.2006 | 12519.2494 | 12597.449 | 11157 | 0
E330-E300, 100% OA | 18164.3759 | 15932.3298 | 16178.5338 | 17572.9191 | 18528.23 | 17119 | 0
E330-E320, OA-Infl | 4997.0223 | 3759.5937 | 3919.3332 | 5053.6697 | 5930.781 | 5962 | 0
E340-E300, 50/50 OA/inf | 15930.2538 | 14487.6399 | 14625.3969 | 15578.2133 | 15760.481 | 15279 | 0
E330-E340, OA-50/50 | 2234.1221 | 1444.6899 | 1553.1369 | 1994.7059 | 2767.749 | 1840 | 0
E350-E300, Tstat Set Up | -4747.9518 | -5434.6602 | -5529.0384 | -4904.9759 | -4263.749 | -4446 | 0
E360-E300, Overload | 4232.1084 | 3400.8393 | 3426.9252 | 4332.6356 | 4459.339 | 4403 | 0
E400-E300, Ec. T Ctrl | 3075.3436 | 2011.8384 | 2100.9408 | 2727.3459 | 0 | 2650 | 0
E410-E300, Ec. No Compr. | -768.9108 | -2365.6101 | -2303.4729 | 0 | 0 | -2477 | 0
E420-E300, Ec. ODB Lim. | -1545.6363 | -1541.706 | -1217.2443 | -1360.4828 | 0 | -1212 | 0
E430-E300, Ec. Enth Ctrl | -1872.1533 | -1577.1711 | -1721.9625 | -1787.8897 | 0 | -2010 | 0
E440-E300, Ec. Enth Lim | -929.828 | -699.0435 | -798.1113 | -802.8657 | 0 | -823 | 0
E500-E300, 0%OA | -5451.8128 | -3140.5665 | -3140.8596 | -4932.0181 | -4304.002 | -4983 | 0
E510-E500, PLR | 17484.6814 | 17615.0169 | 17615.0169 | 17488.8475 | 17488.438 | 17340 | 0
E525-E520, EDB | 2.0047 | -288.1173 | -288.1173 | 2.4788 | -8.624 | -42 | 0
E530-E500, Dry Coil | -18313.3062 | -18285.3366 | -18285.6297 | -18231.6742 | -18229.955 | -18084 | 0
E545-E540, EDB (Dry) | -0.97976 | -81.4818 | -81.4818 | -8.8672 | -3.086 | -2 | 0
Delta Various Annual Means (COP2, IDB) | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.16552 | 0.1798 | 0.18013 | 0.16518 | 0.17086 | 0.15 | 0
E320-E300, Infiltration | 0.17083 | 0.22029 | 0.21969 | 0.1753 | 0.17958 | 0.16 | 0
E330-E300, 100% OA | 0.24166 | 0.25649 | 0.29907 | 0.26442 | 0.2709 | 0.23 | 0
E330-E320, OA-Infl | 0.070831 | 0.036201 | 0.079382 | 0.089118 | 0.091321 | 0.07 | 0
E340-E300, 50/50 OA/inf | 0.20521 | 0.23966 | 0.25826 | 0.22045 | 0.22316 | 0.19 | 0
E330-E340, OA-50/50 | 0.036452 | 0.016833 | 0.040815 | 0.043961 | 0.047744 | 0.04 | 0
E350-E300, Tstat Set Up | -0.00011501 | 0.003096 | -0.0019178 | 0.0043635 | 0.0025325 | 0 | 0
E360-E300, Overload | 0.41996 | 0.46293 | 0.46845 | 0.43775 | 0.44031 | 0.43 | 0
E400-E300, Ec. T Ctrl | 0.0012106 | 0.013724 | 0.014548 | 0.016855 | 0 | 0.03 | 0
E410-E300, Ec. No Compr. | -0.0095511 | -0.025269 | -0.026661 | 0 | 0 | -0.02 | 0
E420-E300, Ec. ODB Lim. | -0.023 | -0.022394 | -0.019831 | -0.020419 | 0 | -0.02 | 0
E430-E300, Ec. Enth Ctrl | -0.02827 | -0.024649 | -0.025889 | -0.024351 | 0 | -0.02 | 0
E440-E300, Ec. Enth Lim | -0.017725 | -0.015393 | -0.015474 | -0.01474 | 0 | -0.01 | 0
E500-E300, 0%OA | -0.045013 | -0.010183 | -0.010822 | -0.033871 | -0.034365 | -0.03 | 0
E510-E500, PLR | 0.40948 | 0.41598 | 0.41577 | 0.40814 | 0.39713 | 0.41 | 0
E525-E520, EDB | 0.58247 | 0.57414 | 0.57204 | 0.57773 | 0.60629 | 0.49 | 0
E530-E500, Dry Coil | -0.24223 | -0.25849 | -0.25718 | -0.24762 | -0.27645 | -0.22 | 0
E545-E540, EDB (Dry) | 0.5601 | 0.55853 | 0.56036 | 0.46974 | 0.54604 | 0.51 | 0
IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.1313 | 0.055556 | 0 | 0.0023647 | 0.0080616 | 0.02 | 0
E320-E300, Infiltration | 0.27622 | 0.33333 | 0.33333 | 0.14305 | 0.24571 | 0.54 | 0
E330-E300, 100% OA | 0.25545 | 0.22222 | 0.22222 | 0.20615 | 0.21382 | 0.19 | 0
E330-E320, OA-Infl | -0.02077 | -0.11111 | -0.11111 | 0.063101 | -0.031885 | -0.35 | 0
E340-E300, 50/50 OA/inf | 0.25135 | 0.22222 | 0.22222 | 0.22139 | 0.22722 | 0.22 | 0
E330-E340, OA-50/50 | 0.0041016 | 0 | 0 | -0.015241 | -0.013394 | -0.03 | 0
E350-E300, Tstat Set Up | 2.0352 | 2.1111 | 2.1111 | 2.1477 | 2.187 | 2.16 | 0
E360-E300, Overload | 1.7407 | 1.5556 | 1.5 | 1.342 | 1.3992 | 1.38 | 0
E400-E300, Ec. T Ctrl | 0.50202 | 0 | 0 | 0.0013587 | 0 | 0 | 0
E410-E300, Ec. No Compr. | 0.49787 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0.3019 | 0 | 0 | -6.2527e-05 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0.36731 | 0 | 0 | -6.9725e-05 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0.2875 | 0 | 0 | -3.3826e-05 | 0 | 0 | 0
E500-E300, 0%OA | -3.3901 | -3.3889 | -3.5 | -3.6854 | -2.9838 | -1.13 | 0
E510-E500, PLR | 1.2445 | 0.11111 | 0.11111 | -0.022969 | 0 | 0 | 0
E525-E520, EDB | 13.3272 | 13.6111 | 13.5556 | 13.5028 | 13.6289 | 15.8 | 0
E530-E500, Dry Coil | -0.20888 | -0.055556 | 0 | 0.1914 | 0 | 0 | 0
E545-E540, EDB (Dry) | 13.3159 | 13.5556 | 13.5556 | 13.5202 | 13.576 | 15.71 | 0
Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.0020018 | 0.0021 | 0.0021 | 0.0019881 | 0.0019998 | 0.0019 | 0
E320-E300, Infiltration | 0.00091896 | 0.0009 | 0.0009 | 0.0008715 | 0.00087438 | 0.0007 | 0
E330-E300, 100% OA | 0.00067186 | 0.0007 | 0.0007 | 0.00071519 | 0.00063678 | 0.0007 | 0
E330-E320, OA-Infl | -0.00024709 | -0.0002 | -0.0002 | -0.00015631 | -0.00023759 | 0 | 0
E340-E300, 50/50 OA/inf | 0.00072232 | 0.0007 | 0.0007 | 0.00073675 | 0.00069351 | 0.0007 | 0
E330-E340, OA-50/50 | -5.0461e-05 | 0 | 0 | -2.1555e-05 | -5.6729e-05 | 0 | 0
E350-E300, Tstat Set Up | 0.00063685 | 0.0008 | 0.0008 | 0.00063099 | 0.00058373 | 0.00057 | 0
E360-E300, Overload | -0.0005696 | -0.0005 | -0.0005 | -0.00055909 | -0.00062237 | -0.00062 | 0
E400-E300, Ec. T Ctrl | 0.00073206 | 0.0008 | 0.0008 | 0.00087651 | 0 | 0.0008 | 0
E410-E300, Ec. No Compr. | 0.00067139 | 0.0003 | 0.0003 | 0 | 0 | 0.0003 | 0
E420-E300, Ec. ODB Lim. | 0.00019481 | 0.0002 | 0.0002 | 0.00018218 | 0 | 0.0001 | 0
E430-E300, Ec. Enth Ctrl | 0.00024119 | 0.0002 | 0.0002 | 0.00022163 | 0 | 0.0002 | 0
E440-E300, Ec. Enth Lim | 8.8738e-05 | 0.0001 | 0.0001 | 6.5316e-05 | 0 | 0 | 0
E500-E300, 0%OA | 0.00070622 | 0 | 0 | -1.9753e-05 | 0.0010435 | 0.0015 | 0
E510-E500, PLR | 0.00037457 | 0 | 0 | 8.3769e-06 | -8.8998e-07 | 0 | 0
E525-E520, EDB | 0.0070203 | 0 | 0 | 0.0073646 | 0.0069569 | 0.00747 | 0
E530-E500, Dry Coil | -0.0035488 | 0 | 0 | -0.0026609 | -0.0044208 | -0.00403 | 0
E545-E540, EDB (Dry) | 0.0017664 | 0 | 0 | 0.0024077 | 0.0028945 | 0.00259 | 0
Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 9.7158 | 10.25 | 10.25 | 10.0163 | 10.0148 | 9.87 | 0
E320-E300, Infiltration | 3.3904 | 2.95 | 2.97 | 3.5083 | 3.2773 | 2.01 | 0
E330-E300, 100% OA | 2.2296 | 2.32 | 2.37 | 2.6617 | 2.2587 | 2.77 | 0
E330-E320, OA-Infl | -1.1608 | -0.63 | -0.6 | -0.84659 | -1.0186 | 0.76 | 0
E340-E300, 50/50 OA/inf | 2.4702 | 2.43 | 2.45 | 2.7026 | 2.4705 | 2.85 | 0
E330-E340, OA-50/50 | -0.24056 | -0.11 | -0.08 | -0.040899 | -0.21187 | -0.08 | 0
E350-E300, Tstat Set Up | -3.1309 | -2.81 | -2.73 | -3.3505 | -3.5099 | -3.37 | 0
E360-E300, Overload | -7.5814 | -6.77 | -6.79 | -6.581 | -6.9551 | -6.72 | 0
E400-E300, Ec. T Ctrl | 2.156 | 3.95 | 3.97 | 4.3298 | 0 | 4.08 | 0
E410-E300, Ec. No Compr. | 1.8822 | 1.39 | 1.35 | 0 | 0 | 1.82 | 0
E420-E300, Ec. ODB Lim. | 0.16451 | 0.88 | 0.69 | 0.90472 | 0 | 0.83 | 0
E430-E300, Ec. Enth Ctrl | 0.20708 | 0.91 | 1.02 | 1.0997 | 0 | 1.24 | 0
E440-E300, Ec. Enth Lim | -0.28509 | 0.2 | 0.29 | 0.32416 | 0 | 0.3 | 0
E500-E300, 0%OA | 17.9113 | 0 | 0 | 9.9915 | 18.1158 | 15.8 | 0
E510-E500, PLR | -2.3476 | 0 | 0 | 0.11782 | -0.010621 | 0.11 | 0
E525-E520, EDB | -8.4071 | 0 | 0 | -7.2115 | -10.0881 | -14.8 | 0
E530-E500, Dry Coil | -19.7962 | 0 | 0 | -10.4047 | -24.4903 | -24.13 | 0
E545-E540, EDB (Dry) | -11.8961 | 0 | 0 | -7.5469 | -3.1763 | -14.62 | 0
Delta Hourly Integrated Maximum Total Consumptions | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total Consumption (Wh,e) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 968.3645 | 1019 | 993 | 576.3704 | 721 | 614 | 0
E320-E300, Infiltration | 1402.1615 | 1352 | 1379 | 993.1303 | 1172 | 1327 | 0
E330-E300, 100% OA | 1720.664 | 1648 | 1805 | 1360.526 | 1535 | 1787 | 0
E330-E320, OA-Infl | 318.5024 | 296 | 426 | 367.3957 | 363 | 460 | 0
E340-E300, 50/50 OA/inf | 1554.8648 | 1594 | 1588 | 1179.2169 | 1345 | 1553 | 0
E330-E340, OA-50/50 | 165.7992 | 54 | 217 | 181.3091 | 190 | 234 | 0
E350-E300, Tstat Set Up | 0.85194 | 90 | 0 | -0.0072418 | 0 | -2 | 0
E360-E300, Overload | 1143.4651 | 1172 | 1124 | 780.7195 | 931 | 1214 | 0
E400-E300, Ec. T Ctrl | 1.8307 | 0 | 75 | -0.01154 | 0 | -29 | 0
E410-E300, Ec. No Compr. | 1.8307 | 0 | 0 | 0 | 0 | 1 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | 1.0004e-10 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | 1.0004e-10 | 0 | -87 | 0
E500-E300, 0%OA | -1459.5539 | -1133 | -1177 | -1557.1915 | -1755 | -1274 | 0
E510-E500, PLR | 1038.4136 | 1159 | 1162 | 1012.234 | 1009 | 1070 | 0
E525-E520, EDB | -1668.6417 | -1451 | -1483 | -1673.579 | -1625 | -1099 | 0
E530-E500, Dry Coil | -2138.1546 | -2372 | -2370 | -2145.4765 | -2185 | -2185 | 0
E545-E540, EDB (Dry) | -1494.1291 | -1593 | -1593 | -1308.4538 | -1495 | -1514 | 0
Sensible + Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 5153.95 | 5349 | 5578 | 4315.0471 | 4759 | 4919 | 0
E320-E300, Infiltration | 8143.55 | 22412 | 22368 | 7039.5416 | 7402 | 7848 | 0
E330-E300, 100% OA | 11317.95 | 12227 | 33117 | 10540.4711 | 11476 | 10343 | 0
E330-E320, OA-Infl | 3174.4 | -10185 | 10749 | 3500.9295 | 4074 | 2495 | 0
E340-E300, 50/50 OA/inf | 9477.65 | 19418 | 28094 | 8550.9999 | 8864 | 9060 | 0
E330-E340, OA-50/50 | 1840.3 | -7191 | 5023 | 1989.4712 | 2612 | 1283 | 0
E350-E300, Tstat Set Up | -82.32 | 0 | -1 | -0.025077 | 0 | 5 | 0
E360-E300, Overload | 6683.11 | 9212 | 9564 | 5634.0125 | 5820 | 6379 | 0
E400-E300, Ec. T Ctrl | 9004.55 | 9142 | 18383 | 8054.7322 | 0 | 8702 | 0
E410-E300, Ec. No Compr. | -82.32 | 0 | 0 | 0 | 0 | 1 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | 2.7649e-10 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | 2.7649e-10 | 0 | -295 | 0
E500-E300, 0%OA | -4688.54 | -3694 | -3749 | -5401.0537 | -5935 | -4517 | 0
E510-E500, PLR | 3107.54 | 3481 | 3482 | 3538.1292 | 3381 | 3542 | 0
E525-E520, EDB | 410.17 | -412 | -412 | -166.7296 | 8 | -881 | 0
E530-E500, Dry Coil | -7651.41 | -8131 | -8131 | -8000.2799 | -7791 | -7929 | 0
E545-E540, EDB (Dry) | 500.2 | -291 | -292 | -273.7041 | -30 | -302 | 0
Sensible Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | -183.1 | -123 | -86 | -318.1104 | -379 | -259 | 0
E320-E300, Infiltration | 8038.2 | 7916 | 7867 | 8065.5499 | 7677 | 8059 | 0
E330-E300, 100% OA | 9948.7 | 10207 | 11285 | 11229.0176 | 10540 | 10513 | 0
E330-E320, OA-Infl | 1910.5 | 2291 | 3418 | 3163.4677 | 2863 | 2454 | 0
E340-E300, 50/50 OA/inf | 9551.5 | 8883 | 8881 | 9273.9256 | 9483 | 9272 | 0
E330-E340, OA-50/50 | 397.2 | 1324 | 2404 | 1955.092 | 1057 | 1241 | 0
E350-E300, Tstat Set Up | 0.1 | 0 | 0 | -0.039522 | 0 | -32 | 0
E360-E300, Overload | 8783.3 | 8908 | 8860 | 8946.1221 | 8524 | 9271 | 0
E400-E300, Ec. T Ctrl | 0.1 | 0 | 0 | -0.05333 | 0 | -31 | 0
E410-E300, Ec. No Compr. | -11.7 | 0 | 0 | 0 | 0 | -15 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | 2.9104e-11 | 0 | -15 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | 5.0204e-10 | 0 | -15 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | 3.0559e-10 | 0 | -33 | 0
E500-E300, 0%OA | -3728.2 | -3194 | -3197 | -3667.2651 | -4681 | -3090 | 0
E510-E500, PLR | 2180 | 2504 | 2505 | 2432.0566 | 2345 | 2451 | 0
E525-E520, EDB | 286.8 | -309 | -304 | -413.5213 | -210 | -717 | 0
E530-E500, Dry Coil | 284.9 | -433 | -433 | -139.7703 | 0 | -192 | 0
E545-E540, EDB (Dry) | 500.2 | -291 | -292 | -273.7041 | -35 | -302 | 0
Latent Coil Load (Wh,th) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 6271.3 | 5835 | 5876 | 6049.2222 | 5737 | 5685 | 0
E320-E300, Infiltration | 13511.6 | 22193 | 22109 | 12161.09 | 11322 | 11537 | 0
E330-E300, 100% OA | 18189.5 | 17637 | 31415 | 17001.6155 | 17809 | 17096 | 0
E330-E320, OA-Infl | 4677.9 | -4556 | 9306 | 4840.5255 | 6487 | 5559 | 0
E340-E300, 50/50 OA/inf | 15212.6 | 21147 | 26617 | 13840.6802 | 13850 | 13402 | 0
E330-E340, OA-50/50 | 2976.9 | -3510 | 4798 | 3160.9352 | 3959 | 3694 | 0
E350-E300, Tstat Set Up | 115.56 | -1 | -1 | 0.55759 | 380 | 1211 | 0
E360-E300, Overload | -360.54 | 722 | 942 | -1687.8651 | -1516 | -1458 | 0
E400-E300, Ec. T Ctrl | 17439.6 | 16274 | 23002 | 16172.5916 | 0 | 16253 | 0
E410-E300, Ec. No Compr. | 1503.2 | 0 | -3 | 0 | 0 | -15 | 0
E420-E300, Ec. ODB Lim. | 115.34 | 0 | 0 | -1.3824e-10 | 0 | 2 | 0
E430-E300, Ec. Enth Ctrl | 0 | 1801 | 1707 | 780.2398 | 0 | 2 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | -3 | -8.3674e-11 | 0 | -253 | 0
E500-E300, 0%OA | -1670.24 | -1571 | -1661 | -2686.1278 | -2570 | -2630 | 0
E510-E500, PLR | 927.1 | 990 | 990 | 1132.0803 | 1045 | 1112 | 0
E525-E520, EDB | 123.37 | -122 | -122 | 221.1694 | 212 | -144 | 0
E530-E500, Dry Coil | -7965.46 | -7733 | -7733 | -7798.7789 | -7626 | -7726.1 | 0
E545-E540, EDB (Dry) | -627.186 | 0 | 0 | -1636.359 | -841 | -1181 | 0
Delta Hourly Integrated Maximum and Minimum COP2 and Zone Conditions (IDB, Humidity Ratio, Relative Humidity) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Delta Hourly Integrated Maximum and Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | -0.025037 | 0.272 | 0.271 | 0.27226 | 0.25703 | 0.24 | 0
E320-E300, Infiltration | 0 | 1.274 | 1.11 | 0.041596 | 0.072694 | 0.5 | 0
E330-E300, 100% OA | 0 | 0.24 | 1.738 | 0.17299 | 0.25134 | 0.17 | 0
E330-E320, OA-Infl | 0 | -1.034 | 0.628 | 0.13139 | 0.17864 | -0.33 | 0
E340-E300, 50/50 OA/inf | 0 | 0.752 | 1.482 | 0.091522 | 0.14655 | 0.07 | 0
E330-E340, OA-50/50 | 0 | -0.512 | 0.256 | 0.081466 | 0.10479 | 0.1 | 0
E350-E300, Tstat Set Up | 0 | 0.02 | 0.006 | 0.42216 | 0.061488 | 0 | 0
E360-E300, Overload | 0.23263 | 0.559 | 0.57 | 0.50758 | 0.5614 | 0.56 | 0
E400-E300, Ec. T Ctrl | -0.091398 | 0.219 | 0.919 | 0.17297 | 0 | 0.17 | 0
E410-E300, Ec. No Compr. | -0.28043 | 0.034 | -0.002 | 0 | 0 | -0.04 | 0
E420-E300, Ec. ODB Lim. | -0.38705 | -0.062 | -0.098 | -0.078559 | 0 | 0.06 | 0
E430-E300, Ec. Enth Ctrl | -0.38705 | -0.064 | -0.098 | -0.11877 | 0 | 0.05 | 0
E440-E300, Ec. Enth Lim | -0.28486 | -0.095 | -0.098 | -0.11877 | 0 | -0.07 | 0
E500-E300, 0%OA | 0.1068 | 3.498 | 1.444 | 0.31113 | 0.31401 | 0.26 | 0
E510-E500, PLR | 0.4174 | 0 | 0 | 0.47259 | 0.50496 | 0.39 | 0
E525-E520, EDB | 0.90402 | 1.429 | 1.379 | 0.83955 | 0.83633 | 0.56 | 0
E530-E500, Dry Coil | -0.26907 | -3.386 | -1.451 | -0.31413 | -0.34458 | -0.26 | 0
E545-E540, EDB (Dry) | 0.79448 | 0.819 | 0.973 | 0.69873 | 0.48982 | 0.48 | 0
Minimum COP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.072169 | 0.052 | 0.05 | 0.092733 | 0.087015 | 0.06 | 0
E320-E300, Infiltration | 0.032137 | 0.003 | 0.004 | 0.048689 | 0.028893 | 0.02 | 0
E330-E300, 100% OA | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0
E330-E320, OA-Infl | 0 | -0.003 | -0.004 | 0.0054718 | 0.0088028 | 0.01 | 0
E340-E300, 50/50 OA/inf | 0.032137 | 0 | 0 | 0.054161 | 0.037696 | 0.03 | 0
E330-E340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300, Tstat Set Up | -0.0026372 | 0 | 0 | -8.3391e-08 | 0.00027963 | 0 | 0
E360-E300, Overload | 0.032137 | 0.001 | 0 | 0.054163 | 0.037696 | 0.03 | 0
E400-E300, Ec. T Ctrl | -0.011155 | -0.064 | -0.066 | -4.2365e-07 | 0 | 0 | 0
E410-E300, Ec. No Compr. | -0.0072339 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | -0.021929 | -0.064 | -0.066 | 4.885e-15 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | -0.010585 | -0.064 | -0.066 | 0 | 0 | 0 | 0
E500-E300, 0%OA | -0.10787 | -0.105 | -0.149 | -0.079652 | -0.11916 | -0.1 | 0
E510-E500, PLR | 0.20276 | 0.124 | 0 | 0.20451 | 0.21527 | 0.19 | 0
E525-E520, EDB | 0.46939 | 0.476 | 0.42 | 0.47145 | 0.56074 | 0.43 | 0
E530-E500, Dry Coil | -0.18393 | -0.198 | -0.154 | -0.20025 | -0.19318 | -0.19 | 0
E545-E540, EDB (Dry) | 0.4795 | 0.459 | 0.46 | 0.37917 | 0.54916 | 0.44 | 0
Delta Hourly Integrated Maximum and Minimum IDB | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.8779 | 1.78 | 1.61 | 1.5534 | 1.57 | 1 | 0
E320-E300, Infiltration | 6.1605 | 6.5 | 6.39 | 6.8407 | 7.27 | 5.46 | 0
E330-E300, 100% OA | 6.0322 | 6.61 | 6.89 | 6.493 | 6.85 | 5.11 | 0
E330-E320, OA-Infl | -0.1283 | 0.11 | 0.5 | -0.34771 | -0.42 | -0.35 | 0
E340-E300, 50/50 OA/inf | 6.1067 | 6.5 | 6.45 | 6.7419 | 7.1 | 5.39 | 0
E330-E340, OA-50/50 | -0.0745 | 0.11 | 0.44 | -0.24889 | -0.25 | -0.28 | 0
E350-E300, Tstat Set Up | 8.3842 | 9.83 | 9.83 | 9.9988 | 9.95 | 8.81 | 0
E360-E300, Overload | 7.5586 | 7.67 | 7.45 | 7.8165 | 7.95 | 6.94 | 0
E400-E300, Ec. T Ctrl | 0.9149 | 2.45 | 3.72 | 1.8999 | 0 | -0.15 | 0
E410-E300, Ec. No Compr. | 0.6257 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | -1.56e-11 | 0 | 0.04 | 0
E430-E300, Ec. Enth Ctrl | 0.9993 | 0 | 0 | 0.00048996 | 0 | 0.26 | 0
E440-E300, Ec. Enth Lim | 0.8453 | 0 | 0 | 0.00048996 | 0 | 0.07 | 0
E500-E300, 0%OA | -0.3945 | 0 | 0 | -0.001584 | -0.03 | -1.19 | 0
E510-E500, PLR | 0.2949 | 0 | 0 | 8.488e-07 | 0 | 0 | 0
E525-E520, EDB | 19.9568 | 18.95 | 19.12 | 19.7296 | 19.02 | 16.38 | 0
E530-E500, Dry Coil | 0.3106 | -0.05 | -0.05 | 0.0010308 | 0 | 0 | 0
E545-E540, EDB (Dry) | 19.525 | 19.89 | 19.89 | 19.9975 | 19.95 | 20 | 0
Minimum IDB (°C) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0 | 0 | 0 | -7.6877e-05 | 0 | 0 | 0
E320-E300, Infiltration | 0 | 1.94 | 1.95 | -0.97006 | 0 | 0 | 0
E330-E300, 100% OA | 0 | 0 | 0 | -0.0015637 | 0 | 0 | 0
E330-E320, OA-Infl | 0 | -1.94 | -1.95 | 0.96849 | 0 | 0 | 0
E340-E300, 50/50 OA/inf | 0 | 0 | 0 | -0.0015637 | 0 | 0 | 0
E330-E340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300, Overload | 0 | 0 | 0 | 0.00017992 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | 0 | 0 | 0 | -3.0198e-14 | 0 | 0 | 0
E410-E300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | -3.0198e-14 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | -3.0198e-14 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | -3.0198e-14 | 0 | 0.01 | 0
E500-E300, 0%OA | 0.49703 | -0.72 | -0.89 | 0.11004 | 0.54 | 17.05 | 0
E510-E500, PLR | 0 | 0 | 0 | 9.3018e-09 | 0 | 0 | 0
E525-E520, EDB | 0.13889 | 0.06 | 0.05 | 0.17939 | 0.03 | 19.44 | 0
E530-E500, Dry Coil | -0.00551 | 0 | 0 | 0.14539 | 0 | 0 | 0
E545-E540, EDB (Dry) | 0.22078 | 0.06 | 0.05 | 0.18093 | 0.03 | 18.06 | 0
Delta Hourly Integrated Maximum and Minimum Zone Humidity Ratio | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.0024658 | 0.005 | 0.0052 | 0.0019812 | 0.001975 | 0.0023 | 0
E320-E300, Infiltration | 0.0047326 | 0.0039 | 0.0039 | 0.0041823 | 0.00409 | 0.0043 | 0
E330-E300, 100% OA | 0.0043671 | 0.004 | 0.004 | 0.004303 | 0.003588 | 0.0043 | 0
E330-E320, OA-Infl | -0.0003655 | 0.0001 | 0.0001 | 0.00012066 | -0.000502 | 0 | 0
E340-E300, 50/50 OA/inf | 0.0045871 | 0.0039 | 0.0037 | 0.0041869 | 0.003815 | 0.0043 | 0
E330-E340, OA-50/50 | -0.00022 | 0.0001 | 0.0003 | 0.00011606 | -0.000227 | 0 | 0
E350-E300, Tstat Set Up | 0.0034739 | 0.0061 | 0.0062 | 0.0034245 | 0.003022 | 0.0032 | 0
E360-E300, Overload | 0.0001491 | 0 | 0 | -3.5233e-08 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | 0.0036593 | 0.0032 | 0.0033 | 0.0033728 | 0 | 0.0039 | 0
E410-E300, Ec. No Compr. | 0.0035512 | 0.0031 | 0.0032 | 0 | 0 | 0.0039 | 0
E420-E300, Ec. ODB Lim. | 0.0010125 | 0.0009 | 0.0004 | 0.0010861 | 0 | 0.0013 | 0
E430-E300, Ec. Enth Ctrl | 0.0029463 | 0.0018 | 0.0019 | 0.0026257 | 0 | 0.0024 | 0
E440-E300, Ec. Enth Lim | 2.85e-05 | 0 | 0 | 1.6639e-12 | 0 | 0 | 0
E500-E300, 0%OA | -0.0015646 | -0.0019 | -0.0019 | -0.0021408 | -0.001744 | -0.0019 | 0
E510-E500, PLR | 0.0001517 | 0 | 0.0001 | 1.0006e-05 | 3e-06 | 0 | 0
E525-E520, EDB | 0.010392 | 0.0103 | 0.0102 | 0.010744 | 0.01006 | 0.0067 | 0
E530-E500, Dry Coil | -0.0047305 | -0.0038 | -0.0037 | -0.0045893 | -0.006222 | -0.00473 | 0
E545-E540, EDB (Dry) | 0.0009051 | 0.0072 | 0.0059 | 4.3897e-15 | 0.003433 | 0.00129 | 0
Minimum Humidity Ratio (kg/kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 1e-08 | 0 | 0 | 1.4269e-05 | 5.1e-05 | -1e-05 | 0
E320-E300, Infiltration | 0 | 0 | 0 | 5.8778e-06 | 0 | 0 | 0
E330-E300, 100% OA | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | 0
E330-E320, OA-Infl | 0 | 0 | 0 | -5.8949e-06 | 0 | 0 | 0
E340-E300, 50/50 OA/inf | 0 | 0 | 0 | -1.7099e-08 | 0 | 0 | 0
E330-E340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300, Overload | 0 | 0 | 0 | -2.2215e-11 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | 0 | 0 | 0 | 3.0931e-12 | 0 | 0 | 0
E410-E300, Ec. No Compr. | 0 | 0 | 0 | 0 | 0 | 0 | 0
E420-E300, Ec. ODB Lim. | 0 | 0 | 0 | -7.6947e-13 | 0 | 0 | 0
E430-E300, Ec. Enth Ctrl | 0 | 0 | 0 | 3.0931e-12 | 0 | 0 | 0
E440-E300, Ec. Enth Lim | 0 | 0 | 0 | -9.3204e-13 | 0 | 0 | 0
E500-E300, 0%OA | 0.0049507 | 0 | 0 | 0.0050316 | 0.00494 | 0.00833 | 0
E510-E500, PLR | 0 | 0 | 0 | 0 | 0 | 0.0002 | 0
E525-E520, EDB | 0.00073266 | 0 | 0 | 0.00053199 | 0.000384 | 0.00883 | 0
E530-E500, Dry Coil | -0.00061959 | 0 | 0 | -0.00051756 | -0.001454 | -0.00367 | 0
E545-E540, EDB (Dry) | 0.0020983 | 0 | 0 | 0.0029798 | 0.003432 | 0.0028 | 0
Delta Hourly Integrated Maximum and Minimum Zone Relative Humidity | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 8.9137 | 30.83 | 31.85 | 10.1493 | 9 | 10.75 | 0
E320-E300, Infiltration | 13.0466 | 14.06 | 14.82 | 14.9388 | 15 | 14.44 | 0
E330-E300, 100% OA | 7.8699 | 9.11 | 9.09 | 8.8625 | 8 | 11.26 | 0
E330-E320, OA-Infl | -5.1767 | -4.95 | -5.73 | -6.0763 | -7 | -3.18 | 0
E340-E300, 50/50 OA/inf | 11.1401 | 12.02 | 12.41 | 12.7691 | 12 | 12.81 | 0
E330-E340, OA-50/50 | -3.2702 | -2.91 | -3.32 | -3.9066 | -4 | -1.55 | 0
E350-E300, Tstat Set Up | 0 | 11.77 | 12.27 | 0 | 2 | 5.21 | 0
E360-E300, Overload | 0 | 0 | 0 | -0.00017286 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | 14.9642 | 16.22 | 16.72 | 16.856 | 0 | 18.87 | 0
E410-E300, Ec. No Compr. | 14.4355 | 15.44 | 15.94 | 0 | 0 | 18.74 | 0
E420-E300, Ec. ODB Lim. | 2.0519 | 5.16 | 2.68 | 5.5009 | 0 | 6.41 | 0
E430-E300, Ec. Enth Ctrl | 11.9195 | 9.08 | 9.58 | 12.9398 | 0 | 11.5 | 0
E440-E300, Ec. Enth Lim | -0.065 | 0 | 0 | 8.1634e-09 | 0 | 0.07 | 0
E500-E300, 0%OA | 31.2108 | 0 | 0 | 32.2238 | 32 | -7.36 | 0
E510-E500, PLR | 0 | 0 | 0 | 0 | 0 | -2.57 | 0
E525-E520, EDB | 9.7701 | 0 | 0 | 6.3958 | 5 | -20.65 | 0
E530-E500, Dry Coil | -8.9555 | 0 | 0 | -8.302 | -21 | -24.07 | 0
E545-E540, EDB (Dry) | 29.6022 | 0 | 0 | 41.2182 | 50 | -15.82 | 0
Minimum Relative Humidity (%) | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | TRNSYS | DOE-2.2 | DOE21E-E | Energy+ | CODYRUN | HOT3000 | 0
0 | TRNSYS/TUD | DOE-2.2/NREL | DOE-2.1E-E/NREL | ENERGY+ v{{ engine.config["EnergyPlusVersion"] }}/GARD | CODYRUN/UR | HOT3000/NRCan | Your Software
E310-E300, Latent Gains | 0.0586 | 0 | 0 | 1.0832 | 1 | 0.99 | 0
E320-E300, Infiltration | 0 | 0 | 0 | 0.40959 | 0 | -2.02 | 0
E330-E300, 100% OA | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0
E330-E320, OA-Infl | 0 | 0 | 0 | -0.40947 | 0 | 2.02 | 0
E340-E300, 50/50 OA/inf | 0 | 0 | 0 | 0.00011523 | 0 | 0 | 0
E330-E340, OA-50/50 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E350-E300, Tstat Set Up | 0 | 0 | 0 | 0 | 0 | 0 | 0
E360-E300, Overload | 0 | 0 | 0 | -5.6978e-05 | 0 | 0 | 0
E400-E300, Ec. T Ctrl | -0.1222 | 0 | 0 | -0.46234 | 0 | -0.37 | 0
E410-E300, Ec. No Compr. | -0.1221 | 0 | 0 | 0 | 0 | -0.36 | 0
E420-E300, Ec. ODB Lim. | -0.1213 | 0 | 0 | -0.46224 | 0 | -0.35 | 0
E430-E300, Ec. Enth Ctrl | -0.1234 | 0 | 0 | -0.46235 | 0 | -0.36 | 0
E440-E300, Ec. Enth Lim | -0.1243 | 0 | 0 | -0.46235 | 0 | -0.4 | 0
E500-E300, 0%OA | 40.0742 | 0 | 0 | 39.0378 | 39 | 37.89 | 0
E510-E500, PLR | -1.3175 | 0 | 0 | 0.10666 | 0 | 0.32 | 0
E525-E520, EDB | -15.7395 | 0 | 0 | -15.0875 | -17 | -17.5 | 0
E530-E500, Dry Coil | -23.812 | 0 | 0 | -20.8644 | -26 | -19.15 | 0
E545-E540, EDB (Dry) | -19.3505 | 0 | 0 | -16.6007 | -12 | -19.6 | 0
0 | 0 | e300results.xls t:a476..m519; 07/19/04 | 0 | 0 | 0 | 0 | 0