## Data
Standard 140-2007 Furnace Test Results Comparison
EnergyPlus {{ engine.config["EnergyPlusVersion"] }} Set Convection coefficients, Standard 140-2007 Weather
Set convection Coefficients, Final WYEC2 weather, corrected PLF curve | [13 empty] | Space Temp (C)
[10 empty] | Energy to Space | Rate of Fuel Consumption | Fan Power | Furnace Input | Mean | Max | Min
Case HE100 - Base Case Building, 100% Efficient Furnace |  |  |  |  | Space | Htg Coil | Fan Run Time | Furnace Input | HE100 | 77.76 | 0.00026316 |  | 77.76 | 20 | 20 | 20
| Standard 140-2007 | EnergyPlus | Difference (%) |  | Temp (C) | Rate (W) | Fraction | (GJ) | HE110 | 77.76 | 0.00032895 |  | 97.2 | 20 | 20 | 20
Energy Delivered to Space (GJ) | 77.74 | 77.76 | 0.02573% | min | 20 | 10000 | 1 |  | HE120 | 31.104 | 0.00012954 |  | 38.2771 | 20 | 20 | 20
Average Rate of Fuel Consumption (m3/s) | 0.000263 | 0.00026316 | 0.06004% | max | 20 | 10000 | 1 | 77.76 | HE130 | 0 | 0 |  | 0 | 20 | 20 | 20
|  |  |  | mean | 20 |  |  |  | HE140 | 31.104 | 0.00013172 |  | 38.9211 | 20 | 20 | 20
[9 empty] | HE150 | 29.5999 | 0.00012528 | 432 | 37.0176 | 20.0333 | 20.425 | 20
Case HE110 - 80% Efficient Furnace | [8 empty] | HE160 | 30.4913 | 0.00012905 | 170.3571 | 38.1324 | 20.0003 | 20.0015 | 20
| Standard 140-2007 | EnergyPlus | Difference (%) | [5 empty] | HE170 | 29.5999 | 0.00012528 | 473.1306 | 37.0176 | 20.0333 | 20.425 | 20
Energy Delivered to Space (GJ) | 77.74 | 77.76 | 0.02573% | min | 20 | 10000 | 1 |  | HE210 | 42.0456 | 0.00017762 | 292.7469 | 52.4831 | 20.0003 | 20.0016 | 20
Average Rate of Fuel Consumption (m3/s) | 0.000329 | 0.00032895 | -0.016% | max | 20 | 10000 | 1 | 97.2 | HE220 | 39.8259 | 0.00016795 | 277.0665 | 49.6276 | 18.5373 | 20.0016 | 15
|  |  |  | mean | 20 |  |  |  | HE230 | 34.4954 | 0.0001464 | 480.7315 | 43.258 | 15.4637 | 20.0016 | 2.0135
Case HE120 - Simple Part Load Test
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 31.1 | 31.104 | 0.01291% | min | 20 | 4000.002 | 0.4
Average Rate of Fuel Consumption (m3/s) | 0.0001295 | 0.00012954 | 0.0299% | max | 20 | 4000.002 | 0.4 | 38.2771
|  |  |  | mean | 20
Case HE130 - No Load Test
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 0 | 0 | 0% | min | 20 | 0 | 1
Average Rate of Fuel Consumption (m3/s) | 0 | 0 | 0% | max | 20 | 0 | 1 | 0
|  |  |  | mean | 20
Case HE140 - Complex Part Load Test
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 31.1 | 31.104 | 0.0129% | min | 20 | 52.6003 | 0.00526
Average Rate of Fuel Consumption (m3/s) | 0.000132 | 0.00013172 | -0.2137% | max | 20 | 7947.3701 | 0.80461 | 38.9211
Total Fan Power (GJ) | 0 | 0 | 0% | mean | 20
Case HE150 - Continuous Circulating Fan Test
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 29.65 | 29.5999 | -0.1691% | min | 20 | 0 | 1
Average Rate of Fuel Consumption (m3/s) | 0.0001253 | 0.00012528 | -0.01911% | max | 20.425 | 7747.2937 | 1 | 37.0176
Total Fan Power (GJ) | 1.56 | 1.5552 | -0.3077% | mean | 20.0333
Continuous fan, heat added by fan when no
Case HE160 - Cycling Circulating Fan Test |  |  |  |  | heating load drives up temp
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 31.1 | 30.4913 | -1.957% | min | 20 | 51.5681 | 0.0051568
Average Rate of Fuel Consumption (m3/s) | 0.0001289 | 0.00012905 | 0.1156% | max | 20.0015 | 7790.0002 | 0.78847 | 38.1324
Total Fan Power (GJ) | 0.62 | 0.61329 | -1.083% | mean | 20.0003
Case HE170 - Draft Fan Test
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) | 29.65 | 29.5999 | -0.1691% | min | 20 | 0 | 1
Average Rate of Fuel Consumption (m3/s) | 0.0001253 | 0.00012528 | -0.01911% | max | 20.425 | 7747.2937 | 1 | 37.0176
Total Fan Power (GJ) | 1.7034 | 1.7033 | -0.01043% | mean | 20.0333
Continuous fan, heat added by fan when no
Standard 140-2007 Furnace Test Results Comparison |  |  |  |  | heating load drives up temp
EnergyPlus {{ engine.config["EnergyPlusVersion"] }} Set Convection coefficients, Standard 140-2007 Weather
Set convection Coefficients, Final WYEC2 weather, corrected PLF curve
Case HE210 - Realistic Weather Data
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) |  | 42.0456
Average Rate of Fuel Consumption (m3/s) |  | 0.00017762
Total Circulating Fan Power (GJ) |  | 0.84396
Total Draft Fan Power (GJ) |  | 0.20993
Average Space Temperature (C) |  | 20.0003
Minimum Space Temperature (C) |  | 20
Time of Minimum Temperature, Month/Day |  | 02/12
Time of Minimum Temperature, Hour |  | 09:00
Maximum Space Temperature (C) |  | 20.0016
Time of Maximum Temperature, Month/Day |  | 01/29
Time of Maximum Temperature, Hour |  | 08:00
Furnace Input (GJ) |  | 52.4831
Case HE220 - Setback Thermostat
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) |  | 39.8259
Average Rate of Fuel Consumption (m3/s) |  | 0.00016795
Total Circulating Fan Power (GJ) |  | 0.79893
Total Draft Fan Power (GJ) |  | 0.19851
Average Space Temperature (C) |  | 18.5373
Minimum Space Temperature (C) |  | 15
Time of Minimum Temperature, Month/Day |  | 02/20
Time of Minimum Temperature, Hour |  | 02:00
Maximum Space Temperature (C) |  | 20.0016
Time of Maximum Temperature, Month/Day |  | 01/29
Time of Maximum Temperature, Hour |  | 09:00
Furnace Input (GJ) |  | 49.6276
Case HE230 - Undersized Furnace
| Standard 140-2007 | EnergyPlus | Difference (%)
Energy Delivered to Space (GJ) |  | 34.4954
Average Rate of Fuel Consumption (m3/s) |  | 0.0001464
Total Circulating Fan Power (GJ) |  | 1.3846
Total Draft Fan Power (GJ) |  | 0.34606
Average Space Temperature (C) |  | 15.4637
Minimum Space Temperature (C) |  | 2.0135
Time of Minimum Temperature, Month/Day |  | 01/27
Time of Minimum Temperature, Hour |  | 06:00
Maximum Space Temperature (C) |  | 20.0016
Time of Maximum Temperature, Month/Day |  | 03/15
Time of Maximum Temperature, Hour |  | 22:00
Furnace Input (GJ) |  | 43.258