## EPlus Results
EnergyPlus Results for Standard 140-2007 HVAC -Furnace Analytical Test HE170
Sinusoid change in outdoor temperature, mean=0C, swing=20C
Date/Time | Hour of Year | EnergyPlus Outdoor Temperature (C) | Environment:Site Diffuse Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | Environment:Site Direct Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | ZONE ONE:Zone Mean Air Temperature [C](Hourly:OUTVARSCHED) | ZONE ONE:Zone Air System Sensible Heating Energy [J](Hourly:OUTVARSCHED) | GAS FURNACE 1 SUPPLY FAN:Fan Electric Power [W](Hourly:OUTVARSCHED) | EnergyPlus Heating Coil Output (W) | EnergyPlus Furnace Input (W) | GAS FURNACE 1 SUPPLY FAN:Fan Runtime Fraction [](Hourly:OUTVARSCHED) | GAS FURNACE 1 HEATING COIL:Heating Coil Electric Power [W](Hourly:OUTVARSCHED) | EnergyPlus Total Fan Power (W)
01/01 01:00:00 | 1 | 3.25 | 0 | 0 | 20 | 12060525.9624 | 200 | 3150.1461 | 3857.1097 | 1 | 15.4284 | 215.4284
01/01 02:00:00 | 2 | 8.2 | 0 | 0 | 20 | 8496492.0823 | 200 | 2160.1367 | 2638.2268 | 1 | 10.5529 | 210.5529
01/01 03:00:00 | 3 | 12.5625 | 0 | 0 | 20 | 5355423.8011 | 200 | 1287.6177 | 1576.3972 | 1 | 6.3056 | 206.3056
01/01 04:00:00 | 4 | 16.1 | 0 | 0 | 20 | 2808332.4246 | 200 | 580.0923 | 714.4586 | 1 | 2.8578 | 202.8578
01/01 05:00:00 | 5 | 18.55 | 0 | 0 | 20.0087 | 1084791.6591 | 200 | 105.0433 | 130.1674 | 1 | 0.52067 | 200.5207
01/01 06:00:00 | 6 | 19.7375 | 0 | 0 | 20.2076 | 604039.9089 | 200 | 0 | 0 | 1 | 0 | 200
01/01 07:00:00 | 7 | 19.5625 | 0 | 0 | 20.425 | 687424.5465 | 200 | 0 | 0 | 1 | 0 | 200
01/01 08:00:00 | 8 | 18.05 | 0 | 0 | 20.158 | 1173044.987 | 200 | 82.2918 | 101.8193 | 1 | 0.40728 | 200.4073
01/01 09:00:00 | 9 | 15.3 | 0 | 0 | 20.0011 | 3365730.4781 | 200 | 733.5124 | 901.9724 | 1 | 3.6079 | 203.6079
01/01 10:00:00 | 10 | 11.5375 | 0 | 0 | 20 | 6089247.3625 | 200 | 1491.4523 | 1824.0728 | 1 | 7.2963 | 207.2963
01/01 11:00:00 | 11 | 7 | 0 | 0 | 20 | 9357108.8806 | 200 | 2399.1969 | 2930.6319 | 1 | 11.7225 | 211.7225
01/01 12:00:00 | 12 | 1.95 | 0 | 0 | 20 | 12993712.4583 | 200 | 3409.3646 | 4180.2198 | 1 | 16.7209 | 216.7209
01/01 13:00:00 | 13 | -3.25 | 0 | 0 | 20 | 16738183.8857 | 200 | 4449.4955 | 5496.6699 | 1 | 21.9867 | 221.9867
01/01 14:00:00 | 14 | -8.2 | 0 | 0 | 20 | 20302570.4855 | 200 | 5439.6029 | 6778.2499 | 1 | 27.113 | 227.113
01/01 15:00:00 | 15 | -12.5625 | 0 | 0 | 20 | 23443896.0615 | 200 | 6312.1934 | 7923.4498 | 1 | 31.6938 | 231.6938
01/01 16:00:00 | 16 | -16.1 | 0 | 0 | 20 | 25991175.0875 | 200 | 7019.7709 | 8853.8384 | 1 | 35.4154 | 235.4154
01/01 17:00:00 | 17 | -18.55 | 0 | 0 | 20 | 27755436.3588 | 200 | 7509.8434 | 9493.634 | 1 | 37.9745 | 237.9745
01/01 18:00:00 | 18 | -19.7375 | 0 | 0 | 20 | 28610257.1487 | 200 | 7747.2937 | 9800.8992 | 1 | 39.2036 | 239.2036
01/01 19:00:00 | 19 | -19.5625 | 0 | 0 | 20 | 28485267.1467 | 200 | 7712.5742 | 9756.1499 | 1 | 39.0246 | 239.0246
01/01 20:00:00 | 20 | -18.05 | 0 | 0 | 20 | 27396057.741 | 200 | 7410.016 | 9363.9151 | 1 | 37.4557 | 237.4557
01/01 21:00:00 | 21 | -15.3 | 0 | 0 | 20 | 25416229.357 | 200 | 6860.0637 | 8644.2699 | 1 | 34.5771 | 234.5771
01/01 22:00:00 | 22 | -11.5375 | 0 | 0 | 20 | 22707357.1129 | 200 | 6107.5992 | 7654.2158 | 1 | 30.6169 | 230.6169
01/01 23:00:00 | 23 | -7 | 0 | 0 | 20 | 19440454.6989 | 200 | 5200.1263 | 6466.0256 | 1 | 25.8641 | 225.8641
01/01 24:00:00 | 24 | -1.95 | 0 | 0 | 20 | 15804513.9252 | 200 | 4190.1428 | 5165.3704 | 1 | 20.6615 | 220.6615
[8 empty] | 91357.576 | 114251.7637 |  |  | 5257.0071
| a | 0.0080473
| b | 0.87564
| c | 0.2925
| d | -0.17624
| PLR | HIR
| 0.1 | 0.09836
| 0.2 | 0.19347
| 0.3 | 0.29231
| 0.4 | 0.39383
| 0.5 | 0.49696
| 0.6 | 0.60067
| 0.7 | 0.70387
| 0.8 | 0.80553
| 0.9 | 0.90457
| 1 | 0.99995

## Furnace BESTEST
Standard 140-2007 HVAC -Furnace Results
Data taken from User's Manual
Sinusoidal change in outdoor temperature
| Hour | T_out_air | Load Delivered
|  | Standard 140-2007 Outdoor Temperature (C) | Standard 140-2007 Heating Coil Output (W) | Standard 140-2007 Furnace Input (W) | Standard 140-2007 Total Fan Power (W)
| 1 | 5.18 | 2764.03 | 3358.79 | 214
| 2 | 10 | 1799.53 | 2175.84 | 209
| 3 | 14.14 | 971.3 | 1196.21 | 205
| 4 | 17.32 | 335.77 | 472.15 | 202
| 5 | 19.32 | 0 | 0 | 200
| 6 | 20 | 0 | 0 | 200
| 7 | 19.32 | 0 | 0 | 200
| 8 | 17.32 | 335.77 | 472.15 | 202
| 9 | 14.14 | 971.3 | 1196.21 | 205
| 10 | 10 | 1799.53 | 2175.84 | 209
| 11 | 5.18 | 2764.03 | 3358.79 | 214
| 12 | 0 | 3799.07 | 4665.79 | 219
| 13 | -5.18 | 4834.1 | 5997.33 | 224
| 14 | -10 | 5798.6 | 7247.32 | 229
| 15 | -14.14 | 6626.83 | 8318.55 | 233
| 16 | -17.32 | 7262.36 | 9134.2 | 236
| 17 | -19.32 | 7661.87 | 9642.42 | 238
| 18 | -20 | 7798.13 | 9814.78 | 239
| 19 | -19.32 | 7661.87 | 9642.42 | 238
| 20 | -17.32 | 7262.36 | 9134.2 | 236
| 21 | -14.14 | 6626.83 | 8318.55 | 233
| 22 | -10 | 5798.6 | 7247.32 | 229
| 23 | -5.18 | 4834.1 | 5997.33 | 224
| 24 | 0 | 3799.07 | 4665.79 | 219
|  |  | 91505.05 | 114231.98 | 5257