## EPlus Results
EnergyPlus Results for Standard 140-2007 HVAC -Furnace Analytical Test HE210
Ottawa Weather File
Date/Time | Hour of Year | EnergyPlus Outdoor Temperature (C) | Environment:Site Diffuse Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | Environment:Site Direct Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | ZONE ONE:Zone Mean Air Temperature [C](Hourly:OUTVARSCHED) | ZONE ONE:Zone Air System Sensible Heating Energy [J](Hourly:OUTVARSCHED) | EnergyPlus Supply Fan Power (W) | EnergyPlus Heating Coil Output (W) | EnergyPlus Furnace Input (W) | GAS FURNACE 1 SUPPLY FAN:Fan Runtime Fraction [](Hourly:OUTVARSCHED) | EnergyPlus Draft Fan Power (W) | EnergyPlus Total Fan Power (W)
01/01 01:00:00 | 1 | -4.2997 | 0 | 0 | 20 | 16668978.7715 | 90.7896 | 4539.4822 | 5614.5185 | 0.45395 | 22.4581 | 113.2477
01/01 02:00:00 | 2 | 1.3948 | 0 | 0 | 20 | 12564388.9994 | 68.4335 | 3421.6746 | 4194.9473 | 0.34217 | 16.7798 | 85.2133
01/01 03:00:00 | 3 | 3.6172 | 0 | 0 | 20 | 10602240.822 | 57.7464 | 2887.3205 | 3530.4846 | 0.28873 | 14.1219 | 71.8683
01/01 04:00:00 | 4 | 4.2712 | 0 | 0 | 20 | 9693483.9872 | 52.7968 | 2639.8377 | 3225.2673 | 0.26398 | 12.9011 | 65.6978
01/01 05:00:00 | 5 | 3.9379 | 0 | 0 | 20 | 9548567.0362 | 52.0074 | 2600.3723 | 3176.7368 | 0.26004 | 12.7069 | 64.7144
01/01 06:00:00 | 6 | 3.3036 | 0 | 0 | 20 | 9665117.431 | 52.6423 | 2632.1126 | 3215.7531 | 0.26321 | 12.863 | 65.5053
01/01 07:00:00 | 7 | 1.6534 | 0 | 0 | 20 | 11159669.1645 | 60.7825 | 3039.1256 | 3718.5791 | 0.30391 | 14.8743 | 75.6568
01/01 08:00:00 | 8 | 0.38948 | 6.5 | 45.875 | 20 | 12518258.5813 | 68.1822 | 3409.1118 | 4178.7269 | 0.34091 | 16.7149 | 84.8971
01/01 09:00:00 | 9 | 0.48477 | 56.0625 | 355.125 | 20 | 12546413.3366 | 68.3356 | 3416.7792 | 4188.274 | 0.34168 | 16.7531 | 85.0887
01/01 10:00:00 | 10 | 0.88673 | 106.5625 | 342.4375 | 20 | 12159346.6172 | 66.2274 | 3311.3689 | 4056.6533 | 0.33114 | 16.2266 | 82.454
01/01 11:00:00 | 11 | 1.0734 | 101 | 26.625 | 20 | 11754414.5175 | 64.0219 | 3201.0933 | 3919.3074 | 0.32011 | 15.6772 | 79.6991
01/01 12:00:00 | 12 | 0.97508 | 106.4375 | 4.875 | 20 | 11592025.2746 | 63.1374 | 3156.8696 | 3864.3069 | 0.31569 | 15.4572 | 78.5946
01/01 13:00:00 | 13 | 0.6647 | 137.6875 | 19.6875 | 20 | 11592006.4962 | 63.1373 | 3156.8645 | 3864.3005 | 0.31569 | 15.4572 | 78.5945
01/01 14:00:00 | 14 | -0.19104 | 115.4375 | 3.125 | 20 | 12355851.2328 | 67.2977 | 3364.8832 | 4123.5462 | 0.33649 | 16.4942 | 83.7918
01/01 15:00:00 | 15 | -1.5228 | 87.25 | 5.5 | 20 | 13534917.8712 | 73.7196 | 3685.9798 | 4525.9872 | 0.3686 | 18.1039 | 91.8235
01/01 16:00:00 | 16 | -2.5601 | 42.6875 | 10 | 20 | 14237597.4285 | 77.5468 | 3877.3413 | 4767.2114 | 0.38773 | 19.0688 | 96.6157
01/01 17:00:00 | 17 | -3.4379 | 5.125 | 0.8125 | 20 | 14894258.5005 | 81.1234 | 4056.1706 | 4993.7858 | 0.40562 | 19.9751 | 101.0986
01/01 18:00:00 | 18 | -3.7856 | 0 | 0 | 20 | 15191971.9734 | 82.7449 | 4137.2473 | 5096.7591 | 0.41372 | 20.387 | 103.132
01/01 19:00:00 | 19 | -3.9367 | 0 | 0 | 20 | 15461598.9076 | 84.2135 | 4210.6751 | 5190.2586 | 0.42107 | 20.761 | 104.9745
01/01 20:00:00 | 20 | -4.7242 | 0 | 0 | 20 | 16118258.9675 | 87.7901 | 4389.5041 | 5418.6541 | 0.43895 | 21.6746 | 109.4647
01/01 21:00:00 | 21 | -6.0919 | 0 | 0 | 20 | 17134919.052 | 93.3274 | 4666.3723 | 5774.1343 | 0.46664 | 23.0965 | 116.424
01/01 22:00:00 | 22 | -7.6598 | 0 | 0 | 20 | 18331850.9618 | 99.8467 | 4992.3341 | 6195.3548 | 0.49923 | 24.7814 | 124.6281
01/01 23:00:00 | 23 | -9.0626 | 0 | 0 | 20 | 19555851.1339 | 106.5134 | 5325.6675 | 6628.8763 | 0.53257 | 26.5155 | 133.0289
01/01 24:00:00 | 24 | -9.994 | 0 | 0 | 20 | 20510259.1347 | 111.7117 | 5585.5826 | 6968.5407 | 0.55856 | 27.8742 | 139.5858
[8 empty] | 89703.7708 | 110430.9643 |  |  | 2235.7993
| a | 0.0080473
| b | 0.87564
| c | 0.2925
| d | -0.17624
| PLR | HIR
| 0.1 | 0.09836
| 0.2 | 0.19347
| 0.3 | 0.29231
| 0.4 | 0.39383
| 0.5 | 0.49696
| 0.6 | 0.60067
| 0.7 | 0.70387
| 0.8 | 0.80553
| 0.9 | 0.90457
| 1 | 0.99995

## Furnace BESTEST
HVAC Standard 140-2007-Furnace Results
Data taken from User's Manual
Ottawa Weather File
| Hour | T_out_air | Load Delivered
|  | BESTEST Outdoor Temperature (C) | BESTEST Heating Coil Output (W) | BESTEST Furnace Input (W) | BESTEST Total Fan Power (W)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
|  |  | 0 | 0 | 0