## EPlus Results
EnergyPlus Results for Standard 140-2007 HVAC -Furnace Analytical Test HE220
Ottawa Weather File
Date/Time | Hour of Year | EnergyPlus Outdoor Temperature (C) | Environment:Site Diffuse Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | Environment:Site Direct Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | EnergyPlus Space Temperature (C) | ZONE ONE:Zone Air System Sensible Heating Energy [J](Hourly:OUTVARSCHED) | EnergyPlus Supply Fan Power (W) | Energy Plus Heating Coil Output (W) | EnegyPlus Furnace Input (W) | GAS FURNACE 1 SUPPLY FAN:Fan Runtime Fraction [](Hourly:OUTVARSCHED) | EnergyPlus Draft Fan Power (W) | EnergyPlus Total Fan Power (W)
01/01 01:00:00 | 1 | -3.15 | 0 | 0 | 15 | 13064401.4519 | 71.1569 | 3557.8433 | 4368.6557 | 0.35578 | 17.4746 | 88.6315
01/01 02:00:00 | 2 | 2.55 | 0 | 0 | 15 | 8961634.2322 | 48.8106 | 2440.5322 | 2980.9696 | 0.24405 | 11.9239 | 60.7345
01/01 03:00:00 | 3 | 5.275 | 0 | 0 | 15 | 7000230.4434 | 38.1276 | 1906.3808 | 2328.4721 | 0.19064 | 9.3139 | 47.4415
01/01 04:00:00 | 4 | 6.5375 | 0 | 0 | 15 | 6091945.5648 | 33.1805 | 1659.0266 | 2027.5896 | 0.1659 | 8.1104 | 41.2909
01/01 05:00:00 | 5 | 6.7375 | 0 | 0 | 15 | 5947292.8507 | 32.3927 | 1619.6331 | 1979.7201 | 0.16196 | 7.9189 | 40.3115
01/01 06:00:00 | 6 | 6.575 | 0 | 0 | 15 | 6064029.1584 | 33.0285 | 1651.4241 | 2018.3475 | 0.16514 | 8.0734 | 41.1019
01/01 07:00:00 | 7 | 4.5 | 0 | 0 | 19.8991 | 15249236.1363 | 84.1005 | 4196.4146 | 5195.5705 | 0.4205 | 20.7823 | 104.8828
01/01 08:00:00 | 8 | 2.6125 | 6.5 | 45.875 | 20 | 12523157.5073 | 68.2089 | 3410.4466 | 4180.3945 | 0.34104 | 16.7216 | 84.9305
01/01 09:00:00 | 9 | 2.575 | 56.0625 | 355.125 | 20 | 12549552.1756 | 68.3527 | 3417.634 | 4189.3427 | 0.34176 | 16.7574 | 85.1101
01/01 10:00:00 | 10 | 3.1125 | 106.5625 | 342.4375 | 20 | 12161823.896 | 66.2409 | 3312.0435 | 4057.4946 | 0.3312 | 16.23 | 82.4708
01/01 11:00:00 | 11 | 3.675 | 101 | 26.625 | 20 | 11756369.6755 | 64.0325 | 3201.6257 | 3919.9698 | 0.32016 | 15.6799 | 79.7124
01/01 12:00:00 | 12 | 3.9 | 106.4375 | 4.875 | 20 | 11593724.8162 | 63.1466 | 3157.3325 | 3864.8821 | 0.31573 | 15.4595 | 78.6062
01/01 13:00:00 | 13 | 3.9 | 137.6875 | 19.6875 | 20 | 11593576.8512 | 63.1458 | 3157.2922 | 3864.832 | 0.31573 | 15.4593 | 78.6052
01/01 14:00:00 | 14 | 2.8375 | 115.4375 | 3.125 | 20 | 12357168.6425 | 67.3048 | 3365.242 | 4123.9941 | 0.33652 | 16.496 | 83.8008
01/01 15:00:00 | 15 | 1.2 | 87.25 | 5.5 | 20 | 13535957.6186 | 73.7253 | 3686.263 | 4526.3434 | 0.36863 | 18.1054 | 91.8306
01/01 16:00:00 | 16 | 0.225 | 42.6875 | 10 | 20 | 14238418.0347 | 77.5513 | 3877.5648 | 4767.4938 | 0.38776 | 19.07 | 96.6213
01/01 17:00:00 | 17 | -0.6875 | 5.125 | 0.8125 | 20 | 14894906.1526 | 81.1269 | 4056.347 | 4994.0097 | 0.40563 | 19.976 | 101.103
01/01 18:00:00 | 18 | -1.1 | 0 | 0 | 20 | 15192534.9518 | 82.748 | 4137.4006 | 5096.9541 | 0.41374 | 20.3878 | 103.1358
01/01 19:00:00 | 19 | -1.475 | 0 | 0 | 20 | 15462071.2041 | 84.2161 | 4210.8037 | 5190.4225 | 0.42108 | 20.7617 | 104.9778
01/01 20:00:00 | 20 | -2.3875 | 0 | 0 | 20 | 16118631.721 | 87.7921 | 4389.6056 | 5418.784 | 0.43896 | 21.6751 | 109.4672
01/01 21:00:00 | 21 | -3.8 | 0 | 0 | 20 | 17135213.2425 | 93.329 | 4666.4524 | 5774.2374 | 0.46665 | 23.0969 | 116.426
01/01 22:00:00 | 22 | -5.4625 | 0 | 0 | 20 | 18332083.1476 | 99.8479 | 4992.3974 | 6195.4367 | 0.49924 | 24.7817 | 124.6297
01/01 23:00:00 | 23 | -7.1625 | 0 | 0 | 20 | 19556034.3833 | 106.5143 | 5325.7174 | 6628.9414 | 0.53257 | 26.5158 | 133.0301
01/01 24:00:00 | 24 | -8.4875 | 0 | 0 | 15.1592 | 12829768.9137 | 69.7323 | 3486.6158 | 4310.4482 | 0.34866 | 17.2418 | 86.9741
[8 empty] | 82882.0389 | 102003.3065 |  |  | 2065.8262
| a | 0.0080473
| b | 0.87564
| c | 0.2925
| d | -0.17624
| PLR | HIR
| 0.1 | 0.09836
| 0.2 | 0.19347
| 0.3 | 0.29231
| 0.4 | 0.39383
| 0.5 | 0.49696
| 0.6 | 0.60067
| 0.7 | 0.70387
| 0.8 | 0.80553
| 0.9 | 0.90457
| 1 | 0.99995

## Furnace BESTEST
Standard 140-2007 HVAC -Furnace Results
Data taken from User's Manual
Ottawa Weather File
| Hour | T_out_air | Load Delivered
|  | BESTEST Outdoor Temperature (C) | BESTEST Heating Coil Output (W) | BESTEST Furnace Input (W) | BESTEST Total Fan Power (W)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
|  |  | 0 | 0 | 0