## EPlus Results
EnergyPlus Results for Standard 140-2007 HVAC -Furnace Analytical Test HE230
Ottawa Weather File
Date/Time | Hour of Year | EnergyPlus Outdoor Temperature (C) | Environment:Site Diffuse Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | Environment:Site Direct Solar Radiation Rate per Area [W/m2](Hourly:OUTVARSCHED) | EnergyPlus Space Temperature (C) | ZONE ONE:Zone Air System Sensible Heating Energy [J](Hourly:OUTVARSCHED) | EnergyPlus Supply Fan Power (W) | EnergyPlus Heating Coil Output (W) | EnergyPlus Furnace Input (W) | GAS FURNACE 1 SUPPLY FAN:Fan Runtime Fraction [](Hourly:OUTVARSCHED) | EnergyPlus Draft Fan Power (W) | EnergyPlus Total Fan Power (W)
01/01 01:00:00 | 1 | -3.15 | 0 | 0 | 15.0007 | 13066199.532 | 140.6816 | 3489.0447 | 4395.1138 | 0.70341 | 35.1609 | 175.8425
01/01 02:00:00 | 2 | 2.55 | 0 | 0 | 15 | 8962454.3903 | 95.7525 | 2393.8121 | 2966.2064 | 0.47876 | 23.7297 | 119.4821
01/01 03:00:00 | 3 | 5.275 | 0 | 0 | 15 | 7000855.2824 | 74.7955 | 1869.8866 | 2297.2229 | 0.37398 | 18.3778 | 93.1732
01/01 04:00:00 | 4 | 6.5375 | 0 | 0 | 15 | 6092423.6589 | 65.09 | 1627.2499 | 1992.9241 | 0.32545 | 15.9434 | 81.0334
01/01 05:00:00 | 5 | 6.7375 | 0 | 0 | 15 | 5947688.7322 | 63.5437 | 1588.5921 | 1944.7799 | 0.31772 | 15.5582 | 79.1019
01/01 06:00:00 | 6 | 6.575 | 0 | 0 | 15 | 6064367.1972 | 64.7902 | 1619.7562 | 1983.5558 | 0.32395 | 15.8684 | 80.6587
01/01 07:00:00 | 7 | 4.5 | 0 | 0 | 19.36 | 14203486.5907 | 155.6017 | 3875.7363 | 4861.5213 | 0.77801 | 38.8922 | 194.4939
01/01 08:00:00 | 8 | 2.6125 | 6.5 | 45.875 | 20.0007 | 12532941.0768 | 134.8 | 3346.5928 | 4212.5003 | 0.674 | 33.7 | 168.5
01/01 09:00:00 | 9 | 2.575 | 56.0625 | 355.125 | 20.0007 | 12550060.0033 | 134.9914 | 3351.1251 | 4218.4811 | 0.67496 | 33.7478 | 168.7392
01/01 10:00:00 | 10 | 3.1125 | 106.5625 | 342.4375 | 20.0006 | 12162185.1733 | 130.6364 | 3247.7372 | 4082.3878 | 0.65318 | 32.6591 | 163.2955
01/01 11:00:00 | 11 | 3.675 | 101 | 26.625 | 20.0004 | 11756551.7686 | 126.08 | 3139.6162 | 3939.9986 | 0.6304 | 31.52 | 157.5999
01/01 12:00:00 | 12 | 3.9 | 106.4375 | 4.875 | 20.0003 | 11593986.0634 | 124.2546 | 3096.2965 | 3882.9556 | 0.62127 | 31.0636 | 155.3182
01/01 13:00:00 | 13 | 3.9 | 137.6875 | 19.6875 | 20.0003 | 11593845.8681 | 124.253 | 3096.2597 | 3882.9072 | 0.62127 | 31.0633 | 155.3163
01/01 14:00:00 | 14 | 2.8375 | 115.4375 | 3.125 | 20.0006 | 12358103.6194 | 132.8372 | 3300.005 | 4151.1626 | 0.66419 | 33.2093 | 166.0465
01/01 15:00:00 | 15 | 1.2 | 87.25 | 5.5 | 20.0011 | 13537189.2215 | 146.0355 | 3614.3291 | 4563.6106 | 0.73018 | 36.5089 | 182.5444
01/01 16:00:00 | 16 | 0.225 | 42.6875 | 10 | 20.0014 | 14239577.8234 | 153.8371 | 3801.6131 | 4807.4085 | 0.76919 | 38.4593 | 192.2963
01/01 17:00:00 | 17 | -0.6875 | 5.125 | 0.8125 | 20.0015 | 14896184.3439 | 161.0441 | 3976.7982 | 5032.6283 | 0.80522 | 40.261 | 201.3051
01/01 18:00:00 | 18 | -1.1 | 0 | 0 | 20.0016 | 15193728.4079 | 164.2851 | 4056.1956 | 5133.9097 | 0.82143 | 41.0713 | 205.3564
01/01 19:00:00 | 19 | -1.475 | 0 | 0 | 20.0016 | 15463289.3569 | 167.1938 | 4128.167 | 5224.8055 | 0.83597 | 41.7984 | 208.9922
01/01 20:00:00 | 20 | -2.3875 | 0 | 0 | 20.0016 | 16119749.6637 | 174.18 | 4303.5226 | 5443.1262 | 0.8709 | 43.545 | 217.725
01/01 21:00:00 | 21 | -3.8 | 0 | 0 | 20.0013 | 17135787.3954 | 184.6588 | 4575.2389 | 5770.587 | 0.92329 | 46.1647 | 230.8235
01/01 22:00:00 | 22 | -5.4625 | 0 | 0 | 19.9977 | 18318433.4392 | 196.1805 | 4890.9674 | 6130.5602 | 0.9809 | 49.0445 | 245.2249
01/01 23:00:00 | 23 | -7.1625 | 0 | 0 | 19.7255 | 18912499.8251 | 200 | 5000 | 6249.6826 | 1 | 49.9975 | 249.9975
01/01 24:00:00 | 24 | -8.4875 | 0 | 0 | 15.1182 | 13360388.7853 | 143.0977 | 3550.1248 | 4466.0483 | 0.71549 | 35.7284 | 178.8261
[8 empty] | 80938.6669 | 101634.084 |  |  | 4071.693
| a | 0.0080473
| b | 0.87564
| c | 0.2925
| d | -0.17624
| PLR | HIR
| 0.1 | 0.09836
| 0.2 | 0.19347
| 0.3 | 0.29231
| 0.4 | 0.39383
| 0.5 | 0.49696
| 0.6 | 0.60067
| 0.7 | 0.70387
| 0.8 | 0.80553
| 0.9 | 0.90457
| 1 | 0.99995

## Furnace BESTEST
Standard 140-2007 HVAC -Furnace Results
Data taken from User's Manual
Ottawa Weather File
| Hour | T_out_air | Load Delivered
|  | BESTEST Outdoor Temperature (C) | BESTEST Heating Coil Output (W) | BESTEST Furnace Input (W) | BESTEST Total Fan Power (W)
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
|  |  | 0 | 0 | 0