## Ver-Build Title
EnergyPlus 8.2.0

## Test G2
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G2: Solar Position
|  | London |  |  |  | Manchester |  |  |  | Edinburgh
| Time | 51.48°N/0.45°W |  |  |  | 53.25°N/2.27°W |  |  |  | 55.95°N/3.35°W
| (hh/dd/mm) | Azimuth (°) |  | Altitude(°) |  | Azimuth (°) |  | Altitude(°) |  | Azimuth (°) |  | Altitude(°)
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User
| 1200/22/12 | 180 | 180.0377 | 15.1 | 15.0295 | 178.3 | 178.3227 | 13.3 | 13.2439 | 177.3 | 177.3321 | 10.6 | 10.5223
| 1500/27/02 | 224.1 | 224.0732 | 20.4 | 20.2129 | 221.9 | 221.8988 | 19.9 | 19.6759 | 220.2 | 220.2508 | 18.3 | 18.0514
| 1200/21/06 | 178.4 | 178.4679 | 62 | 61.9596 | 175.2 | 175.1972 | 60.1 | 60.1308 | 173.7 | 173.7198 | 57.4 | 57.383
| 1000/20/10 | 151.1 | 150.976 | 24.4 | 24.2584 | 149.6 | 149.4975 | 22.3 | 22.1704 | 149.1 | 148.9385 | 19.7 | 19.5306
Tolerance: within 1.5°C
|  | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range
|  | -0.037739 | Yes | 0.070473 | Yes | -0.022697 | Yes | 0.056056 | Yes | -0.032059 | Yes | 0.077748 | Yes
|  | 0.026772 | Yes | 0.18715 | Yes | 0.0012433 | Yes | 0.22411 | Yes | -0.050756 | Yes | 0.24859 | Yes
|  | -0.067897 | Yes | 0.040428 | Yes | 0.0027564 | Yes | -0.030784 | Yes | -0.019761 | Yes | 0.016958 | Yes
|  | 0.12399 | Yes | 0.14156 | Yes | 0.10247 | Yes | 0.1296 | Yes | 0.16146 | Yes | 0.16939 | Yes
Window 2
[5 empty] | Argon |  |  |  | 0.4

## Test G3Calcs
Test G3.1: Derived Properties
External Wall |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.029939 | 0.04
| Brick | 0.1162 | 0.1162
| Insulation 1 | 1.5 | 1.5
| Masonry | 0.2215 | 0.2215
| Plaster 1 | 0.02143 | 0.02143
| Inside Film | 0.11975 | 0.13
| Sum | 2.0088 | 2.0291
| U-Factor | 0.4978 | 0.49282
Internal Wall 1 |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.029939 | 0.13
| Plaster 2 | 0.0571 | 0.0571
| Insulation 1 | 2.5 | 2.5
| Plaster 2 | 0.0571 | 0.0571
| Inside Film | 0.11975 | 0.13
| Sum | 2.7639 | 2.8742
| U-Factor | 0.36181 | 0.34792
Internal Wall 2 |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.029939 | 0.13
| Plaster 2 | 0.0571 | 0.0571
| Masonry | 0.2215 | 0.2215
| Plaster 2 | 0.0571 | 0.0571
| Inside Film | 0.11975 | 0.13
| Sum | 0.48539 | 0.5957
| U-Factor | 2.0602 | 1.6787
Ceiling/Floor (Upward) |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.081011 | 0.1
| Covering | 0.01739 | 0.01739
| Cement Screed | 0.04286 | 0.04286
| Insulation 2A | 1 | 1
| Concrete | 0.08571 | 0.08571
| Insulation 2B | 2.5 | 2.5
| Acoustical Tile | 0.3333 | 0.3333
| Inside Film | 0.10743 | 0.1
| Sum | 4.1677 | 4.1793
| U-Factor | 0.23994 | 0.23928
Ceiling/Floor (Downward) |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.081011 | 0.17
| Covering | 0.01739 | 0.01739
| Cement Screed | 0.04286 | 0.04286
| Insulation 2A | 1 | 1
| Concrete | 0.08571 | 0.08571
| Insulation 2B | 2.5 | 2.5
| Acoustical Tile | 0.3333 | 0.3333
| Inside Film | 0.10743 | 0.17
| Sum | 4.1677 | 4.3193
| U-Factor | 0.23994 | 0.23152
Roof 1 |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.081011 | 0.1
| Tiles | 0.01739 | 0.01739
| Insulation 2 | 2 | 2
| Concrete | 0.09524 | 0.09524
| Inside Film | 0.10743 | 0.04
| Sum | 2.3011 | 2.2526
| U-Factor | 0.43458 | 0.44393
Roof 2 |  | R (m2-K/W) | R (m2-K/W)
|  | EnergyPlus | TM-33 Spec
| Outside Film | 0.081 | 0.1
| Tiles | 0.01739 | 0.01739
| Insulation 2 | 2 | 2
| Concrete | 0.09524 | 0.09524
| Air Space | 0.18 | 0.18
| Acoustical Tile | 0.3333 | 0.3333
| Inside Film | 0.1074 | 0.04
| Sum | 2.8143 | 2.7659
| U-Factor | 0.35532 | 0.36154
Window 1
|  |  |  | EnergyPlus Window U-Factor from Table |  |  |  | 2.9 | W/m2-K
From Output Ref , pg 38
[5 empty] | Ext Window Film |  |  | 26 | W/m2-K |  |  | R= | 0.038462
[5 empty] | Int Window Film Calc by Program, avg from eio |  |  |  |  | 1.444 | W/m2-K | R= | 0.69252
|  |  |  | Overall R |  | 0.34483
-0.038462
-0.69252
|  |  |  | R Window only |  | -0.38615
[6 empty] | m | k | R
|  |  |  | Outside Film |  |  |  | 0.04
|  |  |  | Glass |  | 0.006 | 1.06 | 0.0056604
|  |  |  | Air |  |  |  | 0.16
|  |  |  | Glass |  | 0.006 | 1.06 | 0.0056604
|  |  |  | Inside Film |  |  |  | 0.13
0.34132
2.9298
Window 2
[6 empty] | m | k | R
|  |  |  | Outside Film |  |  |  | 0.04
|  |  |  | Glass |  | 0.006 | 1.06 | 0.0056604
|  |  |  | Argon |  |  |  | 0.4
|  |  |  | Glass |  | 0.006 | 1.06 | 0.0056604
|  |  |  | Inside Film |  |  |  | 0.13
0.58132
1.7202

## Test G3.1
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G3.1: Derived Properties
| Construction |  |  |  | Transmittance
/W-m-2K-1
[5 empty] | Ref. | User | Diff | In Range
| External Wall |  |  |  | 0.49 | 0.49282 | -0.002822 | Yes
| Internal Wall 1 |  |  |  | 0.35 | 0.34792 | 0.0020771 | Yes
| Internal Wall 2 |  |  |  | 1.68 | 1.6787 | 0.0013027 | Yes
| Floor (upward heat flow) |  |  |  | 0.24 | 0.23928 | 0.00072319 | Yes
| Ceiling (downward heat flow) |  |  |  | 0.23 | 0.23152 | -0.0015211 | Yes
| Roof 1 (upward heat flow) |  |  |  | 0.44 | 0.44393 | -0.0039255 | Yes
| Window 1 |  |  |  | 2.94
| Window 2 |  |  |  | 1.72
Tolerance: within 0.01 W/m-2K-1
Notes: 1) User values adjusted for surface resistances specified in CIBSE TM33 2006 for Test G3.1
2) Unable to specify interior film coefficients in EnergyPlus for windows as they are calculated
by the EnergyPlus convection algorithm
EnergyPlus Nominal Transmittance Values Based on ASHRAE 90.1-2004 Film Coefficients
| Construction |  |  |  | Nominal Transmittance
/W-m-2K-1
EnergyPlus
| External Wall |  |  |  |  | 0.4978
| Internal Wall 1 |  |  |  |  | 0.36181
| Internal Wall 2 |  |  |  |  | 2.0602
| Floor (upward heat flow) |  |  |  |  | 0.23994
| Ceiling (downward heat flow) |  |  |  |  | 0.23994
| Roof 1 (upward heat flow) |  |  |  |  | 0.43458
| Window 1 |  |  |  |  | 2.902
| Window 2 |  |  |  |  | 2.673
ASHRAE 90.1-2004, Appendix A Film Coefficients used by EnergyPlus
| Surface Class |  | Interior Film Coefficient |  |  | Exterior Film Coefficient
|  |  | (m2-K/W) |  |  | (m2-K/W)
| Wall |  | 0.11975 |  |  | 0.029939
| Floor |  | 0.16202 |  |  | 0.081011
| Ceiling/Roof |  | 0.10743 |  |  | 0.081011
CIBSE TM33 2006 Surface Resistances Specified for Test G3.1
| Heat Flow Direction |  |  | Internal |  | External
|  |  |  | (m2-K/W) |  | (m2-K/W)
| Horizontal |  |  | 0.13 |  | 0.04
| Upward |  |  | 0.1 |  | 0.04
| Downward |  |  | 0.17 |  | 0.04

## Test G3.2
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G3.2: Dynamic Conduction (Timestep=60)
| Test No. | Air temperature after stated time (C)
|  | 2 hours |  | 6 hours |  | 12 hours |  | 24 hours |  | 120 hours
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User
| G3.2.1 | 20.04 | 20.0399 | 21.26 | 21.2732 | 23.48 | 23.4475 | 26.37 | 26.3492 | 30 | 29.9721
| G3.2.2 | 25.09 | 24.4565 | 29.63 | 29.4431 | 30 | 29.9821 | 30 | 30.0064 | 30 | 30.0065
| G3.2.3 | 20 | 20.0067 | 20.26 | 20.2332 | 21.67 | 21.6097 | 24.9 | 24.8216 | 29.95 | 29.9438
| G3.2.4 | 20 | 20.0473 | 20.06 | 20.1024 | 20.25 | 20.2847 | 20.63 | 20.6611 | 23.17 | 23.1947
Tolerance: within 0.6°C
|  | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range
|  | 0.00011542 | Yes | -0.013207 | Yes | 0.032519 | Yes | 0.020849 | Yes | 0.027945 | Yes
|  | 0.63348 | No | 0.18688 | Yes | 0.017869 | Yes | -0.0064476 | Yes | -0.006499 | Yes
|  | -0.0066552 | Yes | 0.026757 | Yes | 0.060281 | Yes | 0.078419 | Yes | 0.0061519 | Yes
|  | -0.047348 | Yes | -0.042414 | Yes | -0.034703 | Yes | -0.031103 | Yes | -0.024686 | Yes
Test G3.2: Dynamic Conduction (Timestep=6)
| Test No. | Air temperature after stated time (C)
|  | 2 hours |  | 6 hours |  | 12 hours |  | 24 hours |  | 120 hours
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User
| G3.2.1 | 20.04 | 20.0466 | 21.26 | 21.292 | 23.48 | 23.4547 | 26.37 | 26.3455 | 30 | 29.9708
| G3.2.2 | 25.09 | 24.0571 | 29.63 | 29.2467 | 30 | 29.9548 | 30 | 30.0041 | 30 | 30.0065
| G3.2.3 | 20 | 24.0571 | 20.26 | 20.2436 | 21.67 | 21.5908 | 24.9 | 24.7607 | 29.95 | 29.932
| G3.2.4 | 20 | 20.0487 | 20.06 | 20.1071 | 20.25 | 20.29 | 20.63 | 20.6661 | 23.17 | 23.1978
Tolerance: within 0.6°C
|  | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range
|  | -0.0066184 | Yes | -0.032024 | Yes | 0.025289 | Yes | 0.024512 | Yes | 0.029188 | Yes
|  | 1.0329 | No | 0.38334 | Yes | 0.045248 | Yes | -0.0040836 | Yes | -0.006499 | Yes
|  | -4.0571 | No | 0.016393 | Yes | 0.079241 | Yes | 0.13933 | Yes | 0.018017 | Yes
|  | -0.048678 | Yes | -0.047122 | Yes | -0.03996 | Yes | -0.036079 | Yes | -0.027758 | Yes

## Test G4
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G4: Solar Shading
Shading Fraction
| Time | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Test 5 |  | Test 6
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User | Ref. | User
| 7:00 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1
| 7:30 | 0.32 | 0.32234 | 0.68 | 0.67766 | 1 | 1 | 0 | 0 | 0.04 | 0.036175 | 1 | 1
| 8:00 | 0.44 | 0.44136 | 0.56 | 0.55864 | 1 | 1 | 0 | 0 | 0.1 | 0.09568 | 1 | 1
| 8:30 | 0.58 | 0.58538 | 0.42 | 0.41462 | 1 | 1 | 0 | 0 | 0.17 | 0.1677 | 1 | 1
| 9:00 | 0.72 | 0.7252 | 0.27 | 0.26996 | 0.99 | 0.99516 | 0 | 0 | 0.26 | 0.25867 | 0.98 | 0.98265
| 9:30 | 0.74 | 0.74544 | 0.14 | 0.1402 | 0.88 | 0.88564 | 0 | 0 | 0.38 | 0.37997 | 0.74 | 0.74006
| 10:00 | 0.72 | 0.71925 | 0.04 | 0.0391 | 0.76 | 0.75835 | 0.04 | 0.033166 | 0.55 | 0.55363 | 0.4 | 0.39273
| 10:30 | 0.67 | 0.66963 | 0 | 0 | 0.67 | 0.66963 | 0.17 | 0.16073 | 0.82 | 0.82236 | 0 | 0
| 11:00 | 0.63 | 0.63287 | 0 | 0 | 0.63 | 0.63287 | 0.24 | 0.23427 | 0.96 | 0.96183 | 0 | 0
| 11:30 | 0.61 | 0.61202 | 0 | 0 | 0.61 | 0.61202 | 0.28 | 0.27596 | 0.96 | 0.95634 | 0 | 0
| 12:00 | 0.6 | 0.60396 | 0 | 0 | 0.6 | 0.60396 | 0.3 | 0.29209 | 0.95 | 0.95408 | 0 | 0
| 12:30 | 0.6 | 0.60755 | 0 | 0 | 0.6 | 0.60755 | 0.29 | 0.28491 | 1 | 1 | 1 | 1
| 13:00 | 0.62 | 0.62328 | 0 | 0 | 0.62 | 0.62328 | 0.26 | 0.25343 | 1 | 1 | 1 | 1
Tolerance: within 0.05
|  | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range | Diff | In Range
|  | 0 | Yes | 0 | Yes | 0 | Yes | 0 | Yes | 0 | Yes | 0 | Yes
|  | -0.0023425 | Yes | 0.0023425 | Yes | 0 | Yes | 0 | Yes | 0.003825 | Yes | 0 | Yes
|  | -0.0013625 | Yes | 0.0013625 | Yes | 0 | Yes | 0 | Yes | 0.00432 | Yes | 0 | Yes
|  | -0.0053831 | Yes | 0.0053831 | Yes | 0 | Yes | 0 | Yes | 0.002305 | Yes | 0 | Yes
|  | -0.0052005 | Yes | 4.3634e-05 | Yes | -0.0051568 | Yes | 0 | Yes | 0.001325 | Yes | -0.00265 | Yes
|  | -0.0054413 | Yes | -0.00020345 | Yes | -0.0056448 | Yes | 0 | Yes | 3e-05 | Yes | -6.2e-05 | Yes
|  | 0.00074947 | Yes | 0.00089961 | Yes | 0.0016491 | Yes | 0.0068335 | Yes | -0.003635 | Yes | 0.007274 | Yes
|  | 0.000365 | Yes | 0 | Yes | 0.000365 | Yes | 0.009268 | Yes | -0.0023556 | Yes | 0 | Yes
|  | -0.002865 | Yes | 0 | Yes | -0.002865 | Yes | 0.005734 | Yes | -0.0018332 | Yes | 0 | Yes
|  | -0.00202 | Yes | 0 | Yes | -0.00202 | Yes | 0.004044 | Yes | 0.0036555 | Yes | 0 | Yes
|  | -0.003955 | Yes | 0 | Yes | -0.003955 | Yes | 0.00791 | Yes | -0.0040806 | Yes | 0 | Yes
|  | -0.007545 | Yes | 0 | Yes | -0.007545 | Yes | 0.00509 | Yes | 0 | Yes | 0 | Yes
|  | -0.003285 | Yes | 0 | Yes | -0.003285 | Yes | 0.006566 | Yes | 0 | Yes | 0 | Yes
Window 2
[5 empty] | Argon |  |  |  | 0.4

## Test G5
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G5: Glazing Properties
| Test | g-value w/Air |  | g-value w/Argon |  | U-value w/Air |  | U-value w/Argon
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User
| Case G5-1 | 0.72 | 0.716 | 0.72 | 0.717 | 2.83 | 2.693 | 2.68 | 2.522
| Case G5-2 | 0.68 | 0.638 | 0.68 | 0.641 | 1.92 | 2.025 | 1.64 | 1.916 | Type A for Case G7-1 and G7-3
| Case G5-3 | 0.44 | 0.422 | 0.44 | 0.422 | 1.92 | 2.025 | 1.64 | 1.916
| Case G5-4 | 0.37 | 0.389 | 0.37 | 0.389 | 1.58 | 1.63 | 1.24 | 1.63 | Type B for Case G7-2 and G7-4
| Case G5-5 | 0.64 | 0.627 | 0.64 | 0.627 | 1.88 | 1.758 | 1.74 | 1.758
|  |  | Delta |  | Delta |  | Delta |  | Delta
| Case G5-1 |  | -0.004 |  | -0.003 |  | -0.137 |  | -0.158
| Case G5-2 |  | -0.042 |  | -0.039 |  | 0.105 |  | 0.276
| Case G5-3 |  | -0.018 |  | -0.018 |  | 0.105 |  | 0.276
| Case G5-4 |  | 0.019 |  | 0.019 |  | 0.05 |  | 0.39
| Case G5-5 |  | -0.013 |  | -0.013 |  | -0.122 |  | 0.018
|  |  | % Diff |  | % Diff |  | % Diff |  | % Diff
| Case G5-1 |  | -0.5556% |  | -0.4167% |  | -4.841% |  | -5.896%
| Case G5-2 |  | -6.176% |  | -5.735% |  | 5.469% |  | 16.83%
| Case G5-3 |  | -4.091% |  | -4.091% |  | 5.469% |  | 16.83%
| Case G5-4 |  | 5.135% |  | 5.135% |  | 3.165% |  | 31.45%
| Case G5-5 |  | -2.031% |  | -2.031% |  | -6.489% |  | 1.034%
|  |  | Within Range |  | Within Range |  | Within Range |  | Within Range
| Case G5-1 |  | Yes |  | Yes |  | No |  | No
| Case G5-2 |  | No |  | No |  | No |  | No
| Case G5-3 |  | Yes |  | Yes |  | No |  | No
| Case G5-4 |  | Yes |  | Yes |  | No |  | No
| Case G5-5 |  | Yes |  | Yes |  | No |  | Yes
Tolerance: within 0.02 for g-value
Tolerance: within 0.02 for U-value w/air and 0.04 for U-value w/argon
Note: EnergyPlus SHGC same as g-value
Note: EnergyPlus U-value is films

## Test G6
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G6: Steady State Heat Loss from Rooms
| Test | Model | Temperature (C) of Stated Surface | [7 empty] | Air Temp (C) | Op. Temp (C)
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
| A1 | Reference | 20.5 | 20.6 | 20.5 | 19.4 | 20.9 | 20.2 | 11.1 |  | 22.2
|  | Basic | 20.6 | 20.6 | 20.6 | 19 | 20.9 | 20.1 | 11.1 |  | 22.2
|  | Simple | Temperature (C) of Stated Surface 1: This method is not recommended for surface temperatures |  | 22.1 |  | Deltas
|  | User | 20.5406 | 20.5713 | 20.5406 | 19.374 | 20.8735 | 20.1095 | 10.6539 |  | 22.2028 | 21 | 0.040569 | -0.028748 | 0.040569 | -0.026016 | -0.026473 | -0.090459 | -0.44606 | 0.0028116
Within 0.2K
[13 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes
Tolerance: within 0.2 C
| A2 | Reference | 20.8 | 21 | 20.8 | 19.7 | 20.9 | 20.8 | 11.2 |  | 21.3
|  | Basic | 20.9 | 20.9 | 20.9 | 19.4 | 21 | 20.8 | 11.2 |  | 21.3
|  | Simple | Temperature (C) of Stated Surface 1: This method is not recommended for surface temperatures |  | 21.3 |  | Deltas
|  | User | 20.9702 | 21.0002 | 20.9702 | 19.8077 | 21.0758 | 20.8121 | 10.88 |  | 21.5361 | 20.879 | 0.17024 | 0.00020096 | 0.17024 | 0.1077 | 0.1758 | 0.01212 | -0.31999 | 0.23608
Within 0.2K
[13 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | No
Tolerance: within 0.2 C
| B1 | Reference | 20.2 | 19 | 19 | 19.2 | 20.8 | 19.7 | 11 |  | 22.8
|  | Basic | 20.3 | 18.9 | 18.9 | 18.9 | 20.8 | 19.6 | 10.9 |  | 22.8
|  | Simple | Temperature (C) of Stated Surface 1: This method is not recommended for surface temperatures |  | 22.6 |  | Deltas
|  | User | 20.3075 | 18.8626 | 18.8786 | 19.1599 | 20.8071 | 19.6369 | 10.537 |  | 22.8382 | 20.9921 | 0.10748 | -0.13742 | -0.12143 | -0.040149 | 0.0070587 | -0.063137 | -0.46298 | 0.038213
Within 0.2K
[13 empty] | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes
Tolerance: within 0.2 C
| B2 | Reference | 20.9 | 19.6 | 19.5 | 19.8 | 21 | 20.9 | 11.3 |  | 21.2
|  | Basic | 20.9 | 19.5 | 19.5 | 19.4 | 21 | 21 | 11.2 |  | 21.2
|  | Simple | Temperature (C) of Stated Surface 1: This method is not recommended for surface temperatures |  | 21.1 |  | Deltas
|  | User | 21.1062 | 19.6536 | 19.6714 | 19.9664 | 21.1558 | 20.9748 | 10.9515 |  | 21.4723 | 20.7035 | 0.20615 | 0.053621 | 0.17136 | 0.16644 | 0.15578 | 0.074776 | -0.34849 | 0.2723
Within 0.2K
[13 empty] | No | Yes | Yes | Yes | Yes | Yes | No | No
Tolerance: within 0.2 C
| Test | Model | Temperature (C) of Stated Surface 1: Heat Loss / W
|  |  | Fabric | Infiltration | Total
| A1 | Reference | Temperature (C) of Stated Surface 1: 542; Temperature (C) of Stated Surface 2: 121; Temperature (C) of Stated Surface 3: 663
|  | Basic | Temperature (C) of Stated Surface 1: 541; Temperature (C) of Stated Surface 2: 121; Temperature (C) of Stated Surface 3: 662
|  | Simple | Temperature (C) of Stated Surface 1: 568; Temperature (C) of Stated Surface 2: 120; Temperature (C) of Stated Surface 3: 688; Temperature (C) of Stated Surface 5: Delta-Total Heat Loss
|  | User | Temperature (C) of Stated Surface 1: 553.607; Temperature (C) of Stated Surface 2: 133.0072; Temperature (C) of Stated Surface 3: 686.6142; Temperature (C) of Stated Surface 5: 3.562%
Within 2.5%
No
| A2 | Reference | Temperature (C) of Stated Surface 1: 556; Temperature (C) of Stated Surface 2: 117; Temperature (C) of Stated Surface 3: 673
|  | Basic | Temperature (C) of Stated Surface 1: 554; Temperature (C) of Stated Surface 2: 117; Temperature (C) of Stated Surface 3: 671
|  | Simple | Temperature (C) of Stated Surface 1: 574; Temperature (C) of Stated Surface 2: 117; Temperature (C) of Stated Surface 3: 690; Temperature (C) of Stated Surface 5: Delta-Total Heat Loss
|  | User | Temperature (C) of Stated Surface 1: 312.7245; Temperature (C) of Stated Surface 2: 129.6228; Temperature (C) of Stated Surface 3: 442.3473; Temperature (C) of Stated Surface 5: -34.27%
Within 2.5%
No
| B1 | Reference | Temperature (C) of Stated Surface 1: 831; Temperature (C) of Stated Surface 2: 496; Temperature (C) of Stated Surface 3: 1327
|  | Basic | Temperature (C) of Stated Surface 1: 830; Temperature (C) of Stated Surface 2: 496; Temperature (C) of Stated Surface 3: 1326
|  | Simple | Temperature (C) of Stated Surface 1: 860; Temperature (C) of Stated Surface 2: 491; Temperature (C) of Stated Surface 3: 1352; Temperature (C) of Stated Surface 5: Delta-Total Heat Loss
|  | User | Temperature (C) of Stated Surface 1: 839.1315; Temperature (C) of Stated Surface 2: 544.9306; Temperature (C) of Stated Surface 3: 1384.0622; Temperature (C) of Stated Surface 5: 4.3%
Within 2.5%
No
| B2 | Reference | Temperature (C) of Stated Surface 1: 862; Temperature (C) of Stated Surface 2: 465; Temperature (C) of Stated Surface 3: 1327
|  | Basic | Temperature (C) of Stated Surface 1: 859; Temperature (C) of Stated Surface 2: 465; Temperature (C) of Stated Surface 3: 1324
|  | Simple | Temperature (C) of Stated Surface 1: 877; Temperature (C) of Stated Surface 2: 464; Temperature (C) of Stated Surface 3: 1342; Temperature (C) of Stated Surface 5: Delta-Total Heat Loss
|  | User | Temperature (C) of Stated Surface 1: 363.6007; Temperature (C) of Stated Surface 2: 517.196; Temperature (C) of Stated Surface 3: 880.7967; Temperature (C) of Stated Surface 5: -33.62%
Within 2.5%
No
Tolerance: within 2.5% for total heat loss
Window 2
|  |  | Temperature (C) of Stated Surface 4: Argon | 0.4

## Test G7-CIBSE Weather
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
With Weather File from CIBSE web site
Test G7: Annual Cooling and Heating Demand
| Test | Heating Demand / kW-h |  | Cooling Demand / kW-h
|  | Ref. | User | Ref. | User
| Case G7-1 | 2592 | 2465.1763 | 1025 | 474.4318
| Case G7-2 | 3257 | 3064.1298 | 449 | 116.2387
| Case G7-3 | 2653 | 2586.8655 | 1236 | 575.1886
| Case G7-4 | 3155 | 3109.026 | 474 | 161.0651
|  |  | Delta |  | Delta
| Case G7-1 |  | -126.8237 |  | -550.5682
| Case G7-2 |  | -192.8702 |  | -332.7613
| Case G7-3 |  | -66.1345 |  | -660.8114
| Case G7-4 |  | -45.974 |  | -312.9349
|  |  | % Diff |  | % Diff
| Case G7-1 |  | -4.893% |  | -53.71%
| Case G7-2 |  | -5.922% |  | -74.11%
| Case G7-3 |  | -2.493% |  | -53.46%
| Case G7-4 |  | -1.457% |  | -66.02%
|  |  | Within Range |  | Within Range
| Case G7-1 |  | Yes |  | No
| Case G7-2 |  | Yes |  | No
| Case G7-3 |  | Yes |  | No
| Case G7-4 |  | Yes |  | No
Tolerance: within 8% heating
Tolerance: within 12% cooling

## Test G7-Andy WeatherJan2013
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
With Andy Tindale Weather File from Jan 2013
Test G7: Annual Heating and Cooling Demand
| Test | Heating Demand / kW-h |  | Cooling Demand / kW-h
|  | Ref. | User | Ref. | User | Delta Changes between cases using G7-1 as reference |  |  |  |  | Switch of Emissivities
| Case G7-1 | 2592 | 2113.4604 | 1025 | 580.5331 |  |  |  |  | Heavy weight construction, Type A glass (clear/low emissivity) | Case G7-1 | 2592 | 1939.1943 | 1025 | 696.354
| Case G7-2 | 3257 | 2761.4387 | 449 | 210.8931 | 665 | 647.9783 | -576 | -369.64 | Heavy weight construction, Type B glass (high performance/clear)
| Case G7-3 | 2653 | 2314.9374 | 1236 | 726.8161 | 61 | 201.4771 | 211 | 146.2829 | Light weight construction, Type A glass (clear/low emissivity) | Case G7-3 | 2653 | 2179.0404 | 1236 | 882.9738
| Case G7-4 | 3155 | 2809.3427 | 474 | 260.4063 | 563 | 695.8823 | -551 | -320.1268 | Light weight construction, Type B glass (high performance/clear)
[6 empty] | 502 | 494.4053 | -762 | -466.4098
|  |  | Delta |  | Delta
| Case G7-1 |  | -478.5396 |  | -444.4669
| Case G7-2 |  | -495.5613 |  | -238.1069
| Case G7-3 |  | -338.0626 |  | -509.1839
| Case G7-4 |  | -345.6573 |  | -213.5937
|  |  | % Diff |  | % Diff
| Case G7-1 |  | -18.46% |  | -43.36%
| Case G7-2 |  | -15.22% |  | -53.03%
| Case G7-3 |  | -12.74% |  | -41.2%
| Case G7-4 |  | -10.96% |  | -45.06%
|  |  | Within Range |  | Within Range
| Case G7-1 |  | No |  | No
| Case G7-2 |  | No |  | No
| Case G7-3 |  | No |  | No
| Case G7-4 |  | No |  | No

## Test G9-Infil+Vent
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
Test G9: Infiltration and Ventilation
To convert EnergyPlus flows in kg/s to L/s need to know air density
| Connection | Air Flow Rate (L/s)
|  | Test 1 |  | Test 2 |  | Test 3 |  | Test 4 |  | Calcualtion of Outdoor Air Density
|  | Ref. | User | Ref. | User | Ref. | User | Ref. | User |  | Outdoor DBT (C) | Outdoor Density (kg/m3)
| Entering room 1 via B1 | -11.6 | -11.5641 | -20.6 | -20.5404 | -36 | -35.9024 | -20.4 | -20.3103 | Test 1 | 12.1 | 1.2377
| Entering room 1 via B2 | 16.6 | 16.4663 | 17.1 | 16.9263 | 29.9 | 29.5534 | 28.7 | 28.5304 | Test 2 | 18.3 | 1.2114
[10 empty] | Test 3 | 18.8 | 1.2093
| Entering room 1 via D1 | -5.5 | -5.3583 | 3.4 | 3.5394 | 6 | 6.27 | -9.2 | -8.9384 | Test 4 | 12.8 | 1.2347
| Entering room 2 via B6 | 26.4 | 26.8082 | 11.6 | 12.3455 | 13.6 | 14.2281 | 39.4 | 39.5114
| Entering room 2 via R1 | -27.3 | -27.7386 | -11.7 | -12.5023 | -14 | -14.3841 | -40.7 | -40.7826 | Calculation of Indoor Density
[11 empty] | Indoor DBT (C) | Indoor Density (kg/m3)
| Entering room 3 via B3 | 13.8 | 13.3459 | 5.3 | 4.7181 | 9 | 7.9484 | 23.4 | 22.6131
| Entering room 3 via B4 | -7.2 | -8.2587 | 10.5 | 9.556 | 18 | 16.071 | -17.4 | -18.8242 | Rooms 1 and 4 | 20 | 1.2043
| Entering room 3 via D2 | -12.7 | -10.9451 | -12.8 | -10.7946 | -21.4 | -17.8366 | -16.2 | -13.5158 | Rooms 2 and 3 | 22 | 1.1962
| Entering room 4 via R2 | -21.1 | -21.6735 | -23.4 | -22.9972 | -38.7 | -37.4963 | -23.7 | -23.8063
| Entering room 4 via B5 | 8.3 | 10.5113 | 10.6 | 12.2045 | 17.2 | 19.6996 | 7.2 | 10.1271
|  |  | Delta |  | Delta |  | Delta |  | Delta
| Entering room 1 via B1 |  | 0.035938 |  | 0.059581 |  | 0.097647 |  | 0.089725
| Entering room 1 via B2 |  | -0.13366 |  | -0.17369 |  | -0.34664 |  | -0.16965
| Entering room 1 via D1 |  | 0.14167 |  | 0.13936 |  | 0.27001 |  | 0.26155
| Entering room 2 via B6 |  | 0.40821 |  | 0.74554 |  | 0.62811 |  | 0.11139
| Entering room 2 via R1 |  | -0.43863 |  | -0.80227 |  | -0.38406 |  | -0.082603
| Entering room 3 via B3 |  | -0.45415 |  | -0.58191 |  | -1.0516 |  | -0.78694
| Entering room 3 via B4 |  | -1.0587 |  | -0.94403 |  | -1.929 |  | -1.4242
| Entering room 3 via D2 |  | 1.7549 |  | 2.0054 |  | 3.5634 |  | 2.6842
| Entering room 4 via R2 |  | -0.57347 |  | 0.40283 |  | 1.2037 |  | -0.10631
| Entering room 4 via B5 |  | 2.2113 |  | 1.6045 |  | 2.4996 |  | 2.9271
|  |  | % Diff |  | % Diff |  | % Diff |  | % Diff
| Entering room 1 via B1 |  | -0.3098% |  | -0.2892% |  | -0.2712% |  | -0.4398%
| Entering room 1 via B2 |  | -0.8052% |  | -1.016% |  | -1.159% |  | -0.5911%
| Entering room 1 via D1 |  | -2.576% |  | 4.099% |  | 4.5% |  | -2.843%
| Entering room 2 via B6 |  | 1.546% |  | 6.427% |  | 4.618% |  | 0.2827%
| Entering room 2 via R1 |  | 1.607% |  | 6.857% |  | 2.743% |  | 0.203%
| Entering room 3 via B3 |  | -3.291% |  | -10.98% |  | -11.68% |  | -3.363%
| Entering room 3 via B4 |  | 14.7% |  | -8.991% |  | -10.72% |  | 8.185%
| Entering room 3 via D2 |  | -13.82% |  | -15.67% |  | -16.65% |  | -16.57%
| Entering room 4 via R2 |  | 2.718% |  | -1.722% |  | -3.11% |  | 0.4486%
| Entering room 4 via B5 |  | 26.64% |  | 15.14% |  | 14.53% |  | 40.65%
|  |  | Within Range |  | Within Range |  | Within Range |  | Within Range
| Entering room 1 via B1 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 1 via B2 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 1 via D1 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 2 via B6 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 2 via R1 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 3 via B3 |  | Yes |  | No |  | No |  | Yes
| Entering room 3 via B4 |  | No |  | Yes |  | No |  | Yes
| Entering room 3 via D2 |  | No |  | No |  | No |  | No
| Entering room 4 via R2 |  | Yes |  | Yes |  | Yes |  | Yes
| Entering room 4 via B5 |  | No |  | No |  | No |  | No
Tolerance: within 10% for air flow rate

## Test G10-Air-Handling Unit Test
CIBSE TM33: 2006
Comparison of Results
EnergyPlus 8.2.0
With Weather File from Tinsdale 2013
Test G10: Air-Handling Unit Test
| Component | Energy Demand / kW-h
|  | AHU1 |  | AHU2 |  | AHU3
|  | Ref. | User | Ref. | User | Ref. | User
| Cooling Coil | 12348 | 10534.8379 | 11744 | 10677.0296 | 0
| Heating Coil | 5461 | 4496.1561 | 5579 | 5806.0523 | 10914
| Fan Motor(s) | 1132 | 1136.0714 | 1698 | 2190.9949 | 1698
| Humidifier | 0 | 0 | 0 |  | 4038
|  |  | Delta |  | Delta
| Cooling Coil |  | -1813.1621 |  | -1066.9704
| Heating Coil |  | -964.8439 |  | 227.0523
| Fan Motor(s) |  | 4.0714 |  | 492.9949
| Humidifier |  | 0 |  | 0
|  |  | % Diff |  | % Diff
| Cooling Coil |  | -14.68% |  | -9.085%
| Heating Coil |  | -17.67% |  | 4.07%
| Fan Motor(s) |  | 0.3597% |  | 29.03%
| Humidifier |  | #DIV/0! |  | #DIV/0!
|  |  | Within Range |  | Within Range
| Cooling Coil |  | No |  | Yes
| Heating Coil |  | No |  | Yes
| Fan Motor(s) |  | Yes |  | No
| Humidifier |  | #DIV/0! |  | #DIV/0!
Tolerance: within 2%