## Annual
Global Energy Balance Test
Window AC
Varying Loads, Annual Run
Window AC with Baseboard Heat
Zone Level Energy Balance for Annual Test Cases
Zone Energy Input - - - - - - - - - - - - - - - - - - - - - - - - - - >
|  | Daily | Internal | Internal | Daily | Zone Air Temp. | Zone Air Temp. | Zone Air Humidity Ratio | Zone Air Humidity Ratio
|  | Other | Convective | Latent | Total
Test | Month | Equipment | Load | Load | Internal | Min | Max | Min | Max
Case |  | Consump. |  |  | Load
|  | (Wh) | (Wh) | (Wh) | (Wh) | (C) | (C) | ( ) | ( )
I | Jan | -744000 | -744000 | 0 | -744000 | 22.2 | 22.2 | 0.0019353 | 0.0019353
J | Feb | -672000 | -672000 | 0 | -672000 | 22.2 | 22.2 | 0.0019353 | 0.0019353
K | Mar | -744000 | -744000 | 0 | -744000 | 22.2 | 22.2 | 0.0019353 | 0.0019353
L | Apr | -720000 | -720000 | 0 | -720000 | 22.2 | 22.2 | 0.0019353 | 0.0019353
M | May | 744000 | 520800 | 223200 | 744000 | 22.1961 | 22.2 | 0.0030897 | 0.010168
N | Jun | 720000 | 504000 | 216000 | 720000 | 22.1963 | 22.1972 | 0.0093247 | 0.010225
O | Jul | 744000 | 520800 | 223200 | 744000 | 22.1963 | 22.1972 | 0.0095298 | 0.010288
P | Aug | 744000 | 520800 | 223200 | 744000 | 22.1963 | 22.1971 | 0.0095052 | 0.0102
Q | Sep | 720000 | 504000 | 216000 | 720000 | 22.1962 | 22.1972 | 0.0093581 | 0.010079
R | Oct | -744000 | -744000 | 0 | -744000 | 22.2 | 22.2 | 0.0093501 | 0.0093501
S | Nov | -720000 | -720000 | 0 | -720000 | 22.2 | 22.2 | 0.0093501 | 0.0093501
T | Dec | -744000 | -744000 | 0 | -744000 | 22.2 | 22.2 | 0.0093501 | 0.0093501
|  | Zone Energy Output - - - - - - - - - - - - - - - - > |  |  |  | Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain |  | Difference (Total Output - Total Input) | Difference (Latent Output - Latent Input) | Difference (Sensible Output - Sensible Input) | Difference (Total Output vs. Total Input) | Difference (Latent Output vs. Latent Input) | Difference (Sensible Output vs. Sensible Input)
Case
|  | (Wh) | (Wh) | (Wh) |  | (Wh) | (Wh) | (Wh) | (%) | (%) | (%)
I | Jan | -744000 | 0 | -744000 |  | 0 | 0 | 0 | 0% | 0% | 0%
J | Feb | -672000 | 0 | -672000 |  | 0 | 0 | 0 | 0% | 0% | 0%
K | Mar | -744000 | 0 | -744000 |  | 0 | 0 | 0 | 0% | 0% | 0%
L | Apr | -720000 | 0 | -720000 |  | 0 | 0 | 0 | 0% | 0% | 0%
M | May | 744000 | 223200 | 520800 |  | 0 | 0 | 0 | 0% | 0% | 0%
N | Jun | 720000 | 216000 | 504000 |  | 0 | 0 | 0 | 0% | 0% | 0%
O | Jul | 744000 | 223200 | 520800 |  | 0 | 0 | 0 | 0% | 0% | 0%
P | Aug | 744000 | 223200 | 520800 |  | 0 | 0 | 0 | 0% | 0% | 0%
Q | Sep | 720000 | 216000 | 504000 |  | 0 | 0 | 0 | 0% | 0% | 0%
R | Oct | -744000 | 0 | -744000 |  | 0 | 0 | 0 | 0% | 0% | 0%
S | Nov | -720000 | 0 | -720000 |  | 0 | 0 | 0 | 0% | 0% | 0%
T | Dec | -744000 | 0 | -744000 |  | 0 | 0 | 0 | 0% | 0% | 0%
Window AC with Baseboard Heat
Coil Level Energy Balance for Annual Test Cases
For Cooling Months
|  | Zone Cooling Requirement - - - - - - - - - - - > |  |  |  | Cooling Coil Requirement - - - - - - - - - - > |  |  | Cooling Coil Output - - - - - - - - - - - - - - - >
Test Case | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain | Fan Heat Added to Air Stream | DX Coil Total Cooling Req'd | DX Coil Latent Cooling Req'd | DX Coil Sensible Cooling Req'd | DX Coil Total Cooling Energy | DX Coil Latent Cooling Energy | DX Coil Sensible Cooling Energy
|  | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh) | (Wh)
I | Jan | -744000 | 0 | -744000 | 2677911231.4842 | 2677167231.4842 | 0 | 2677167231.4842 | 0 | 0 | 0
J | Feb | -672000 | 0 | -672000 | 2419199953.9117 | 2418527953.9117 | 0 | 2418527953.9117 | 0 | 0 | 0
K | Mar | -744000 | 0 | -744000 | 2678399989.9803 | 2677655989.9803 | 0 | 2677655989.9803 | 0 | 0 | 0
L | Apr | -720000 | 0 | -720000 | 2591999989.914 | 2591279989.914 | 0 | 2591279989.914 | 0 | 0 | 0
M | May | 744000 | 223200 | 520800 | 25334.2535 | 769334.2535 | 223200 | 546134.2535 | 766381.347 | 222134.9643 | 544246.3827
N | Jun | 720000 | 216000 | 504000 | 25488.0826 | 745488.0826 | 216000 | 529488.0826 | 743708.3022 | 215988.6047 | 527719.6975
O | Jul | 744000 | 223200 | 520800 | 26777.843 | 770777.843 | 223200 | 547577.843 | 768979.1151 | 223196.6677 | 545782.4474
P | Aug | 744000 | 223200 | 520800 | 26430.7164 | 770430.7164 | 223200 | 547230.7164 | 768593.59 | 223182.0819 | 545411.5081
Q | Sep | 720000 | 216000 | 504000 | 24965.113 | 744965.113 | 216000 | 528965.113 | 743204.395 | 216045.8336 | 527158.5615
R | Oct | -744000 | 0 | -744000 | 2678420834.2389 | 2677676834.2389 | 0 | 2677676834.2389 | 0 | 0 | 0
S | Nov | -720000 | 0 | -720000 | 2591999991.503 | 2591279991.503 | 0 | 2591279991.503 | 0 | 0 | 0
T | Dec | -744000 | 0 | -744000 | 2678399989.5938 | 2677655989.5938 | 0 | 2677655989.5938 | 0 | 0 | 0
Window AC with Baseboard Heat
Coil Level Energy Balance for Annual Test Cases
For Cooling Months
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (DX Coil Total Output - DX Coil Total Req'd) | Difference (DX Coil Latent Output - DX Coil Latent Req'd) | Difference (DX Coil Sensible Output - DX Coil Sensible Req'd) | Difference (DX Coil Total Output vs. DX Coil Total Req'd) | Difference (DX Coil Latent Output vs. DX Coil Latent Req'd) | Difference (DX Coil Sensible Output vs. DX Coil Sensible Req'd)
|  | (Wh) | (Wh) | (Wh) | (%) | (%) | (%)
I | Jan | -2677167231.4842 | 0 | -2677167231.4842 | 359834% | 0% | 359834%
J | Feb | -2418527953.9117 | 0 | -2418527953.9117 | 359900% | 0% | 359900%
K | Mar | -2677655989.9803 | 0 | -2677655989.9803 | 359900% | 0% | 359900%
L | Apr | -2591279989.914 | 0 | -2591279989.914 | 359900% | 0% | 359900%
M | May | -2952.9066 | -1065.0357 | -1887.8709 | -0.3838% | -0.4772% | -0.3457%
N | Jun | -1779.7803 | -11.3953 | -1768.385 | -0.2387% | -0.005276% | -0.334%
O | Jul | -1798.7279 | -3.3323 | -1795.3956 | -0.2334% | -0.001493% | -0.3279%
P | Aug | -1837.1265 | -17.9181 | -1819.2083 | -0.2385% | -0.008028% | -0.3324%
Q | Sep | -1760.718 | 45.8336 | -1806.5515 | -0.2363% | 0.02122% | -0.3415%
R | Oct | -2677676834.2389 | 0 | -2677676834.2389 | 359903% | 0% | 359903%
S | Nov | -2591279991.503 | 0 | -2591279991.503 | 359900% | 0% | 359900%
T | Dec | -2677655989.5938 | 0 | -2677655989.5938 | 359900% | 0% | 359900%
Window AC with Baseboard Heat
Coil Level Energy Balance for Annual Test Cases
For Heating Months
Comparison - - - - - - - - - - >
Test Case | Month | Zone Heating Req'd | Baseboard Heater Req'd | Baseboard Heater Output |  | Difference (Baseboard Output - Baseboard Req'd) | Difference (Baseboard Output vs. Baseboard Req'd)
|  | (Wh) | (Wh) | (Wh) |  | (Wh) | (%)
I | Jan | -744000 | -744000 | -743864.231 |  | 135.769 | -0.01825%
J | Feb | -672000 | -672000 | -671999.9872 |  | 0.012802 | -1.905e-06%
K | Mar | -744000 | -744000 | -743999.9972 |  | 0.0027832 | -3.741e-07%
L | Apr | -720000 | -720000 | -719999.9972 |  | 0.0028017 | -3.891e-07%
M | May | 744000 | 744000 | 0 |  | -744000 | -100%
N | Jun | 720000 | 720000 | 0 |  | -720000 | -100%
O | Jul | 744000 | 744000 | 0 |  | -744000 | -100%
P | Aug | 744000 | 744000 | 0 |  | -744000 | -100%
Q | Sep | 720000 | 720000 | 0 |  | -720000 | -100%
R | Oct | -744000 | -744000 | -744005.7873 |  | -5.7873 | 0.0007779%
S | Nov | -720000 | -720000 | -719999.9976 |  | 0.0023603 | -3.278e-07%
T | Dec | -744000 | -744000 | -743999.9971 |  | 0.0028906 | -3.885e-07%
Window AC with Baseboard Heat
HVAC System Level Energy Balance for Annual Test Cases
For Cooling Months
|  | Zone Cooling Requirement - - - - - - - - - - - > |  |  |  | Cooling Delivered to Zone - - - - - - - - - >
Test Case | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain |  | Window AC Total Zone Cooling Energy | Window AC Latent Zone Cooling Energy | Window AC Sensible Zone Cooling Energy
|  | (Wh) | (Wh) | (Wh) |  | (Wh) | (Wh) | (Wh)
I | Jan | -744000 | 0 | -744000 |  | 0 | 0 | 0
J | Feb | -672000 | 0 | -672000 |  | 0 | 0 | 0
K | Mar | -744000 | 0 | -744000 |  | 0 | 0 | 0
L | Apr | -720000 | 0 | -720000 |  | 0 | 0 | 0
M | May | 744000 | 223200 | 520800 |  | 741047.0934 | 222134.9643 | 518912.1291
N | Jun | 720000 | 216000 | 504000 |  | 718220.2197 | 215988.6047 | 502231.615
O | Jul | 744000 | 223200 | 520800 |  | 742201.2721 | 223196.6677 | 519004.6044
P | Aug | 744000 | 223200 | 520800 |  | 742162.8735 | 223182.0819 | 518980.7917
Q | Sep | 720000 | 216000 | 504000 |  | 718239.282 | 216045.8336 | 502193.4485
R | Oct | -744000 | 0 | -744000 |  | 0 | 0 | 0
S | Nov | -720000 | 0 | -720000 |  | 0 | 0 | 0
T | Dec | -744000 | 0 | -744000 |  | 0 | 0 | 0
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (Total Deliv'd - Total Req'd) | Difference (Latent Deliv'd - Latent Req'd) | Difference (Sensible Deliv'd - Sensible Req'd) | Difference (Total Deliv'd vs. Total Req'd) | Difference (Latent Deliv'd vs. Latent Req'd) | Difference (Sensible Deliv'd vs. Sensible Req'd)
|  | (Wh) | (Wh) | (Wh) | (%) | (%) | (%)
I | Jan | 744000 | 0 | 744000 | -100% | 0% | -100%
J | Feb | 672000 | 0 | 672000 | -100% | 0% | -100%
K | Mar | 744000 | 0 | 744000 | -100% | 0% | -100%
L | Apr | 720000 | 0 | 720000 | -100% | 0% | -100%
M | May | -2952.9066 | -1065.0357 | -1887.8709 | -0.3969% | -0.4772% | -0.3625%
N | Jun | -1779.7803 | -11.3953 | -1768.385 | -0.2472% | -0.005276% | -0.3509%
O | Jul | -1798.7279 | -3.3323 | -1795.3956 | -0.2418% | -0.001493% | -0.3447%
P | Aug | -1837.1265 | -17.9181 | -1819.2083 | -0.2469% | -0.008028% | -0.3493%
Q | Sep | -1760.718 | 45.8336 | -1806.5515 | -0.2445% | 0.02122% | -0.3584%
R | Oct | 744000 | 0 | 744000 | -100% | 0% | -100%
S | Nov | 720000 | 0 | 720000 | -100% | 0% | -100%
T | Dec | 744000 | 0 | 744000 | -100% | 0% | -100%
Window AC with Baseboard Heat
HVAC System Level Energy Balance for Annual Test Cases
For Heating Months
Comparison - - - - - - - - - - >
Test Case | Month | Zone Internal Total Heat Gain | Baseboard Heater Output |  | Difference (Baseboard Heat Deliv'd - Zone Heat Req'd) | Difference (Baseboard Heat Deliv'd vs. Zone Heat Req'd)
|  | (Wh) | (Wh) |  | (Wh) | (%)
I | Jan | -744000 | -743864.231 |  | 135.769 | -0.01825%
J | Feb | -672000 | -671999.9872 |  | 0.012802 | -1.905e-06%
K | Mar | -744000 | -743999.9972 |  | 0.0027832 | -3.741e-07%
L | Apr | -720000 | -719999.9972 |  | 0.0028017 | -3.891e-07%
M | May | 744000 | 0 |  | -744000 | -100%
N | Jun | 720000 | 0 |  | -720000 | -100%
O | Jul | 744000 | 0 |  | -744000 | -100%
P | Aug | 744000 | 0 |  | -744000 | -100%
Q | Sep | 720000 | 0 |  | -720000 | -100%
R | Oct | -744000 | -744005.7873 |  | -5.7873 | 0.0007779%
S | Nov | -720000 | -719999.9976 |  | 0.0023603 | -3.278e-07%
T | Dec | -744000 | -743999.9971 |  | 0.0028906 | -3.885e-07%
Window AC with Baseboard Heat
Equipment Performance Summary for Annual Test Cases
Test Case | Month | HVAC Cooling Electric Consump. | HVAC System Total Cooling | HVAC System Average COP | Supply Fan Electric Consump. |  | Baseboard Heater Output | Baseboard Heater Consumption | Baseboard Heater Efficiency
|  | (Wh) | (Wh) |  | (Wh) |  | (Wh) | (Wh) | (%)
I | Jan | [5 empty] | -743864.231 | -743864.231 | 1
J | Feb | [5 empty] | -671999.9872 | -671999.9872 | 1
K | Mar | [5 empty] | -743999.9972 | -743999.9972 | 1
L | Apr | [5 empty] | -719999.9972 | -719999.9972 | 1
M | May | 188174.3078 | 741047.0934 | 3.9381 | 25334.2535
N | Jun | 200059.3966 | 718220.2197 | 3.59 | 25488.0826
O | Jul | 215672.9987 | 742201.2721 | 3.4413 | 26777.843
P | Aug | 208160.061 | 742162.8735 | 3.5653 | 26430.7164
Q | Sep | 189481.2129 | 718239.282 | 3.7906 | 24965.113
R | Oct | [5 empty] | -744005.7873 | -744005.7873 | 1
S | Nov | [5 empty] | -719999.9976 | -719999.9976 | 1
T | Dec | [5 empty] | -743999.9971 | -743999.9971 | 1
|  | Cooling Delivered to Zone By HVAC System |  |  |  |  | HVAC System Cooling Including Fan Heat |  |  |  | Output of Cooling Coil
Test Case | Month | Window AC Total Zone Cooling Energy | Window AC Latent Zone Cooling Energy | Window AC Zone Sensible Zone Cooling Energy | Fan Heat Added to Air Stream |  | Req'd Window AC Total Zone Cooling Energy | Req'd Window AC Latent Zone Cooling Energy | Req'd Window AC Sensible Zone Cooling Energy |  | DX Coil Total Cooling Energy | DX Coil Latent Cooling Energy | DX Coil Sensible Cooling Energy
|  | (Wh) | (Wh) | (Wh) | (Wh) | [5 empty] | (Wh) | (Wh) | (Wh)
M | May | 741047.0934 | 222134.9643 | 518912.1291 | 25334.2535 |  | 766381.347 | 222134.9643 | 544246.3827 |  | 766381.347 | 222134.9643 | 544246.3827
N | Jun | 718220.2197 | 215988.6047 | 502231.615 | 25488.0826 |  | 743708.3022 | 215988.6047 | 527719.6975 |  | 743708.3022 | 215988.6047 | 527719.6975
O | Jul | 742201.2721 | 223196.6677 | 519004.6044 | 26777.843 |  | 768979.1151 | 223196.6677 | 545782.4474 |  | 768979.1151 | 223196.6677 | 545782.4474
P | Aug | 742162.8735 | 223182.0819 | 518980.7917 | 26430.7164 |  | 768593.59 | 223182.0819 | 545411.5081 |  | 768593.59 | 223182.0819 | 545411.5081
Q | Sep | 718239.282 | 216045.8336 | 502193.4485 | 24965.113 |  | 743204.395 | 216045.8336 | 527158.5615 |  | 743204.395 | 216045.8336 | 527158.5615
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (Total Deliv'd - Total Req'd) | Difference (Latent Deliv'd - Latent Req'd) | Difference (Sensible Deliv'd - Sensible Req'd) | Difference (Total Deliv'd vs. Total Req'd) | Difference (Latent Deliv'd vs. Latent Req'd) | Difference (Sensible Deliv'd vs. Sensible Req'd)
|  | (Wh) | (Wh) | (Wh) | (%) | (%) | (%)
M | May | -1.0477e-09 | 0 | 0 | -1.367e-13% | 0% | 0%
N | Jun | 0 | 0 | -1.0477e-09 | 0% | 0% | -1.985e-13%
O | Jul | 0 | 0 | 0 | 0% | 0% | 0%
P | Aug | 0 | 0 | 0 | 0% | 0% | 0%
Q | Sep | 0 | 0 | 0 | 0% | 0% | 0%