## CSV Labels Hidden
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
Varying internal loads of either 10000W or -10000W
16 Day Test
Hydronic Heating/Cooling System
Zone Level Energy Balance for Daily Test Cases
Zone Energy Input - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
|  |  | Daily | Daily | Daily | Daily | Internal | Internal | Daily | Zone Air Temp. | Zone Air Temp. | Zone Air Humidity Ratio | Zone Air Humidity Ratio
|  | Daily | Electric | Other | Gas | Steam | Loads | Loads | Total
Test | Day | Lights | Equipment | Equipment | Equipment | Equipment | % | % | Internal | Min | Max | Min | Max
Case |  | Consump. | Consump. | Consump. | Consump. | Consump. | Latent | Radiant | Consump.
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  |  | (kWh) | (C) | (C) | ( ) | ( )
| 1 | 0 | 0 | -240 | 0 | 0 | 0 | 0 | -240 | 22.1998 | 22.2004 | 0.010093 | 0.010093
A | 2 | 0 | 0 | -240 | 0 | 0 | 0 | 0 | -240 | 22.2 | 22.2005 | 0.010093 | 0.010093
| 3 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 22.1994 | 22.1999 | 0.010093 | 0.010093
B | 4 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 22.1991 | 22.1994 | 0.010093 | 0.010093
| 5 | 240 | 240 | 0 | 0 | 0 | 0 | 0 | 480 | 22.1995 | 22.2002 | 0.010093 | 0.010093
C | 6 | 240 | 240 | 0 | 0 | 0 | 0 | 0 | 480 | 22.2 | 22.2001 | 0.010093 | 0.010093
| 7 | 240 | 240 | 240 | 0 | 0 | 0 | 0 | 720 | 22.2001 | 22.2002 | 0.010093 | 0.010093
D | 8 | 240 | 240 | 240 | 0 | 0 | 0 | 0 | 720 | 22.2002 | 22.2002 | 0.010093 | 0.010093
| 9 | 240 | 240 | 240 | 240 | 0 | 0 | 0 | 960 | 22.1993 | 22.2012 | 0.010116 | 0.010203
E | 10 | 240 | 240 | 240 | 240 | 0 | 0 | 0 | 960 | 22.1991 | 22.2008 | 0.010189 | 0.010201
| 11 | 240 | 240 | 240 | 240 | 240 | 0 | 0 | 1200 | 22.1981 | 22.201 | 0.0091219 | 0.0096446
F | 12 | 240 | 240 | 240 | 240 | 240 | 0 | 0 | 1200 | 22.1979 | 22.2013 | 0.0090356 | 0.0091425
| 13 | 0 | 0 | 240 | 0 | 0 | 0 | 20 | 240 | 22.1999 | 22.2006 | 0.0090313 | 0.0090313
G | 14 | 0 | 0 | 240 | 0 | 0 | 0 | 20 | 240 | 22.1998 | 22.2001 | 0.0090313 | 0.0090313
| 15 | 0 | 0 | 240 | 0 | 0 | 30 | 0 | 240 | 22.1999 | 22.2001 | 0.0094666 | 0.015807
H | 16 | 0 | 0 | 240 | 0 | 0 | 30 | 0 | 240 | 22.1999 | 22.2004 | 0.015807 | 0.015812
|  | Zone Energy Output - - - - - - - - - - - - - - - - - - - - - > |  |  |  | Comparison - - - - - - - - - - - - - >
Test Case | Day | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain |  | Difference (Total Output - Total Input) | Difference (Total Output vs. Total Input)
|  | (kWh) | (kWh) | (kWh) |  | (kWh) | (kWh)
| 1 | -240 | 0 | -240 |  | 0 | 0%
A | 2 | -240 | 0 | -240 |  | 0 | 0%
| 3 | 240 | 0 | 240 |  | 0 | 0%
B | 4 | 240 | 0 | 240 |  | 0 | 0%
| 5 | 480 | 0 | 480 |  | 0 | 0%
C | 6 | 480 | 0 | 480 |  | 0 | 0%
| 7 | 720 | 0 | 720 |  | 0 | 0%
D | 8 | 720 | 0 | 720 |  | 0 | 0%
| 9 | 960 | 0 | 960 |  | 0 | 0%
E | 10 | 960 | 0 | 960 |  | 0 | 0%
| 11 | 1200 | 0 | 1200 |  | 0 | 0%
F | 12 | 1200 | 0 | 1200 |  | 0 | 0%
| 13 | 240 | 0 | 240 |  | 0 | 0%
G | 14 | 240 | 0 | 240 |  | 0 | 0%
| 15 | 240 | 72 | 168 |  | 0 | 0%
H | 16 | 240 | 72 | 168 |  | 0 | 0%
Hydronic Heating/Cooling System
Cooling Coil Level Energy Balance for Daily Test Cases
|  | Zone Cooling Requirement - - - - - - - - - - - - - - - > |  |  |  | Cooling Coil Requirement - - - - - - - - - - - - - - - > |  |  | Cooling Coil Output - - - - - - - - - - - - - - - - - - - >
Test Case | Day | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain | Fan Heat Added to Air Stream | Cooling Coil Total Cooling Req'd) | Cooling Coil Latent Cooling Req'd | Cooling Coil Sensible Cooling Req'd | Cooling Coil Total Cooling Energy | Cooling Coil Latent Cooling Energy | Cooling Coil Sensible Cooling Energy
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
| 1 | 0 | 4.4467e-05 | -4.4467e-05 | 0 | 0 | 4.4467e-05 | -4.4467e-05 | 0 | 0 | 0
A | 2 | 0 | 4.4467e-05 | -4.4467e-05 | 0 | 0 | 4.4467e-05 | -4.4467e-05 | 0 | 0 | 0
| 3 | 0.000148 | 4.4467e-05 | 0.00010353 | 4.1539 | 4.154 | 4.4467e-05 | 4.154 | 0.12441 | 0 | 0.12441
B | 4 | 240 | 0 | 240 | 26.1759 | 266.1759 | 0 | 266.1759 | 266.191 | 0 | 266.191
| 5 | 480 | 240 | 240 | 26.1759 | 506.1759 | 240 | 266.1759 | 506.1842 | 0 | 506.1842
C | 6 | 480 | 0 | 480 | 26.1759 | 506.1759 | 0 | 506.1759 | 506.1837 | 0 | 506.1837
| 7 | 720 | 240 | 480 | 26.1759 | 746.1759 | 240 | 506.1759 | 746.1812 | 0 | 746.1812
D | 8 | 720 | 0 | 720 | 26.1759 | 746.1759 | 0 | 746.1759 | 746.1801 | 0 | 746.1801
| 9 | 960 | 240 | 720 | 26.1759 | 986.1759 | 240 | 746.1759 | 985.7391 | -0.4348 | 986.1739
E | 10 | 960 | 0 | 960 | 26.1759 | 986.1759 | 0 | 986.1759 | 986.1818 | 0.0030407 | 986.1788
| 11 | 1200 | 240 | 960 | 26.1759 | 1226.1759 | 240 | 986.1759 | 1230.733 | 4.5038 | 1226.2292
F | 12 | 1200 | 0 | 1200 | 26.1759 | 1226.1759 | 0 | 1226.1759 | 1226.5751 | 0.39781 | 1226.1773
| 13 | 240 | 0 | 240 | 26.1759 | 266.1759 | 0 | 266.1759 | 263.6479 | 0 | 263.6479
G | 14 | 240 | 0 | 240 | 26.1759 | 266.1759 | 0 | 266.1759 | 264.9299 | 0 | 264.9299
| 15 | 240 | 0 | 240 | 26.1759 | 266.1759 | 0 | 266.1759 | 238.8967 | 42.2929 | 196.6038
H | 16 | 240 | 72 | 168 | 26.1759 | 266.1759 | 72 | 194.1759 | 266.7013 | 70.8154 | 195.8859
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Day | Difference (Total Output - Total Req'd) | Difference (Latent Output - Latent Req'd) | Difference (Sensible Output - Sensible Req'd) | Difference (Total Output vs. Total Req'd) | Difference (Latent Output vs. Latent Req'd) | Difference (Sensible Output vs. Sensible Req'd)
|  | (kWh) | (kWh) | (kWh) | (%) | (%) | (%)
| 1 | 0 | -4.4467e-05 | 4.4467e-05 | 0% | -100% | -100%
A | 2 | 0 | -4.4467e-05 | 4.4467e-05 | 0% | -100% | -100%
| 3 | -4.0296 | -4.4467e-05 | -4.0295 | -97% | -100% | -97%
B | 4 | 0.015115 | 0 | 0.015115 | 0.005679% | 0% | 0.005679%
| 5 | 0.0082737 | -240 | 240.0083 | 0.001635% | -100% | 90.17%
C | 6 | 0.0078342 | 0 | 0.0078342 | 0.001548% | 0% | 0.001548%
| 7 | 0.0052986 | -240 | 240.0053 | 0.0007101% | -100% | 47.42%
D | 8 | 0.0041978 | 0 | 0.0041978 | 0.0005626% | 0% | 0.0005626%
| 9 | -0.43678 | -240.4348 | 239.998 | -0.04429% | -100.2% | 32.16%
E | 10 | 0.0058775 | 0.0030407 | 0.0028368 | 0.000596% | 0% | 0.0002877%
| 11 | 4.5571 | -235.4962 | 240.0533 | 0.3717% | -98.12% | 24.34%
F | 12 | 0.3992 | 0.39781 | 0.0013927 | 0.03256% | 0% | 0.0001136%
| 13 | -2.528 | 0 | -2.528 | -0.9498% | 0% | -0.9498%
G | 14 | -1.246 | 0 | -1.246 | -0.4681% | 0% | -0.4681%
| 15 | -27.2792 | 42.2929 | -69.5721 | -10.25% | 0% | -26.14%
H | 16 | 0.52538 | -1.1846 | 1.71 | 0.1974% | -1.645% | 0.8806%
Hydronic Heating/Cooling System
Heating Coil Level Energy Balance for Daily Test Cases
|  | Zone Heating Requirement - - - - - - - - - - - - - - - - > | [6 empty] | Comparison - - - - - - - >
Test Case | Day | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain | Fan Heat Added to Air Stream | Heating Coil Total Heating Req'd) | Heating Coil Total Heating Energy Output |  | Difference (Total Output - Total Req'd) | Difference (Total Output vs. Total Req'd)
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (kWh) | (%)
| 1 | 0.000148 | 4.4467e-05 | 0.00010353 | 4.1539 | 4.154 | 0 |  | -4.154 | -100%
A | 2 | -240 | 0 | -240 | 26.1759 | -213.8241 | -213.7967 |  | 0.027407 | -0.01282%
Hydronic Heating/Cooling System
Hot Water Loop Energy Balance for Daily Test Cases
Test Case | Month | Zone/Sys Daily Average Temp | Zone/Sys Daily Heating Req'd | Heating Coil Daily Output | Daily Fan Heat to Air Stream | Fan Coil Daily Heating Output Delivered to Zone | Hot Water Pump Daily Electric Consumption | Daily Hot Water Pump Heat to Fluid | Daily Boiler Load | Daily Boiler Load Should = Heating Coil Output - Pump Heat to Fluid | Daily Boiler Load Should = Zone Heating Req'd -Fan Heat - Pump Heat to Fluid
|  | (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
| 1 | 8907.9103 | 26.1759 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 22.0221
A | 2 | 22.2004 | 239.9735 | 213.7967 | 26.1759 | 239.9726 | 4.1539 | 3.7385 | 209.6254 | 210.0582 | 210.0591
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Day | Difference (Daily Boiler Load vs. Heating Coil Output - Pump Heat to Fluid) | Difference (Daily Boiler Load vs. Zone Heating Req'd -Fan Heat - Pump Heat to Fluid) | Difference (Daily Boiler Load vs. Heating Coil Output - Pump Heat to Fluid) | Difference (Daily Boiler Load vs. Zone Heating Req'd -Fan Heat - Pump Heat to Fluid)
|  | (kWh) | (kWh) | (%) | (%)
| 1 | 0 | 22.0221 | #DIV/0! | #DIV/0!
A | 2 | 0.43286 | 0.43374 | 0.2065% | 0.2069%
Hydronic Heating/Cooling System
Chilled Water Loop Energy Balance for Daily Test Cases
| OUTVARSCHED:Schedule Value [](Hourly:OUTVARSCHED) | COMPACT HVAC-ALWAYS 100:Schedule Value [](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Evaporator Outlet Temperature [C](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Electric Power [W](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Part Load Ratio [](Hourly:OUTVARSCHED) | 0 | 0 | HOT WATER LOOP HW SUPPLY PUMP:Pump Fluid Heat Gain Rate [W](Hourly:OUTVARSCHED) |  |  | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | 0 | 0 | 0
Test Case | Day | Zone/Sys Daily Average Temp | Zone/Sys Daily Cooling Req'd | Cooling Coil Daily Output | Daily Fan Heat to Air Stream | Fan Coil Daily Cooling Output Delivered to Zone | Chilled Water Pump Daily Electric Consumption | Daily Chilled Water Pump Heat to Fluid | Daily Chiller Load | Daily Chiller Load Should = Cooling Coil Output + CHW Pump Heat | Daily Chiller Load Should = Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid
|  | (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
| 1 | 8907.9103 | 0.000148 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 4.154
A | 2 | 8908.195 | 0.000148 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 4.154
| 3 | 0 | 0.000148 | 0.12441 | 0 | 0.014001 | 0 | 0 | 0 | 0.12441 | 0.000148
B | 4 | 22.1993 | 240 | 266.191 | 26.1759 | 240.0151 | 33.5813 | 30.2231 | 296.2811 | 296.4142 | 296.399
| 5 | 22.2001 | 480 | 506.1842 | 26.1759 | 480.0083 | 33.5813 | 30.2231 | 534.3891 | 536.4073 | 536.399
C | 6 | 22.2001 | 480 | 506.1837 | 26.1759 | 480.0078 | 33.5813 | 30.2231 | 535.9488 | 536.4069 | 536.399
| 7 | 22.2002 | 720 | 746.1812 | 26.1759 | 720.0053 | 33.5813 | 30.2231 | 773.889 | 776.4043 | 776.399
D | 8 | 22.2002 | 720 | 746.1801 | 26.1759 | 720.0042 | 33.5813 | 30.2231 | 775.4471 | 776.4032 | 776.399
| 9 | 22.2001 | 960 | 985.7391 | 26.1759 | 959.5632 | 33.5813 | 30.2231 | 1012.7993 | 1015.9623 | 1016.399
E | 10 | 22.1998 | 960 | 986.1818 | 26.1759 | 960.0059 | 33.5813 | 30.2231 | 1014.7991 | 1016.4049 | 1016.399
| 11 | 22.1996 | 1200 | 1230.733 | 26.1759 | 1204.5571 | 33.5813 | 30.2231 | 1256.9596 | 1260.9561 | 1256.399
F | 12 | 22.1995 | 1200 | 1226.5751 | 26.1759 | 1200.3992 | 33.5813 | 30.2231 | 1254.3679 | 1256.7983 | 1256.399
| 13 | 22.2001 | 240 | 263.6479 | 26.1759 | 237.472 | 33.5813 | 30.2231 | 299.9976 | 293.871 | 296.399
G | 14 | 22.2 | 240 | 264.9299 | 26.1759 | 238.754 | 33.5813 | 30.2231 | 295.0181 | 295.153 | 296.399
| 15 | 22.2 | 240 | 238.8967 | 26.1759 | 212.7208 | 33.5813 | 30.2231 | 268.9983 | 269.1199 | 296.399
H | 16 | 22.2 | 240 | 266.7013 | 26.1759 | 240.5254 | 33.5813 | 30.2231 | 296.7916 | 296.9244 | 296.399
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Day | Difference (Daily Chiller Load vs. Cooling Coil Output + CHW Pump Heat) | Difference (Daily Chiller Load vs. Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid) | Difference (Daily Chiller Load vs. Cooling Coil Output + CHW Pump Heat) | Difference (Daily Chiller Load vs. Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid)
|  | (kWh) | (kWh) | (%) | (%)
| 1 | 0 | 4.154 | 0% | 0%
A | 2 | 0 | 4.154 | 0% | 0%
| 3 | 0.12441 | 0.000148 | #DIV/0! | #DIV/0!
B | 4 | 0.13308 | 0.11797 | 0.04492% | 0.03982%
| 5 | 2.0182 | 2.0099 | 0.3777% | 0.3761%
C | 6 | 0.45805 | 0.45022 | 0.08547% | 0.084%
| 7 | 2.5154 | 2.5101 | 0.325% | 0.3243%
D | 8 | 0.95618 | 0.95199 | 0.1233% | 0.1228%
| 9 | 3.1629 | 3.5997 | 0.3123% | 0.3554%
E | 10 | 1.6058 | 1.5999 | 0.1582% | 0.1577%
| 11 | 3.9965 | -0.56059 | 0.3179% | -0.0446%
F | 12 | 2.4304 | 2.0312 | 0.1938% | 0.1619%
| 13 | -6.1266 | -3.5986 | -2.042% | -1.2%
G | 14 | 0.13491 | 1.381 | 0.04573% | 0.4681%
| 15 | 0.12159 | 27.4008 | 0.0452% | 10.19%
H | 16 | 0.13281 | -0.39257 | 0.04475% | -0.1323%
Hydronic Heating/Cooling System
Condenser Water Loop Energy Balance for Daily Test Cases
Comparison - - - - - - - - - - - - - >
Test Case | Day | Chiller Daily Electric Consumption | Condenser Water Pump Daily Electric Consumption | Daily Condenser Water Pump Heat to Fluid | Daily Cooling Tower Load | Daily Cooling Tower Load Should = Chiller Load + Chiller Electric Consumption + CNW Pump Heat | Difference(Daily Colling Tower Load vs. Chiller Load + Chiller Electric Consumption + CNW Pump Heat) | Difference(Daily Colling Tower Load vs. Chiller Load + Chiller Electric Consumption + CNW Pump Heat)
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%)
| 1 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
A | 2 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
B | 4 | 111.6383 | 50.4022 | 45.362 | 453.2923 | 453.2814 | -0.010968 | -0.00242%
| 5 | 172.0112 | 50.4022 | 45.362 | 749.8171 | 751.7623 | 1.9452 | 0.2594%
C | 6 | 172.3971 | 50.4022 | 45.362 | 753.7269 | 753.7079 | -0.018999 | -0.002521%
| 7 | 227.7608 | 50.4022 | 45.362 | 1045.1085 | 1047.0117 | 1.9032 | 0.1821%
D | 8 | 228.1137 | 50.4022 | 45.362 | 1048.9497 | 1048.9228 | -0.026901 | -0.002565%
| 9 | 278.3938 | 50.4022 | 45.362 | 1334.6933 | 1336.5551 | 1.8618 | 0.1395%
E | 10 | 278.8036 | 50.4022 | 45.362 | 1338.9996 | 1338.9647 | -0.034861 | -0.002603%
| 11 | 324.999 | 50.4022 | 45.362 | 1625.5007 | 1627.3206 | 1.8199 | 0.112%
F | 12 | 324.5413 | 50.4022 | 45.362 | 1624.3045 | 1624.2711 | -0.03333 | -0.002052%
| 13 | 112.5139 | 50.4022 | 45.362 | 465.5588 | 457.8734 | -7.6854 | -1.651%
G | 14 | 111.3049 | 50.4022 | 45.362 | 451.692 | 451.6849 | -0.0070986 | -0.001572%
| 15 | 104.3558 | 50.4022 | 45.362 | 418.7116 | 418.7161 | 0.0045313 | 0.001082%
H | 16 | 111.7731 | 50.4022 | 45.362 | 453.939 | 453.9267 | -0.012308 | -0.002711%
Hydronic Heating/Cooling System
Equipment Performance Summary for Daily Test Cases
Test Case | Day | Daily Chiller Load | Chiller Daily Electric Consumption | Chiller Average COP |  | Daily Boiler Load | Boiler Daily Gas Consumption | Boiler Average Efficiency
|  | (kWh) | (kWh) | ( ) |  | (kWh) | (kWh) | (% )
| 1 |  |  |  |  | 0 | 0 | #DIV/0!
A | 2 |  |  |  |  | 209.6254 | 262.2701 | 79.93%
| 3 | 0 | 0 | #DIV/0!
B | 4 | 296.2811 | 111.6383 | 2.6539
| 5 | 534.3891 | 172.0112 | 3.1067
C | 6 | 535.9488 | 172.3971 | 3.1088
| 7 | 773.889 | 227.7608 | 3.3978
D | 8 | 775.4471 | 228.1137 | 3.3994
| 9 | 1012.7993 | 278.3938 | 3.638
E | 10 | 1014.7991 | 278.8036 | 3.6398
| 11 | 1256.9596 | 324.999 | 3.8676
F | 12 | 1254.3679 | 324.5413 | 3.865
| 13 | 299.9976 | 112.5139 | 2.6663
G | 14 | 295.0181 | 111.3049 | 2.6505
| 15 | 268.9983 | 104.3558 | 2.5777
H | 16 | 296.7916 | 111.7731 | 2.6553

## CSV Labels
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
Varying internal loads of either 10000W or -10000W
16 Day Test
Hot Water Loop Energy Balance
| ZONE1FANCOILHEATINGCOIL:Heating Coil Heating Rate [W](Hourly:OUTVARSCHED) | ZONE1FANCOILFAN:Fan Electric Energy [J](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CHW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly:OUTVARSCHED) | 0 | 0 | 0
| Zone/Sys Monthly Average Temp | Zone/Sys Monthly Heating Req'd | Heating Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Heating Output Delivered to Zone | Hot Water Pump Monthly Electric Consumption | Monthly Hot Water Pump Heat to Fluid | Monthly Boiler Load | Monthly Boiler Load Should = Heating Coil Output - Pump Heat to Fluid | Monthly Boiler Load Should = Zone Heating Req'd -Fan Heat - Pump Heat to Fluid
| (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
Day 1 | 8907.9103 | 26.1759 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 22.0221
Day 2 | 8908.195 | 26.1759 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 22.0221
Day 3 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 4 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 5 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 6 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 7 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 8 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 9 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 10 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 11 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 12 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 13 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 14 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day 15 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Day16 | 0 | 26.1759 | 33.5813 | 0 | 0.070464 | 0 | 0 | 0 | 33.5813 | 26.1759
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
10000 W constant cooling load during summer months
-10000 W heating load during winter months
Chilled Water Loop Energy Balance
| ZONE1FANCOILHEATINGCOIL:Heating Coil Heating Rate [W](Hourly:OUTVARSCHED) | ZONE ONE:Zone Thermostat Cooling Setpoint Temperature [C](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CONDENSER WATER LOOP:Plant Supply Side Cooling Demand Rate [W](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CNDW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | 0 | 0 | 0
| Zone/Sys Monthly Average Temp | Zone/Sys Monthly Cooling Req'd | Cooling Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Cooling Output Delivered to Zone | Chilled Water Pump Monthly Electric Consumption | Monthly Chilled Water Pump Heat to Fluid | Monthly Chiller Load | Monthly Chiller Load Should = Cooling Coil Output + CHW Pump Heat | Monthly Chiller Load Should = Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid
| (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
Day 1 | 8907.9103 | 0.000148 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 4.154
Day 2 | 8908.195 | 0.000148 | 0 | 4.1539 | 0 | 0 | 0 | 0 | 0 | 4.154
Day 3 | 0 | 0.000148 | 0.12441 | 0 | 0.014001 | 0 | 0 | 0 | 0.12441 | 0.000148
Day 4 | 0 | 0.000148 | 0.12591 | 0 | 0.014001 | 0 | 0 | 0 | 0.12591 | 0.000148
Day 5 | 0 | 0.000148 | 0.20828 | 0 | 0.014001 | 0 | 0 | 0 | 0.20828 | 0.000148
Day 6 | 0 | 0.000148 | 0.20937 | 0 | 0.014001 | 0 | 0 | 0 | 0.20937 | 0.000148
Day 7 | 0 | 0.000148 | 0.29031 | 0 | 0.014001 | 0 | 0 | 0 | 0.29031 | 0.000148
Day 8 | 0 | 0.000148 | 0.29137 | 0 | 0.014001 | 0 | 0 | 0 | 0.29137 | 0.000148
Day 9 | 0 | 0.000148 | 0.37075 | 0 | 0.014001 | 0 | 0 | 0 | 0.37075 | 0.000148
Day 10 | 0 | 0.000148 | 0.37194 | 0 | 0.014001 | 0 | 0 | 0 | 0.37194 | 0.000148
Day 11 | 0 | 0.000148 | 0.45153 | 0 | 0.014001 | 0 | 0 | 0 | 0.45153 | 0.000148
Day 12 | 0 | 0.000148 | 0.4512 | 0 | 0.014001 | 0 | 0 | 0 | 0.4512 | 0.000148
Day 13 | 0 | 0.000148 | 0.12932 | 0 | 0.014001 | 0 | 0 | 0 | 0.12932 | 0.000148
Day 14 | 0 | 0.000148 | 0.12547 | 0 | 0.014001 | 0 | 0 | 0 | 0.12547 | 0.000148
Day 15 | 0 | 0.000148 | 0.11631 | 0 | 0.014001 | 0 | 0 | 0 | 0.11631 | 0.000148
Day16 | 0 | 0.000148 | 0.12609 | 0 | 0.014001 | 0 | 0 | 0 | 0.12609 | 0.000148
Condenser Water Loop Energy Balance
| 0 | 0 | 0 | 0
| Chiller Monthly Electric Consumption | Condenser Water Pump Monthly Electric Consumption | Monthly Condenser Water Pump Heat to Fluid | Monthly Cooling Tower Load | Monthly Cooling Tower Load Should = Chiller Load + Chiller Electric Consumption + CNW Pump Heat
| (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
Day 1 | 0 | 0 | 0 | 0 | 0
Day 2 | 0 | 0 | 0 | 0 | 0
Day 3 | 0 | 0 | 0 | 0 | 0
Day 4 | 0 | 0 | 0 | 0 | 0
Day 5 | 0 | 0 | 0 | 0 | 0
Day 6 | 0 | 0 | 0 | 0 | 0
Day 7 | 0 | 0 | 0 | 0 | 0
Day 8 | 0 | 0 | 0 | 0 | 0
Day 9 | 0 | 0 | 0 | 0 | 0
Day 10 | 0 | 0 | 0 | 0 | 0
Day 11 | 0 | 0 | 0 | 0 | 0
Day 12 | 0 | 0 | 0 | 0 | 0
Day 13 | 0 | 0 | 0 | 0 | 0
Day 14 | 0 | 0 | 0 | 0 | 0
Day 15 | 0 | 0 | 0 | 0 | 0
Day16 | 0 | 0 | 0 | 0 | 0