## CSV Labels Hidden
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
10000 W constant cooling load during summer months
-10000 W heating load during winter months
Hydronic Heating/Cooling System
Zone Level Energy Balance for Annual Test Cases
Zone Energy Input - - - - - - - - - - - - - - - - - - - - - - - - - - >
|  | Daily | Internal | Internal | Daily | Zone Air Temp. | Zone Air Temp. | Zone Air Humidity Ratio | Zone Air Humidity Ratio
|  | Other | Convective | Latent | Total
Test | Month | Equipment | Load | Load | Internal | Min | Max | Min | Max
Case |  | Consump. |  |  | Load
|  | (kWh) | (kWh) | (kWh) | (kWh) | (C) | (C) | ( ) | ( )
I | Jan | -7440 | -7440 | 0 | -7440 | 22.1999 | 22.2001 | 0.00083893 | 0.0093826
J | Feb | -6720 | -6720 | 0 | -6720 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
K | Mar | -7440 | -7440 | 0 | -7440 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
L | Apr | -7200 | -7200 | 0 | -7200 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
M | May | 7440 | 7440 | 0 | 7440 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
N | Jun | 7200 | 7200 | 0 | 7200 | 22.2001 | 22.2001 | 0.0019353 | 0.0019353
O | Jul | 7440 | 7440 | 0 | 7440 | 22.2001 | 22.2001 | 0.0019353 | 0.0019353
P | Aug | 7440 | 7440 | 0 | 7440 | 22.2001 | 22.2001 | 0.0019353 | 0.0019353
Q | Sep | 7200 | 7200 | 0 | 7200 | 22.2001 | 22.2001 | 0.0019353 | 0.0019353
R | Oct | -7440 | -7440 | 0 | -7440 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
S | Nov | -7200 | -7200 | 0 | -7200 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
T | Dec | -7440 | -7440 | 0 | -7440 | 22.2 | 22.2001 | 0.0019353 | 0.0019353
|  | Zone Energy Output - - - - - - - - - - - - - - - - > |  |  |  | Comparison - - - - - - - - - - - - - >
Test | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain |  | Difference (Total Output - Total Input) | Difference (Total Output vs. Total Input)
Case
|  | (kWh) | (kWh) | (kWh) |  | (kWh) | (%)
I | Jan | -7440 | 0 | -7439.8643 |  | 0 | 0%
J | Feb | -6720 | 0 | -6719.9995 |  | 0 | 0%
K | Mar | -7440 | 0 | -7439.9995 |  | 0 | 0%
L | Apr | -7200 | 0 | -7199.9995 |  | 0 | 0%
M | May | 7440 | 0 | 7440 |  | 0 | 0%
N | Jun | 7200 | 0 | 7200 |  | 0 | 0%
O | Jul | 7440 | 0 | 7440 |  | 0 | 0%
P | Aug | 7440 | 0 | 7440 |  | 0 | 0%
Q | Sep | 7200 | 0 | 7200 |  | 0 | 0%
R | Oct | -7440 | 0 | -7439.9995 |  | 0 | 0%
S | Nov | -7200 | 0 | -7199.9995 |  | 0 | 0%
T | Dec | -7440 | 0 | -7439.9995 |  | 0 | 0%
Hydronic Heating/Cooling System
Coil Level Energy Balance for Annual Test Cases
For Cooling Months
|  | Zone Cooling Requirement - - - - - - - - - - - - - - - > |  |  |  | Cooling Coil Requirement - - - - - - - - - - - - - - - > |  |  | Cooling Coil Output - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain | Fan Heat Added to Air Stream | Cooling Coil Total Cooling Req'd) | Cooling Coil Latent Cooling Req'd | Cooling Coil Sensible Cooling Req'd | Cooling Coil Total Cooling Energy | Cooling Coil Latent Cooling Energy | Cooling Coil Sensible Cooling Energy
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
I | Jan | -7440 | 0 | -7439.8643 | 165.9796 | -7273.8847 | 0 | -7439.8643 | 0 | 0 | 0
J | Feb | -6720 | 0 | -6719.9995 | 149.9171 | -6570.0824 | 0 | -6719.9995 | 0 | 0 | 0
K | Mar | -7440 | 0 | -7439.9995 | 165.9796 | -7274.0198 | 0 | -7439.9995 | 0 | 0 | 0
L | Apr | -7200 | 0 | -7199.9995 | 160.6254 | -7039.3741 | 0 | -7199.9995 | 0 | 0 | 0
M | May | 7440 | 0 | 7440 | 165.9796 | 7605.9796 | 0 | 7605.9796 | 7605.9796 | 0 | 7605.9796
N | Jun | 7200 | 0 | 7200 | 160.6254 | 7360.6254 | 0 | 7360.6254 | 7360.6254 | 0 | 7360.6254
O | Jul | 7440 | 0 | 7440 | 165.9796 | 7605.9796 | 0 | 7605.9796 | 7605.9796 | 0 | 7605.9796
P | Aug | 7440 | 0 | 7440 | 165.9796 | 7605.9796 | 0 | 7605.9796 | 7605.9796 | 0 | 7605.9796
Q | Sep | 7200 | 0 | 7200 | 160.6254 | 7360.6254 | 0 | 7360.6254 | 7360.6254 | 0 | 7360.6254
R | Oct | -7440 | 0 | -7439.9995 | 165.9796 | -7274.0199 | 0 | -7439.9995 | 0 | 0 | 0
S | Nov | -7200 | 0 | -7199.9995 | 160.6254 | -7039.374 | 0 | -7199.9995 | 0 | 0 | 0
T | Dec | -7440 | 0 | -7439.9995 | 165.9796 | -7274.0199 | 0 | -7439.9995 | 0 | 0 | 0
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (Coil Total Output - Coil Total Req'd) | Difference (Coil Latent Output - Coil Latent Req'd) | Difference (Coil Sensible Output - Coil Sensible Req'd) | Difference (Coil Total Output vs. Coil Total Req'd) | Difference (Coil Latent Output vs. Coil Latent Req'd) | Difference (Coil Sensible Output vs. Coil Sensible Req'd)
|  | (Wh) | (Wh) | (Wh) | (%) | (%) | (%)
M | May | 9.9851e-06 | 0 | 9.9851e-06 | -1.342e-07% | 0% | -1.342e-07%
N | Jun | -2.3738e-10 | 0 | -2.3738e-10 | 3.532e-12% | 0% | 3.532e-12%
O | Jul | -3.5561e-10 | 0 | -3.5561e-10 | 4.78e-12% | 0% | 4.78e-12%
P | Aug | -1.5098e-10 | 0 | -1.5098e-10 | 2.097e-12% | 0% | 2.097e-12%
Q | Sep | -1.9827e-10 | 0 | -1.9827e-10 | -2.607e-12% | 0% | -2.607e-12%
Hydronic Heating/Cooling System
Coil Level Energy Balance for Annual Test Cases
For Heating Months
|  | Zone Heating Requirement - - - - - - - - - - - - - - - - > | [6 empty] | Comparison - - - - - - - >
Test Case | Month | Zone Internal Total Heat Gain | Zone Internal Latent Heat Gain | Zone Internal Sensible Heat Gain | Fan Heat Added to Air Stream | Heating Coil Total Heating Req'd) | Heating Coil Total Heating Energy Output |  | Difference (Total Output - Total Req'd) | Difference (Total Output vs. Total Req'd)
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  | (kWh) | (%)
I | Jan | 7439.8643 | 0 | 7439.8643 | 165.9796 | 7273.8847 | 7273.8847 |  | 2.7356e-05 | 3.761e-07%
J | Feb | 6719.9995 | 0 | 6719.9995 | 149.9171 | 6570.0824 | 6570.0824 |  | -9.4581e-06 | -1.44e-07%
K | Mar | 7439.9995 | 0 | 7439.9995 | 165.9796 | 7274.0198 | 7274.0198 |  | -4.9935e-06 | -6.865e-08%
L | Apr | 7199.9995 | 0 | 7199.9995 | 160.6254 | 7039.3741 | 7039.3741 |  | 1.2166e-05 | 1.728e-07%
R | Oct | 7439.9995 | 0 | 7439.9995 | 165.9796 | 7274.0199 | 7274.0199 |  | 1.1427e-05 | 1.571e-07%
S | Nov | 7199.9995 | 0 | 7199.9995 | 160.6254 | 7039.374 | 7039.374 |  | -8.5462e-06 | -1.214e-07%
T | Dec | 7439.9995 | 0 | 7439.9995 | 165.9796 | 7274.0199 | 7274.0198 |  | -5.1675e-06 | -7.104e-08%
Hydronic Heating/Cooling System
Hot Water Loop Energy Balance for Annual Test Cases
|  | ZONE ONE:Zone Mean Air Temperature [C](Hourly:OUTVARSCHED) | ZONE ONE:Zone Air System Sensible Heating Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOILHEATINGCOIL:Heating Coil Heating Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOILFAN:Fan Electric Power [W](Hourly:OUTVARSCHED) | ZONE1FANCOIL:Fan Coil Heating Energy [J](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CNDW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CNDW SUPPLY PUMP:Pump Fluid Heat Gain Rate [W](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CHILLED WATER LOOP:Plant Supply Side Outlet Temperature [C](Hourly:OUTVARSCHED)
Test Case | Month | Zone/Sys Monthly Average Temp | Zone/Sys Monthly Heating Req'd | Heating Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Heating Output Delivered to Zone | Hot Water Pump Monthly Electric Consumption | Monthly Hot Water Pump Heat to Fluid | Monthly Boiler Load | Monthly Boiler Load Should = Heating Coil Output - Pump Heat to Fluid | Monthly Boiler Load Should = Zone Heating Req'd -Fan Heat - Pump Heat to Fluid
|  | (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
I | Jan | 22.2 | 7439.8643 | 7273.8847 | 165.9796 | 7439.8644 | 128.7694 | 115.8924 | 7141.804 | 7157.9923 | 7157.9923
J | Feb | 22.2001 | 6719.9995 | 6570.0824 | 149.9171 | 6719.9995 | 116.3078 | 104.6771 | 6450.7834 | 6465.4054 | 6465.4054
K | Mar | 22.2001 | 7439.9995 | 7274.0198 | 165.9796 | 7439.9995 | 128.7694 | 115.8924 | 7141.9388 | 7158.1274 | 7158.1274
L | Apr | 22.2001 | 7199.9995 | 7039.3741 | 160.6254 | 7199.9995 | 124.6155 | 112.154 | 6911.5537 | 6927.2201 | 6927.2201
R | Oct | 22.2001 | 7439.9995 | 7274.0199 | 165.9796 | 7439.9995 | 128.7694 | 115.8924 | 7141.9388 | 7158.1274 | 7158.1274
S | Nov | 22.2001 | 7199.9995 | 7039.374 | 160.6254 | 7199.9995 | 124.6155 | 112.154 | 6911.5537 | 6927.2201 | 6927.2201
T | Dec | 22.2001 | 7439.9995 | 7274.0198 | 165.9796 | 7439.9995 | 128.7694 | 115.8924 | 7141.9388 | 7158.1274 | 7158.1274
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (Monthly Boiler Load vs. Heating Coil Output - Pump Heat to Fluid) | Difference (Monthly Boiler Load vs. Zone Heating Req'd -Fan Heat - Pump Heat to Fluid) | Difference (Monthly Boiler Load vs. Heating Coil Output - Pump Heat to Fluid) | Difference (Monthly Boiler Load vs. Zone Heating Req'd -Fan Heat - Pump Heat to Fluid)
|  | (kWh) | (kWh) | (%) | (%)
I | Jan | 16.1883 | 16.1883 | 0.2267% | 0.2267%
J | Feb | 14.622 | 14.622 | 0.2267% | 0.2267%
K | Mar | 16.1886 | 16.1886 | 0.2267% | 0.2267%
L | Apr | 15.6664 | 15.6664 | 0.2267% | 0.2267%
R | Oct | 16.1886 | 16.1886 | 0.2267% | 0.2267%
S | Nov | 15.6664 | 15.6664 | 0.2267% | 0.2267%
T | Dec | 16.1886 | 16.1886 | 0.2267% | 0.2267%
Hydronic Heating/Cooling System
Chilled Water Loop Energy Balance for Annual Test Cases
|  | ZONE ONE:Zone Mean Air Temperature [C](Hourly:OUTVARSCHED) | ZONE ONE:Zone Air System Sensible Cooling Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOILCOOLINGCOIL:Cooling Coil Total Cooling Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOILFAN:Fan Electric Power [W](Hourly:OUTVARSCHED) | ZONE1FANCOIL:Fan Coil Total Cooling Energy [J](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Fluid Heat Gain Rate [W](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Electric Power [W](Hourly:OUTVARSCHED) |  |  | CENTRAL BOILER:Boiler Heating Energy [J](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller EIR Temperature Modifier Multiplier [](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller EIR Part Load Modifier Multiplier [](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED)
Test Case | Month | Zone/Sys Monthly Average Temp | Zone/Sys Monthly Cooling Req'd | Cooling Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Cooling Output Delivered to Zone | Chilled Water Pump Monthly Electric Consumption | Monthly Chilled Water Pump Heat to Fluid | Monthly Chiller Load | Monthly Chiller Load Should = Cooling Coil Output + CHW Pump Heat | Monthly Chiller Load Should = Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid
|  | (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
M | May | 22.2001 | 7440 | 7605.9796 | 165.9796 | 7440 | 208.2326 | 187.4093 | 7776.7264 | 7793.389 | 7793.3889
N | Jun | 22.2001 | 7200 | 7360.6254 | 160.6254 | 7200 | 201.5154 | 181.3639 | 7527.4435 | 7541.9893 | 7541.9893
O | Jul | 22.2001 | 7440 | 7605.9796 | 165.9796 | 7440 | 208.2326 | 187.4093 | 7778.3583 | 7793.3889 | 7793.3889
P | Aug | 22.2001 | 7440 | 7605.9796 | 165.9796 | 7440 | 208.2326 | 187.4093 | 7778.3583 | 7793.3889 | 7793.3889
Q | Sep | 22.2001 | 7200 | 7360.6254 | 160.6254 | 7200 | 201.5154 | 181.3639 | 7527.4435 | 7541.9893 | 7541.9893
Comparison - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - >
Test Case | Month | Difference (Monthly Chiller Load vs. Cooling Coil Output + CHW Pump Heat) | Difference (Monthly Chiller Load vs. Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid) | Difference (Monthly Chiller Load vs. Cooling Coil Output + CHW Pump Heat) | Difference (Monthly Chiller Load vs. Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid)
|  | (kWh) | (kWh) | (%) | (%)
M | May | 16.6626 | 16.6626 | 0.2143% | 0.2143%
N | Jun | 14.5458 | 14.5458 | 0.1932% | 0.1932%
O | Jul | 15.0306 | 15.0306 | 0.1932% | 0.1932%
P | Aug | 15.0306 | 15.0306 | 0.1932% | 0.1932%
Q | Sep | 14.5458 | 14.5458 | 0.1932% | 0.1932%
Hydronic Heating/Cooling System
Condenser Water Loop Energy Balance for Annual Test Cases
Test Case | Month | Chiller Monthly Electric Consumption | Condenser Water Pump Monthly Electric Consumption | Monthly Condenser Water Pump Heat to Fluid | Monthly Cooling Tower Load | Monthly Cooling Tower Load Should = Chiller Load + Chiller Electric Consumption + CNW Pump Heat | Difference (Monthly Cooling Tower Load vs. Chiller Load + Chiller Electric Consumption + CNW Pump Heat) | Difference (Monthly Cooling Tower Load vs. Chiller Load + Chiller Electric Consumption + CNW Pump Heat)
|  | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (%)
M | May | 2012.1396 | 312.5368 | 281.2831 | 10068.2872 | 10070.1491 | 1.8618 | 0.01849%
N | Jun | 1947.5543 | 302.455 | 272.2095 | 9747.4611 | 9747.2073 | -0.25384 | -0.002604%
O | Jul | 2012.4711 | 312.5368 | 281.2831 | 10072.3749 | 10072.1125 | -0.26235 | -0.002605%
P | Aug | 2012.6373 | 312.5368 | 281.2831 | 10072.5394 | 10072.2788 | -0.26064 | -0.002588%
Q | Sep | 1947.5527 | 302.455 | 272.2095 | 9747.4595 | 9747.2057 | -0.25388 | -0.002605%
Hydronic Heating/Cooling System
Equipment Performance Summary for Annual Test Cases
Test Case | Month | Monthly Chiller Load | Chiller Monthly Electric Consumption | Chiller Average COP |  | Cooling Tower Monthly Electric Consumption |  | Monthly Boiler Load | Boiler Monthly Gas Consumption | Boiler Average Efficiency
|  | (kWh) | (kWh) | ( ) |  | (kWh) |  | (kWh) | (kWh) | (% )
I | Jan | [6 empty] | 7141.804 | 8929.2337 | 79.98%
J | Feb | [6 empty] | 6450.7834 | 8065.2657 | 79.98%
K | Mar | [6 empty] | 7141.9388 | 8929.4013 | 79.98%
L | Apr | [6 empty] | 6911.5537 | 8641.3562 | 79.98%
M | May | 7776.7264 | 2012.1396 | 3.8649 |  | 47.4475
N | Jun | 7527.4435 | 1947.5543 | 3.8651 |  | 56.7747
O | Jul | 7778.3583 | 2012.4711 | 3.8651 |  | 65.647
P | Aug | 7778.3583 | 2012.6373 | 3.8648 |  | 65.029
Q | Sep | 7527.4435 | 1947.5527 | 3.8651 |  | 52.9965
R | Oct | [6 empty] | 7141.9388 | 8929.4014 | 79.98%
S | Nov | [6 empty] | 6911.5537 | 8641.3561 | 79.98%
T | Dec | [6 empty] | 7141.9388 | 8929.4013 | 79.98%

## CSV Labels
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
10000 W constant sensible cooling load during summer months
-10000 W heating load during winter months
Heating Side Balance
| ZONE ONE:Zone Other Equipment Lost Heat Energy [J](Hourly:OUTVARSCHED) | ZONE ONE:Zone Other Equipment Total Heating Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOIL:Fan Coil Sensible Cooling Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOIL:Fan Coil Heating Energy [J](Hourly:OUTVARSCHED) | COMPACT HVAC-ALWAYS 6.67:Schedule Value [](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Condenser Inlet Temperature [C](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Condenser Outlet Temperature [C](Hourly:OUTVARSCHED) | HOT WATER LOOP HOT WATER LOOP:Plant Supply Side Outlet Temperature [C](Hourly:OUTVARSCHED)
| Zone/Sys Monthly Average Temp | Zone/Sys Monthly Heating Req'd | Heating Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Heating Output Delivered to Zone | Hot Water Pump Monthly Electric Consumption | Monthly Hot Water Pump Heat to Fluid | Monthly Boiler Load | Monthly Boiler Load Should = Heating Coil Output - Pump Heat to Fluid | Monthly Boiler Load Should = Zone Heating Req'd -Fan Heat - Pump Heat to Fluid
| (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
Jan | 0 | -7440 | 0 | 26783511.6901 | 0.0013785 | 21.9034 | 21.9034 | 0.020667 | -21.9034 | -26790973.5935
Feb | 0 | -6720 | 0 | 24191998.1955 | 0.0012451 | 19.7837 | 19.7837 | 0.018667 | -19.7837 | -24198737.9792
Mar | 0 | -7440 | 0 | 26783998.0673 | 0.0013785 | 21.9034 | 21.9034 | 0.020667 | -21.9034 | -26791459.9707
Apr | 0 | -7200 | 0 | 25919998.2153 | 0.001334 | 21.1968 | 21.1968 | 0.02 | -21.1968 | -25927219.4121
Oct | 0 | -7440 | 0 | 26783998.197 | 0.0013785 | 21.9034 | 21.9034 | 0.020667 | -21.9034 | -26791460.1004
Nov | 0 | -7200 | 0 | 25919998.1239 | 0.001334 | 21.1968 | 21.1968 | 0.02 | -21.1968 | -25927219.3207
Dec | 0 | -7440 | 0 | 26783998.0693 | 0.0013785 | 21.9034 | 21.9034 | 0.020667 | -21.9034 | -26791459.9727
Global Energy Test Balance
Fan Coil with Chiller and Boiler
Zone Setpoint Temp = 22.2C
10000 W constant cooling load during summer months
-10000 W heating load during winter months
Cooling Side Balance
| ZONE ONE:Zone Other Equipment Lost Heat Energy [J](Hourly:OUTVARSCHED) | ZONE ONE OTHEQ-HEATING:Other Equipment Total Heating Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOILFAN:Fan Electric Energy [J](Hourly:OUTVARSCHED) | ZONE1FANCOIL:Fan Coil Heating Energy [J](Hourly:OUTVARSCHED) | COMPACT HVAC-ALWAYS 29.44:Schedule Value [](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller Condenser Mass Flow Rate [kg/s](Hourly:OUTVARSCHED) | CHILLED WATER LOOP CNDW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED) | CENTRAL BOILER:Boiler Gas Energy [J](Hourly:OUTVARSCHED) |  |  | CENTRAL BOILER:Boiler Heating Energy [J](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller EIR Temperature Modifier Multiplier [](Hourly:OUTVARSCHED) | CENTRAL CHILLER:Chiller EIR Part Load Modifier Multiplier [](Hourly:OUTVARSCHED) | HOT WATER LOOP HW SUPPLY PUMP:Pump Electric Power [W](Hourly:OUTVARSCHED)
| Zone/Sys Monthly Average Temp | Zone/Sys Monthly Cooling Req'd | Cooling Coil Monthly Output | Monthly Fan Heat to Air Stream | Fan Coil Monthly Cooling Output Delivered to Zone | Chilled Water Pump Monthly Electric Consumption | Monthly Chilled Water Pump Heat to Fluid | Monthly Chiller Load | Monthly Chiller Load Should = Cooling Coil Output + CHW Pump Heat | Monthly Chiller Load Should = Zone Cooling Req'd + Fan Heat + CHW Pump Heat to Fluid | Chiller Monthly Electric Consumption | Condenser Water Pump Monthly Electric Consumption | Monthly Condenser Water Pump Heat to Fluid | Monthly Cooling Tower Load | Monthly Cooling Tower Load Should = Chiller Load + Chiller Electric Consumption + CNW Pump Heat
| (C) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh)
May | 0 | 0 | 165.9796 | 0 | 0.0060843 | 0.43694 | 312.5368 | 0 | 478.5164 | 312.5368 | 0 | 0.74392 | 0.71803 | 0 | 0.71803
Jun | 0 | 0 | 160.6254 | 0 | 0.005888 | 0.42284 | 302.455 | 0 | 463.0804 | 302.455 | 0 | 0.71992 | 0.69498 | 0 | 0.69498
Jul | 0 | 0 | 165.9796 | 0 | 0.0060843 | 0.43694 | 312.5368 | 0 | 478.5164 | 312.5368 | 0 | 0.74392 | 0.71815 | 0 | 0.71815
Aug | 0 | 0 | 165.9796 | 0 | 0.0060843 | 0.43694 | 312.5368 | 0 | 478.5164 | 312.5368 | 0 | 0.74399 | 0.71817 | 0 | 0.71817
Sep | 0 | 0 | 160.6254 | 0 | 0.005888 | 0.42284 | 302.455 | 0 | 463.0804 | 302.455 | 0 | 0.71992 | 0.69498 | 0 | 0.69498