## Coefficients
OR-317 Performance Curves
Manufacturer: |  | York
Class: |  | Electric Reciprocating Water Chiller
| Type: | Water-Cooled
|  |  | NomCap | NomCap | MIN-RATIO | MAX-RATIO | EIR | HERM-REC- COND-TYPE | HERM-REC- COND-PWR | HERM-REC-UNL-RAT | HERM-REC-CAP-FT |  | - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - > |  |  |  | HERM-REC-EIR-FT |  | - - - - - - - - - - - - - - - - - - - - - - - - - - - - - > |  |  |  | HERM-REC-EIR-FPLR |  | - - - - - - - - - - - - - - - - - - - - - >
|  |  | Tons | MMBtu | [6 empty] | a | b | c | d | e | f | a | b | c | d | e | f | a | b | c | d | e | f
| Model | YCWZ33AB0 | 56.5 | 0.678 | 0.26 | 1 | 0.2547 | WATER | -- | -- | 0.5376 | 0.015198 | 0.00010362 | -0.0011743 | -1.0836e-05 | -6.1188e-05 | 0.70162 | -0.01604 | 0.00014063 | 0.0088718 | 6.725e-05 | -0.00013587 | #REF! | #REF! | #REF! | -- | -- | --
| Model | YCWJ55HE0 | 138.9 | 1.6668 | 0.29 | 1 | 0.2547 | WATER | -- | -- | 1.0187 | 0.035768 | 0.00033572 | -0.0068865 | -3.5109e-05 | -0.00019825 | 0.54598 | -0.020497 | 0.00045565 | 0.01589 | 0.00021789 | -0.00044022 | #REF! | #REF! | #REF! | -- | -- | --
| Model | YCWJ99MJ0 | 252.2 | 3.0264 | 0.14 | 1 | 0 | WATER | -- | -- | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | -- | -- | --

## WaterCool-Recip-CAP-FT
Performance Curves
Manufacturer: | York
Class: | Reciprocating Water Chiller
Type: | Water-Cooled, Electric
Source of Data: | YORK Millennium Liquid Chillers, 60 to 250 tons, Form 150.24-EG2 (899)
EnergyPlus Curve: | RecipCapFt |  | CHWS=Chilled Water Supply Temperature (F) |  |  |  | CWS=Entering Condenser Water Temperature (F)
English Units
[9 empty] | Normalized | CAP-FT | % Diff |  | CAP-FT
| Manufacturer | Model | CHWS | CHWS**2 | CWS | CWS**2 | CHWS*CWS | Capacity (tons) | CAP | From Curve
| York | YCWZ33AB0 | 40 | 1600 | 75 | 5625 | 3000 | 55.3 | 0.97876 | 0.97871 | -0.004826% |  | f | e | d | c | b | a | Adjusted a
| York | YCWZ33AB0 | 42 | 1764 | 75 | 5625 | 3150 | 57.5 | 1.0177 | 1.0169 | -0.07612% |  | -6.1188e-05 | -1.0836e-05 | -0.0011743 | 0.00010362 | 0.015198 | 0.5378 | 0.5376
| York | YCWZ33AB0 | 44 | 1936 | 75 | 5625 | 3300 | 59.7 | 1.0566 | 1.056 | -0.0637% |  | 3.5323e-06 | 1.8881e-06 | 0.00035835 | 7.8206e-06 | 0.00076563 | 0.024831
| York | YCWZ33AB0 | 45 | 2025 | 75 | 5625 | 3375 | 60.8 | 1.0761 | 1.0758 | -0.02894% | r2 | 0.99997 | 0.00046728 | #N/A | #N/A | #N/A | #N/A
| York | YCWZ33AB0 | 46 | 2116 | 75 | 5625 | 3450 | 61.9 | 1.0956 | 1.0958 | 0.02349%
| York | YCWZ33AB0 | 48 | 2304 | 75 | 5625 | 3600 | 64.2 | 1.1363 | 1.1365 | 0.02173%
| York | YCWZ33AB0 | 50 | 2500 | 75 | 5625 | 3750 | 66.6 | 1.1788 | 1.1781 | -0.05978%
| York | YCWZ33AB0 | 40 | 1600 | 80 | 6400 | 3200 | 53.8 | 0.95221 | 0.95221 | -0.0005978%
| York | YCWZ33AB0 | 42 | 1764 | 80 | 6400 | 3360 | 55.9 | 0.98938 | 0.98981 | 0.04295%
| York | YCWZ33AB0 | 44 | 1936 | 80 | 6400 | 3520 | 58.1 | 1.0283 | 1.0282 | -0.008306%
| York | YCWZ33AB0 | 45 | 2025 | 80 | 6400 | 3600 | 59.2 | 1.0478 | 1.0478 | -0.002838%
| York | YCWZ33AB0 | 46 | 2116 | 80 | 6400 | 3680 | 60.3 | 1.0673 | 1.0675 | 0.02185%
| York | YCWZ33AB0 | 48 | 2304 | 80 | 6400 | 3840 | 62.6 | 1.108 | 1.1076 | -0.03513%
| York | YCWZ33AB0 | 50 | 2500 | 80 | 6400 | 4000 | 64.9 | 1.1487 | 1.1485 | -0.0159%
| York | YCWZ33AB0 | 40 | 1600 | 85 | 7225 | 3400 | 52.3 | 0.92566 | 0.92516 | -0.05466%
| York | YCWZ33AB0 | 42 | 1764 | 85 | 7225 | 3570 | 54.4 | 0.96283 | 0.96214 | -0.07137%
| York | YCWZ33AB0 | 44 | 1936 | 85 | 7225 | 3740 | 56.5 | 1 | 0.99996 | -0.003954%
| York | YCWZ33AB0 | 45 | 2025 | 85 | 7225 | 3825 | 57.6 | 1.0195 | 1.0192 | -0.02843%
| York | YCWZ33AB0 | 46 | 2116 | 85 | 7225 | 3910 | 58.7 | 1.0389 | 1.0386 | -0.03204%
| York | YCWZ33AB0 | 48 | 2304 | 85 | 7225 | 4080 | 60.9 | 1.0779 | 1.0781 | 0.01881%
| York | YCWZ33AB0 | 50 | 2500 | 85 | 7225 | 4250 | 63.2 | 1.1186 | 1.1184 | -0.01811%
| York | YCWZ33AB0 | 40 | 1600 | 90 | 8100 | 3600 | 50.7 | 0.89735 | 0.89757 | 0.02472%
| York | YCWZ33AB0 | 42 | 1764 | 90 | 8100 | 3780 | 52.8 | 0.93451 | 0.93394 | -0.06113%
| York | YCWZ33AB0 | 44 | 1936 | 90 | 8100 | 3960 | 54.9 | 0.97168 | 0.97115 | -0.05511%
| York | YCWZ33AB0 | 45 | 2025 | 90 | 8100 | 4050 | 56 | 0.99115 | 0.99006 | -0.1101%
| York | YCWZ33AB0 | 46 | 2116 | 90 | 8100 | 4140 | 57 | 1.0088 | 1.0092 | 0.03264%
| York | YCWZ33AB0 | 48 | 2304 | 90 | 8100 | 4320 | 59.2 | 1.0478 | 1.048 | 0.02415%
| York | YCWZ33AB0 | 50 | 2500 | 90 | 8100 | 4500 | 61.5 | 1.0885 | 1.0877 | -0.07021%
| York | YCWZ33AB0 | 40 | 1600 | 95 | 9025 | 3800 | 49.1 | 0.86903 | 0.86943 | 0.04694%
| York | YCWZ33AB0 | 42 | 1764 | 95 | 9025 | 3990 | 51.2 | 0.90619 | 0.9052 | -0.11%
| York | YCWZ33AB0 | 44 | 1936 | 95 | 9025 | 4180 | 53.2 | 0.94159 | 0.94179 | 0.02089%
| York | YCWZ33AB0 | 45 | 2025 | 95 | 9025 | 4275 | 54.3 | 0.96106 | 0.9604 | -0.06924%
| York | YCWZ33AB0 | 46 | 2116 | 95 | 9025 | 4370 | 55.3 | 0.97876 | 0.97921 | 0.04593%
| York | YCWZ33AB0 | 48 | 2304 | 95 | 9025 | 4560 | 57.5 | 1.0177 | 1.0175 | -0.02344%
| York | YCWZ33AB0 | 50 | 2500 | 95 | 9025 | 4750 | 59.7 | 1.0566 | 1.0565 | -0.009256%
Metric Units
|  |  | CHWS=Chilled Water Supply Temperature (C) |  |  |  | CWS=Entering Condenser Water Temperature (C)
[9 empty] | Normalized | CAP-FT | % Diff |  | CAP-FT
| Manufacturer | Model | CHWS | CHWS**2 | CWS | CWS**2 | CHWS*CWS | Capacity (kW) | CAP | From Curve
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 23.8889 | 570.679 | 106.1728 | 194.4331 | 0.97876 | 0.97871 | -0.004826% |  | f | e | d | c | b | a | Adjusted a
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 23.8889 | 570.679 | 132.716 | 202.1682 | 1.0177 | 1.0169 | -0.07612% |  | -0.00019825 | -3.5109e-05 | -0.0068865 | 0.00033572 | 0.035768 | 1.0189 | 1.0187 | a | 1.0187
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 23.8889 | 570.679 | 159.2593 | 209.9033 | 1.0566 | 1.056 | -0.0637% |  | 1.1445e-05 | 6.1174e-06 | 0.00037015 | 2.5339e-05 | 0.00049954 | 0.0059218 |  | b | 0.035768
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 23.8889 | 570.679 | 172.5309 | 213.7709 | 1.0761 | 1.0758 | -0.02894% | r2 | 0.99997 | 0.00046728 | #N/A | #N/A | #N/A | #N/A |  | c | 0.00033572
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 23.8889 | 570.679 | 185.8025 | 217.6384 | 1.0956 | 1.0958 | 0.02349% | [8 empty] | d | -0.0068865
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 23.8889 | 570.679 | 212.3457 | 225.7252 | 1.1363 | 1.1365 | 0.02173% | [8 empty] | e | -3.5109e-05
| York | YCWZ33AB0 | 10 | 100 | 23.8889 | 570.679 | 238.8889 | 234.1635 | 1.1788 | 1.1781 | -0.05978% | [8 empty] | f | -0.00019825
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 26.6667 | 711.1111 | 118.5185 | 189.1591 | 0.95221 | 0.95221 | -0.0005978%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 26.6667 | 711.1111 | 148.1481 | 196.5426 | 0.98938 | 0.98981 | 0.04295%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 26.6667 | 711.1111 | 177.7778 | 204.2778 | 1.0283 | 1.0282 | -0.008306%
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 26.6667 | 711.1111 | 192.5926 | 208.1453 | 1.0478 | 1.0478 | -0.002838%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 26.6667 | 711.1111 | 207.4074 | 212.0129 | 1.0673 | 1.0675 | 0.02185%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 26.6667 | 711.1111 | 237.037 | 220.0996 | 1.108 | 1.1076 | -0.03513%
| York | YCWZ33AB0 | 10 | 100 | 26.6667 | 711.1111 | 266.6667 | 228.1863 | 1.1487 | 1.1485 | -0.0159%
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 29.4444 | 866.9753 | 130.8642 | 183.8851 | 0.92566 | 0.92516 | -0.05466% |  | CHWS | CWS
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 29.4444 | 866.9753 | 163.5802 | 191.2687 | 0.96283 | 0.96214 | -0.07137% |  |  | 21.5 | 23.8889 | 26.6667 | 29.4444 | 32.2222 | 35
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 29.4444 | 866.9753 | 196.2963 | 198.6522 | 1 | 0.99996 | -0.003954% |  | 3.2 | 0.95868 | 0.9369 | 0.91108 | 0.88472 | 0.85781 | 0.83036
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 29.4444 | 866.9753 | 212.6543 | 202.5198 | 1.0195 | 1.0192 | -0.02843% |  | 4.4444 | 1.0011 | 0.97871 | 0.95221 | 0.92516 | 0.89757 | 0.86943
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 29.4444 | 866.9753 | 229.0123 | 206.3873 | 1.0389 | 1.0386 | -0.03204% |  | 5.5556 | 1.0398 | 1.0169 | 0.98981 | 0.96214 | 0.93394 | 0.9052
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 29.4444 | 866.9753 | 261.7284 | 214.1225 | 1.0779 | 1.0781 | 0.01881% |  | 6.6667 | 1.0794 | 1.056 | 1.0282 | 0.99996 | 0.97115 | 0.94179
| York | YCWZ33AB0 | 10 | 100 | 29.4444 | 866.9753 | 294.4444 | 222.2092 | 1.1186 | 1.1184 | -0.01811% |  | 7.2222 | 1.0995 | 1.0758 | 1.0478 | 1.0192 | 0.99006 | 0.9604
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 32.2222 | 1038.2716 | 143.2099 | 178.2596 | 0.89735 | 0.89757 | 0.02472% |  | 7.7778 | 1.1198 | 1.0958 | 1.0675 | 1.0386 | 1.0092 | 0.97921
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 32.2222 | 1038.2716 | 179.0123 | 185.6431 | 0.93451 | 0.93394 | -0.06113% |  | 8.8889 | 1.161 | 1.1365 | 1.1076 | 1.0781 | 1.048 | 1.0175
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 32.2222 | 1038.2716 | 214.8148 | 193.0267 | 0.97168 | 0.97115 | -0.05511% |  | 10 | 1.2031 | 1.1781 | 1.1485 | 1.1184 | 1.0877 | 1.0565
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 32.2222 | 1038.2716 | 232.716 | 196.8942 | 0.99115 | 0.99006 | -0.1101% |  | 11.2 | 1.2494 | 1.2238 | 1.1936 | 1.1628 | 1.1315 | 1.0997
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 32.2222 | 1038.2716 | 250.6173 | 200.4102 | 1.0088 | 1.0092 | 0.03264%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 32.2222 | 1038.2716 | 286.4198 | 208.1453 | 1.0478 | 1.048 | 0.02415%
| York | YCWZ33AB0 | 10 | 100 | 32.2222 | 1038.2716 | 322.2222 | 216.2321 | 1.0885 | 1.0877 | -0.07021%
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 35 | 1225 | 155.5556 | 172.634 | 0.86903 | 0.86943 | 0.04694%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 35 | 1225 | 194.4444 | 180.0176 | 0.90619 | 0.9052 | -0.11%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 35 | 1225 | 233.3333 | 187.0495 | 0.94159 | 0.94179 | 0.02089%
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 35 | 1225 | 252.7778 | 190.9171 | 0.96106 | 0.9604 | -0.06924%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 35 | 1225 | 272.2222 | 194.4331 | 0.97876 | 0.97921 | 0.04593%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 35 | 1225 | 311.1111 | 202.1682 | 1.0177 | 1.0175 | -0.02344%
| York | YCWZ33AB0 | 10 | 100 | 35 | 1225 | 350 | 209.9033 | 1.0566 | 1.0565 | -0.009256%

## WaterCool-Recip-EIR-FT
Performance Curves
Manufacturer: | York
Class: | Reciprocating Water Chiller
Type: | Water-Cooled, Electric
Source of Data: | YORK Millennium Liquid Chillers, 60 to 250 tons, Form 150.24-EG2 (899)
EnergyPlus Curve: | RecipEIRFt |  | CHWS=Chilled Water Supply Temperature (F) |  |  |  | CWS=Entering Condenser Water Temperature (F)
| English Units |  | EER includes compressor power
EIR = 3.413/EER
[9 empty] | Total Unit EER |  | Normalized | EIR-FT | % Diff |  | EIR-FT
| Manufacturer | Model | CHWS | CHWS**2 | CWS | CWS**2 | CHWS*CWS | Capacity (tons) | BTU/Watt | EIR | EIR | From Curve
| York | YCWZ33AB0 | 40 | 1600 | 75 | 5625 | 3000 | 55.3 | 14.5 | 0.23538 | 0.92414 | 0.92109 | -0.3301% |  | f | e | d | c | b | a | Adjusted a
| York | YCWZ33AB0 | 42 | 1764 | 75 | 5625 | 3150 | 57.5 | 15 | 0.22753 | 0.89333 | 0.89169 | -0.1839% |  | -0.00013587 | 6.725e-05 | 0.0088718 | 0.00014063 | -0.01604 | 0.70372 | 0.70162
| York | YCWZ33AB0 | 44 | 1936 | 75 | 5625 | 3300 | 59.7 | 15.5 | 0.22019 | 0.86452 | 0.86342 | -0.127% |  | 1.5715e-05 | 8.4e-06 | 0.0015943 | 3.4794e-05 | 0.0034062 | 0.11047
| York | YCWZ33AB0 | 45 | 2025 | 75 | 5625 | 3375 | 60.8 | 15.7 | 0.21739 | 0.8535 | 0.8497 | -0.4451% | r2 | 0.99971 | 0.0020789 | #N/A | #N/A | #N/A | #N/A
| York | YCWZ33AB0 | 46 | 2116 | 75 | 5625 | 3450 | 61.9 | 16 | 0.21331 | 0.8375 | 0.83627 | -0.1466%
| York | YCWZ33AB0 | 48 | 2304 | 75 | 5625 | 3600 | 64.2 | 16.5 | 0.20685 | 0.81212 | 0.81025 | -0.2304%
| York | YCWZ33AB0 | 50 | 2500 | 75 | 5625 | 3750 | 66.6 | 17 | 0.20076 | 0.78824 | 0.78535 | -0.3655%
| York | YCWZ33AB0 | 40 | 1600 | 80 | 6400 | 3200 | 53.8 | 13.5 | 0.25281 | 0.99259 | 0.99039 | -0.2218%
| York | YCWZ33AB0 | 42 | 1764 | 80 | 6400 | 3360 | 55.9 | 13.9 | 0.24554 | 0.96403 | 0.95964 | -0.4557%
| York | YCWZ33AB0 | 44 | 1936 | 80 | 6400 | 3520 | 58.1 | 14.4 | 0.23701 | 0.93056 | 0.93 | -0.05917%
| York | YCWZ33AB0 | 45 | 2025 | 80 | 6400 | 3600 | 59.2 | 14.6 | 0.23377 | 0.91781 | 0.91561 | -0.2393%
| York | YCWZ33AB0 | 46 | 2116 | 80 | 6400 | 3680 | 60.3 | 14.8 | 0.23061 | 0.90541 | 0.9015 | -0.4314%
| York | YCWZ33AB0 | 48 | 2304 | 80 | 6400 | 3840 | 62.6 | 15.3 | 0.22307 | 0.87582 | 0.87412 | -0.1938%
| York | YCWZ33AB0 | 50 | 2500 | 80 | 6400 | 4000 | 64.9 | 15.8 | 0.21601 | 0.8481 | 0.84786 | -0.02795%
| York | YCWZ33AB0 | 40 | 1600 | 85 | 7225 | 3400 | 52.3 | 12.6 | 0.27087 | 1.0635 | 1.0631 | -0.04092%
| York | YCWZ33AB0 | 42 | 1764 | 85 | 7225 | 3570 | 54.4 | 13 | 0.26254 | 1.0308 | 1.0309 | 0.01684%
| York | YCWZ33AB0 | 44 | 1936 | 85 | 7225 | 3740 | 56.5 | 13.4 | 0.2547 | 1 | 0.99995 | -0.004621%
| York | YCWZ33AB0 | 45 | 2025 | 85 | 7225 | 3825 | 57.6 | 13.6 | 0.25096 | 0.98529 | 0.98488 | -0.04191%
| York | YCWZ33AB0 | 46 | 2116 | 85 | 7225 | 3910 | 58.7 | 13.8 | 0.24732 | 0.97101 | 0.97009 | -0.09523%
| York | YCWZ33AB0 | 48 | 2304 | 85 | 7225 | 4080 | 60.9 | 14.2 | 0.24035 | 0.94366 | 0.94135 | -0.2449%
| York | YCWZ33AB0 | 50 | 2500 | 85 | 7225 | 4250 | 63.2 | 14.6 | 0.23377 | 0.91781 | 0.91374 | -0.4436%
| York | YCWZ33AB0 | 40 | 1600 | 90 | 8100 | 3600 | 50.7 | 11.7 | 0.29171 | 1.1453 | 1.1391 | -0.5425%
| York | YCWZ33AB0 | 42 | 1764 | 90 | 8100 | 3780 | 52.8 | 12.1 | 0.28207 | 1.1074 | 1.1056 | -0.1648%
| York | YCWZ33AB0 | 44 | 1936 | 90 | 8100 | 3960 | 54.9 | 12.5 | 0.27304 | 1.072 | 1.0733 | 0.118%
| York | YCWZ33AB0 | 45 | 2025 | 90 | 8100 | 4050 | 56 | 12.6 | 0.27087 | 1.0635 | 1.0575 | -0.5622%
| York | YCWZ33AB0 | 46 | 2116 | 90 | 8100 | 4140 | 57 | 12.8 | 0.26664 | 1.0469 | 1.042 | -0.4616%
| York | YCWZ33AB0 | 48 | 2304 | 90 | 8100 | 4320 | 59.2 | 13.2 | 0.25856 | 1.0152 | 1.0119 | -0.3159%
| York | YCWZ33AB0 | 50 | 2500 | 90 | 8100 | 4500 | 61.5 | 13.6 | 0.25096 | 0.98529 | 0.98297 | -0.2356%
| York | YCWZ33AB0 | 40 | 1600 | 95 | 9025 | 3800 | 49.1 | 11 | 0.31027 | 1.2182 | 1.2185 | 0.02423%
| York | YCWZ33AB0 | 42 | 1764 | 95 | 9025 | 3990 | 51.2 | 11.3 | 0.30204 | 1.1858 | 1.1836 | -0.1851%
| York | YCWZ33AB0 | 44 | 1936 | 95 | 9025 | 4180 | 53.2 | 11.6 | 0.29422 | 1.1552 | 1.1499 | -0.453%
| York | YCWZ33AB0 | 45 | 2025 | 95 | 9025 | 4275 | 54.3 | 11.8 | 0.28924 | 1.1356 | 1.1335 | -0.1836%
| York | YCWZ33AB0 | 46 | 2116 | 95 | 9025 | 4370 | 55.3 | 12 | 0.28442 | 1.1167 | 1.1174 | 0.06188%
| York | YCWZ33AB0 | 48 | 2304 | 95 | 9025 | 4560 | 57.5 | 12.3 | 0.27748 | 1.0894 | 1.0859 | -0.324%
| York | YCWZ33AB0 | 50 | 2500 | 95 | 9025 | 4750 | 59.7 | 12.7 | 0.26874 | 1.0551 | 1.0556 | 0.04284%
Metric Units
[9 empty] | Total Unit EER |  | Normalized | EIR-FT | % Diff |  | EIR-FT
| Manufacturer | Model | CHWS | CHWS**2 | CWS | CWS**2 | CHWS*CWS | Capacity (tons) | BTU/Watt | EIR | EIR | From Curve
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 23.8889 | 570.679 | 106.1728 | 55.3 | 14.5 | 0.23538 | 0.92414 | 0.92109 | -0.3301% |  | f | e | d | c | b | a | Adjusted a
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 23.8889 | 570.679 | 132.716 | 57.5 | 15 | 0.22753 | 0.89333 | 0.89169 | -0.1839% |  | -0.00044022 | 0.00021789 | 0.01589 | 0.00045565 | -0.020497 | 0.54808 | 0.54598 | a | 0.54598
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 23.8889 | 570.679 | 159.2593 | 59.7 | 15.5 | 0.22019 | 0.86452 | 0.86342 | -0.127% |  | 5.0917e-05 | 2.7216e-05 | 0.0016468 | 0.00011273 | 0.0022224 | 0.026346 |  | b | -0.020497
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 23.8889 | 570.679 | 172.5309 | 60.8 | 15.7 | 0.21739 | 0.8535 | 0.8497 | -0.4451% | r2 | 0.99971 | 0.0020789 | #N/A | #N/A | #N/A | #N/A |  | c | 0.00045565
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 23.8889 | 570.679 | 185.8025 | 61.9 | 16 | 0.21331 | 0.8375 | 0.83627 | -0.1466% | [8 empty] | d | 0.01589
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 23.8889 | 570.679 | 212.3457 | 64.2 | 16.5 | 0.20685 | 0.81212 | 0.81025 | -0.2304% | [8 empty] | e | 0.00021789
| York | YCWZ33AB0 | 10 | 100 | 23.8889 | 570.679 | 238.8889 | 66.6 | 17 | 0.20076 | 0.78824 | 0.78535 | -0.3655% | [8 empty] | f | -0.00044022
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 26.6667 | 711.1111 | 118.5185 | 53.8 | 13.5 | 0.25281 | 0.99259 | 0.99039 | -0.2218%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 26.6667 | 711.1111 | 148.1481 | 55.9 | 13.9 | 0.24554 | 0.96403 | 0.95964 | -0.4557%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 26.6667 | 711.1111 | 177.7778 | 58.1 | 14.4 | 0.23701 | 0.93056 | 0.93 | -0.05917%
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 26.6667 | 711.1111 | 192.5926 | 59.2 | 14.6 | 0.23377 | 0.91781 | 0.91561 | -0.2393%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 26.6667 | 711.1111 | 207.4074 | 60.3 | 14.8 | 0.23061 | 0.90541 | 0.9015 | -0.4314%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 26.6667 | 711.1111 | 237.037 | 62.6 | 15.3 | 0.22307 | 0.87582 | 0.87412 | -0.1938%
| York | YCWZ33AB0 | 10 | 100 | 26.6667 | 711.1111 | 266.6667 | 64.9 | 15.8 | 0.21601 | 0.8481 | 0.84786 | -0.02795%
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 29.4444 | 866.9753 | 130.8642 | 52.3 | 12.6 | 0.27087 | 1.0635 | 1.0631 | -0.04092%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 29.4444 | 866.9753 | 163.5802 | 54.4 | 13 | 0.26254 | 1.0308 | 1.0309 | 0.01684%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 29.4444 | 866.9753 | 196.2963 | 56.5 | 13.4 | 0.2547 | 1 | 0.99995 | -0.004621% |  | COP=EER/3.413= |  | 3.9262
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 29.4444 | 866.9753 | 212.6543 | 57.6 | 13.6 | 0.25096 | 0.98529 | 0.98488 | -0.04191%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 29.4444 | 866.9753 | 229.0123 | 58.7 | 13.8 | 0.24732 | 0.97101 | 0.97009 | -0.09523%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 29.4444 | 866.9753 | 261.7284 | 60.9 | 14.2 | 0.24035 | 0.94366 | 0.94135 | -0.2449%
| York | YCWZ33AB0 | 10 | 100 | 29.4444 | 866.9753 | 294.4444 | 63.2 | 14.6 | 0.23377 | 0.91781 | 0.91374 | -0.4436%
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 32.2222 | 1038.2716 | 143.2099 | 50.7 | 11.7 | 0.29171 | 1.1453 | 1.1391 | -0.5425%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 32.2222 | 1038.2716 | 179.0123 | 52.8 | 12.1 | 0.28207 | 1.1074 | 1.1056 | -0.1648%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 32.2222 | 1038.2716 | 214.8148 | 54.9 | 12.5 | 0.27304 | 1.072 | 1.0733 | 0.118%
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 32.2222 | 1038.2716 | 232.716 | 56 | 12.6 | 0.27087 | 1.0635 | 1.0575 | -0.5622%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 32.2222 | 1038.2716 | 250.6173 | 57 | 12.8 | 0.26664 | 1.0469 | 1.042 | -0.4616%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 32.2222 | 1038.2716 | 286.4198 | 59.2 | 13.2 | 0.25856 | 1.0152 | 1.0119 | -0.3159%
| York | YCWZ33AB0 | 10 | 100 | 32.2222 | 1038.2716 | 322.2222 | 61.5 | 13.6 | 0.25096 | 0.98529 | 0.98297 | -0.2356%
| York | YCWZ33AB0 | 4.4444 | 19.7531 | 35 | 1225 | 155.5556 | 49.1 | 11 | 0.31027 | 1.2182 | 1.2185 | 0.02423%
| York | YCWZ33AB0 | 5.5556 | 30.8642 | 35 | 1225 | 194.4444 | 51.2 | 11.3 | 0.30204 | 1.1858 | 1.1836 | -0.1851%
| York | YCWZ33AB0 | 6.6667 | 44.4444 | 35 | 1225 | 233.3333 | 53.2 | 11.6 | 0.29422 | 1.1552 | 1.1499 | -0.453%
| York | YCWZ33AB0 | 7.2222 | 52.1605 | 35 | 1225 | 252.7778 | 54.3 | 11.8 | 0.28924 | 1.1356 | 1.1335 | -0.1836%
| York | YCWZ33AB0 | 7.7778 | 60.4938 | 35 | 1225 | 272.2222 | 55.3 | 12 | 0.28442 | 1.1167 | 1.1174 | 0.06188%
| York | YCWZ33AB0 | 8.8889 | 79.0123 | 35 | 1225 | 311.1111 | 57.5 | 12.3 | 0.27748 | 1.0894 | 1.0859 | -0.324%
| York | YCWZ33AB0 | 10 | 100 | 35 | 1225 | 350 | 59.7 | 12.7 | 0.26874 | 1.0551 | 1.0556 | 0.04284%